## Slide 1
MMR Modularization
5
Roof Design Concept
■ Overall Roof Design
Roof Module
(Max. 3m height)
Standard Module
■ NP Cross Section (A-A’)
■ Sectional Planning (B-B’)
Duct
Cable
Pipe
Molten Salt Pipe
Access
A’
A
B
B’
1:12 SLOPE
1:12 SLOPE

## Slide 2
MMR Modularization
5
Roof Design Concept
■ Removable Roof Panel for Turbine Hall
■ Removable Roof Panel (Frame View)

## Slide 3
MMR Modularization
5
Roof Design Concept
■ Removal Sequences
Sequence-1
Removable Area
Sequence-2
Sequence-3
Roof Opening
(16.5m x 11.0m)

## Slide 4
MMR Modularization
5
Roof Design Concept
■ Removable Roof Panel (ALT-1)
■ Removable Roof Panel (ALT-2)

## Slide 5
MMR Modularization
5
Passive Firefighting Design
■ Fire Separation for NP Building
[Fire barrier between NP and AP]
Fire separation : 3 hrs
Code : NFPA 804
[ACU Room]
Fire separation : 1hrs
Code : -
[Laydown Storage Room]
Fire separation : 2hrs
Code : CSA N293-12, NBCC
[Change & Changeover Room]
Fire separation : 2hrs (min. 1hr)
[Waste Room]
Fire separation : 2hrs
Code : CSA N293-12, NBCC
[Reactor EQ Room]
Fire separation : 2hrs
Code : -
[Electrical Room]
Fire separation : 2hrs
Code : NFPA 850
[AHU Room]
Fire separation : 1hr
Code : -
[MCR]
Fire separation : 3hrs
Code : NFPA 804
[Corridor (Access to SCA)]
Fire separation : 2hrs
Code : CSA N293-12
[Gas Extinguish Room]
Fire separation : 2hrs
[Decontamination Room]
Fire separation : 2hrs

## Slide 6
MMR Modularization
5
Passive Firefighting Design
■ Requirements for Fire Separation
Most conservative case(time) for each fire separation wall shall be adopted.
For vertical continuity, all fire separation walls shall continue up through the ceiling and void space, so as to terminate tightly against the underside of the floor / ceiling assembly.
Penetration seal (around openings for duct, cable tray, or pipe), having fire resistance rating not less than required time for the separation wall, shall be provided.
Corridor
Fire Barrier
(Up to Roof Level)
Partition wall
(Up to Ceiling Level)
Roof
Ceiling
Void Space

## Slide 7
MMR Modularization
5
Passive Firefighting Design
■ Sample Photo for Firestop Materials
For vertical continuity, all fire separation walls shall continue up through the ceiling and void space, so as to terminate tightly against the underside of the floor / ceiling assembly.
Most conservative case(time) for each fire separation wall shall be adopted.
Penetration seal (around openings for duct, cable tray, or pipe), having fire resistance rating not less than required time for the separation wall, shall be provided.
Low-density Silicon
High-density Grout
RTV Foam
Firestop Sealant
■ Requirements for Fire Separation

## Slide 8
MMR Modularization
5
Drainage System
■ Web opening for steel connection
Web opening
For pipe connection between modules
Cast Iron Pipe with 1:100~500 Slope
Web opening
For steel connection between modules
Ditch
■ Isometric View for Drain Pipe
■ Section Detail
■ Web opening for pipe connection
■ Interconnection pipe
A1-15-02
A1-15-03
Connection pipe to be installed at site.
Connected to Adjacent ditch in Turbine hall
A1-15-03
A1-15-02
A1-15-01
A1-15-02
A1-15-03
A1-15-01

## Slide 9
MMR Modularization
5
Canopy Fixing Detail
■ Door Frame Detail
Indoor
Door Frame supporting the canopy as well as the door
Outdoor
■ Opposite Side
■ Example (Option)

## Slide 10
MMR Modularization
5
Removable Cladding Detail
■ Reference Details
■ Concept Modeling
■ Lifting Lug
Removable Area
Removable Area

## Slide 11
7. Steel module connection detail evaluation : by Jang and Kim
9. Door, Window, Louver fixing method : by Kim and Jang
11. Panel fixing details : by Kim and Jang
12. Removable wall panel details : by Kang and Jang

## Slide 12
MMR Modularization
5
Door, Window, Louver fixing Detail
■ Reference Details
■ Concept Modeling