## 적용규칙A
[Family 작성 및 적용 규칙]
No. | Item | 협력사 작업 기준 (협력사 배포) -실행 | 본사, 팀 내부 기준 (실행) | 본사, 팀 내부 기준 (입찰/기본) | 비고
1 | General
1.1 | Family Name : 모델 Family Name - 패밀리 리스트 Family Name | ▶ 모델상의 Family Name - Family List의 Family Name 반드시 일치 * Family Name 추가 또는 변경 필요 시, HEC 담당자의 검토 및 승인 필수 | ▶ 모델상의 Family Name - Family List의 Family Name 반드시 일치 * BIM협력사가 Family List의 Family Name 추가 또는 변경 필요 시, 반드시 HEC BIM Manager의 검토 및 승인 필수 | ▶ 실행과 동일 | Manual 2.4 참조
1.2 | Family List, Family Name 명명 체계 | ▶ HEC Family List의 Family Name 명명 체계 준수 - Lv1 : Family Category 1단계 - LV2 : Family Category 2단계, Standard Hierarchy - Lv3 : □ / 팀 표준 설계 정보 (Large) - Lv4 : ▶ / 팀 표준 설계 정보 (Middle, Small) Lv5 : 동일 WM Group - Lv6 : 사용자 추가 정보 ※ Lv5까지의 Full Family Name 반드시 준수 | ▶ Family Name은 L1 ~ L6 분류 체계 적용 - Lv1 : Family Category 1단계 - LV2 : Family Category 2단계, Standard Hierarchy - Lv3 : □ / 팀 표준 설계 정보 (Large) - Lv4 : ▶ / 팀 표준 설계 정보 (Middle, Small) Lv5 : 동일 WM Group - Lv6 : 사용자 추가 정보 ※ Lv5까지의 Full Family Name 반드시 준수 | ▶ 실행과 동일 | Manual 2.4 참조
1.3 | Family Name - 부재명 | ▶ 부재명 : Revit 모델 부재명 - 도면, 계산서 부재명 일치 - Type Mark (Type Parameter) - Mark (Instance Parameter) 에 부재명 적용 ▶ Family Name Lv6에 부재명 반영 | ▶ 부재명 : Revit 모델 부재명 - 도면, 계산서 부재명 일치 ▶ Family Name Lv6, Type Mark (Type Parameter)에 부재명 반영 | ▶ 실행과 동일
1.4 | 구조패밀리 : 마감패밀리 분리 | ▶구조부재와 마감부재는 반드시 구분 | ▶구조부재와 마감부재는 반드시 구분 *예외) Room패밀리가 적용되지 않는 구조부재의 Painting은 구조패밀리에 포함 - 외벽의 외부면 페인트 - Trench/Pit의 내부 벽, 바닥 페인트 | ▶구조부재+마감부재 ⇒ 구조부재만 모델링 *예) - Conc. Wall (T200)+마감 Wall ⇒ Conc. Wall (T200) - Roof Slab(T150) + Roof 마감 ⇒ Roof Slab(T150) | Manual 2.4 참조
1.5 | Room 패밀리 : 객체 패밀리 분리 기준 | ▶ Room 패밀리 : 최종 마감만 반영 * Interior Finish Schedule 상의 '바탕(Base)' - '마감(Finish)' 중 '바탕'을 제외한 '마감'만 Room Family에 반영 | ▶ Room 패밀리 : 최종 마감만 반영 * 최종마감 : "BIM 팀 표준 설계 정보"의 Finish Style Name * Interior Finish Schedule 상의 '바탕(Base)' - '마감(Finish)' 중 '바탕'을 제외한 '마감'만 Room Family에 반영 | ▶ 실행과 동일 | Manual 2.4 참조
1.6 | Family Group 구분 : 모델링 |  | ▶ 실행 Family Group - F1 Group : 객체 Family - R1 Group : Room Family - F2 Group : F1 - R1 사이의 Family ▶ “BIM 팀 표준 설계 정보”의 Family Group 구분 및 실행/입찰 구분 기준 적용 | ▶ 입찰 Family Group - F1 Group : 객체 Family - R1 Group : Room Family ▶ 입찰에서는 F1, R1 Group 만으로 최대한 단순화하여 모델링 ▶ “BIM 팀 표준 설계 정보”의 Family Group 구분 및 실행/입찰 구분 기준 적용 | Manual 2.4 참조
1.7 | Family Group 구분 : 물량 산출 (Family List) |  | ▶ 실행 Family List : F1, F2, R1에 대한 각각의 Family List 작성 및 물량 산출 | ▶ 입찰 Family List : F2 Group에 해당하는 물량은 F1/R1 Group의 Family List에서 반영하여 산출
1.8 | 공유매개변수 | ▶ HEC가 제공하는 공유매개변수 적용 | ▶ 팀 기준 공유 매개변수 적용 필수 -추가 또는 변경 필요시, BIM Manager의 검토 필수 -외주 업체 적용 필수 | ▶ 실행과 동일
1.9 | 물량 산출 필수 매개변수 | ▶ 하기 매개변수에 대한 값은 물량산출과 연계되므로, 해당 Family 의 매개변수 값은 모델상에서 자동 산출 되어야함 | ▶ 하기 매개변수에 대한 값은 물량산출과 연계되므로, 해당 Family 의 매개변수 값은 모델상에서 자동 산출 되어야함 | ▶ 실행과 동일 | *Manual 3.1 참조 * Family List / 산출기준 / 모델 Parameter(회색음영부분)
| Family Category | 매개변수 | 매개변수
| Room | Area, Perimeter | Area, Perimeter
| Floor | Volume, Area, Perimeter | Volume, Area, Perimeter
| Roof | Area (Gutter : Length) | Area (Gutter : Length)
| Wall | Volume, Area | Volume, Area
| Structural Foundation (System Family) | Volume, Area, Perimeter, Thickness * Elevation at Bottom Survey : GL=0 를 Survey Level Z=0 로 Setting | Volume, Area, Perimeter, Thickness * Elevation at Bottom Survey : GL=0 를 Survey Level Z=0 로 Setting
| Structural Foundation (Load Family) | Volume, Width, Length, Foundation Thickness * Elevation at Bottom Survey : GL=0 를 Survey Level Z=0 로 Setting | Volume, Width, Length, Foundation Thickness * Elevation at Bottom Survey : GL=0 를 Survey Level Z=0 로 Setting
| Structural Column (RC) | Volume, Width(기둥 가로), Length(기둥 세로), Length(기둥길이) | Volume, Width(기둥 가로), Length(기둥 세로), Length(기둥길이)
| Structural Column (Steel) | Normal Weight, Perimeter, Length | Normal Weight, Perimeter, Length
| Framing (RC) | Volume, Width(보 폭), Height(보 Depth), Length(보길이) | Volume, Width(보 폭), Height(보 Depth), Length(보길이)
| Framing (Steel) | Normal Weight, Perimeter, Length | Normal Weight, Perimeter, Length
| Ceiling | Area | Area
1.10 | 모델 Material Browser에서 Material 지정 | ▶주요물량을 Revit 상에서 즉시 확인하기 위해 주요물량에 대한 Material 지정 : Revit Schedule - Material Takeoff 기능 활용 - RC : Concrete 강도, UG/AG 구분 적용 - Steel : 재질 구분 적용 | ▶주요물량을 Revit 상에서 즉시 확인하기 위해 주요물량에 대한 Material 지정 : Revit Schedule - Material Takeoff 기능 활용 - RC : Concrete 강도, UG/AG 구분 적용 - Steel : 재질 구분 적용 | ▶ 실행과 동일 | 각자 Study
1.11 | Steel Family List 작성 규칙 - Structural Columns, Structural Framing | ▶ Steel Family의 Lv.4 : 국가별 모양, 치수 규정 (KS D 3502, ASTM A6 등) ▶ Steel Family의 Lv.5 : WM에 따라 Heavy, Medium, Light, Purlin & Girth 구분 ▶ Steel Family의 재질 구분이 필요시 Lv.6 또는 Revit Material Browser에서 반영 | ▶ Steel Family의 Lv.4 : 국가별 모양, 치수 규정 (KS D 3502, ASTM A6 등) ▶ Steel Family의 Lv.5 : WM에 따라 Heavy, Medium, Light, Purlin & Girth 구분 ▶ Steel Family의 재질 구분이 필요시 Lv.6 또는 Revit Material Browser에서 반영 | ▶ 실행과 동일
1.12 | Steel 물량 산출 | ▶ Steel 부재 Family는 하기 매개변수에 대한 값 반영 : Normal Weight, Perimeter | ▶ Family List를 이용한 물량 산출 - 중량 : 철골Family 작성시 입력된 Nominal Weight (kgf/m) x Length - 도장 : 철골Family 작성시 입력된 Perimeter (m2/m) x Length ▶ Revit 자동 산출 (Schedule, Material Take off 기능) - 중량 : Revit 자동 산출 V x Material Density x Cut Length - 도장 : Revit 자동 산출 Material Area | ▶ 실행과 동일
1.13 | Structural Foundations : "Elevation at Bottom" | ▶ GL=0 를 Survey Level Z=0 로 Setting | ▶ GL=0 를 Survey Level Z=0 로 Setting | ▶ 실행과 동일
1.14 | 대물량 상시 검토 -Concrete -Steel | ▶ Concrete, Steel 구조부재 Family : Family Type 매개변수 항목인 'Type Comment'에 하기 기준으로 입력 -Concrete : CV-AG, CV-UG -Steel : SW-MA, SW-SE | ▶ Materior Takeoff 활용 ▶ 팀표준 Template에 Setting된 하기 Schedule 양식 준수 -Quantity(Concrete)- Material Takeoff -Quantity(Steel)- Material Takeoff ▶ Family Type 매개변수 항목인 'Type Comment'에 하기 기준으로 입력 -Concrete : CV-AG, CV-UG -Steel : SW-MA, SW-SE | ▶ 실행과 동일
1.15 | 물량산출 수식을 사용하지 않고 직접산출한 물량 값 적용시 |  | ▶ 물량산출식 셀에 산출값 직접입력 -반드시 문자 형식 적용 예) '= 100 결과 값 100 '= 25*3 결과 값 75
2 | 설계 기본 정보 입력
2.1 | 입찰/기본설계용 Template의 Key Schedule ("BIM 팀 표준 설계 정보" 적용) |  |  | ▶ 입찰/기본설계용 Template의 Key Schedule - A_Key Schedule for Interior Finish (Floor) - A_Key Schedule for Interior Finish (Skirt) - A_Key Schedule for Interior Finish (Wall) - A_Key Schedule for Interior Finish (Ceiling) - E_Key Schedule for Wall Style - F_Key Schedule for Roof Style - G_Key Schedule for Door Style - H_Key Schedule for Window Style ▶ Revit 입력 편의를 위해 "BIM 팀 표준 설계 정보"를 Key Schedule로 작성한 것 임.
2.2 | 입찰/기본설계 모델의 정보 입력 | ▶ HEC에서 제공하는 입찰/기본설계 모델의 Schedule 정보 반영 - 01_Room Schedule - 02_Interior Finish Schedule - 03_Wall Schedule - 04_Roof Schedule - 05_Door Schedule - 06_Window Schedule |  | ▶ 입찰/기본설계용 Template의 Key Schedule을 활용하여 모델링 반영 및 하기 작성 - 01_Room Schedule - 02_Interior Finish Schedule - 03_Wall Schedule - 04_Roof Schedule - 05_Door Schedule - 06_Window Schedule
2.3 | 실행 모델링 Template 선택 | ▶ 1) HEC 제공 입찰/기본설계 모델(LOD200)에서 LOD350으로 Develop or ▶ 2) HEC 제공 입찰/기본설계 모델(LOD200)의 정보만 참조하여 협력사의 자체 New Template에서 LOD350 모델 작성 * 협력사의 자체 판단에 따라 1) or 2) 효율적 방법 선택
3 | Room Family
3.1 | Room 마감 모델링 대상 | ▶ 다음 Room 마감은 별개의 객체 Family 적용 - Wall의 Plaster - Tile - Slope용 Screed (Tile Bonding용 Screed : X) - Raised Floor - Suspended Ceiling - 바닥 Screed ▶ 이외에도 도면 표현상 필요 할 경우, 별개의 객체 Family 적용
3.2 | Room 마감 물량 산출 기준 |  | ▶ 모든 최종마감 Tile, Suspended Ceiling, Raised Floor, Paint은 Room Family List에서 물량 산출 | ▶ 실행과 동일
3.3 | Interior Finish Schedule 도면 작성 기준 | ▶ Interior Finish Schedule 도면 : 반드시 Room Family에 입력된 정보를 이용하여 작성 ▶ Interior Finish Schedule 도면 양식 : '바탕(Base)' - '마감(Finish)' 으로 구분하여 작성
3.4 | Room 패밀리 마감 정보 | ▶ Room 패밀리 : 최종 마감만 반영 * Interior Finish Schedule 상의 '바탕(Base)' - '마감(Finish)' 중 '바탕'을 제외한 '마감'만 Room Family에 반영 | ▶ Room 패밀리 : 최종 마감만 반영 - Interior Finish Schedule 상의 '바탕(Base)' - '마감(Finish)' 중 '바탕'을 제외한 '마감'만 Room Family에 반영 * 최종마감 : "BIM 팀 표준 설계 정보"의 Finish Style Name 참조 | ▶ 실행과 동일 | *Manual 3.1 참조
3.5 | Room 패밀리 마감 물량 산출 |  | ▶ Room 최종 마감은 Room Family List에서 산출 ▶객체 패밀리 : Room 패밀리에 반영된 최종 마감 WM 제외 | ▶ 실행과 동일
3.6 | Room에 해당하지 않는 Trench, Pit 등의 패밀리 구성 | ▶ Trench, Pit 등 Room이 적용 되지 않는 객체 - (바닥 Floor + 바닥 마감) 의 복합패밀리로 작성 - (Wall + Wall 내/외부 마감) 의 복합패밀리로 작성 | ▶ Trench, Pit 등 Room이 적용 되지 않는 객체 - (바닥 Floor + 바닥 마감) 의 복합패밀리로 작성 - (Wall + Wall 내/외부 마감) 의 복합패밀리로 작성 | ▶ 실행과 동일
3.7 | 공유매개변수 H_Room H or CH | ▶ Room 패밀리에 공유매개변수 "H_Room H or CH" 적용 : 반드시 반영하고 해당 Room의 층고를 반드시 수동 입력한다. | ▶ Room 패밀리에 공유매개변수 "H_Room H or CH" 적용 : 반드시 반영하고 해당 Room의 층고를 반드시 수동 입력한다. | ▶ 실행과 동일
3.8 | Room Perimeter 값 적용 |  | ▶
4 | Floor
4.1 | Deck Slab |  | ▶ Deck Slab : V = Default Thickness x Area로 계산 되므로 모델에서 평균두께 입력 : Deck 골을 고려한 가중평균 두께 => Family Parameter Thickness에 입력 | ▶ 실행과 동일 | 물량산출시 Revit 자체 산출 Volumn 사용
4.2 | Painting 마감 + 슬라브구체 페밀리 분리 |  | ▶ Slab에 적용된 Painting - F1 Group : Concrete Slab ⇒ Floors - R1 Group : Floor Paint ⇒ Room Floor Finish |  | * Room 바닥 마감이 다양하더라도 전체층에 대한 동일 Floor Family 적용 할 수 있다.
4.3 | Tile 마감은 슬라브구체와 구분 별도 페밀리 적용 |  | ▶ 바닥 Tile 마감 (Screed+Tile) - F1 Group : Slab - F2 Group : Tile (For 도면 표현) - R1 Group : Tile (물량 산출)
4.4 | Roof Concrete Slab | ▶Roof 구조체 : Floor 패밀리 적용 | ▶Roof 구조체 : Floor 패밀리 적용 |  | * Roof Slab를 Floor로 적용한 이유 - 철근 모델링을 위해서는 Strucutre Category에서 모델링해야 함
5 | Roof
5.1 | Concrete Roof 의 Slab / Finish 패밀리 구분 | ▶Roof 마감과 구조체는 패밀리 분리 - Roof Finish : Roof 패밀리 적용 - Roof Concrete Slab : Floor 패밀리 적용 | ▶Roof 마감과 구조체는 패밀리 분리 - Roof Finish : Roof 패밀리 적용 - Roof Concrete Slab : Floor 패밀리 적용
5.2 | Roof Finish 입찰 : 실행 |  | ▶ 모델링 : Roof Slab - Roof Finish 각각 패밀리 작성 ▶ 물량 산출 : Roof Slab - Roof Finish 각각의 패밀리 리스트에서 산출 | ▶ Roof Slab - Roof Finish 각각 패밀리 작성 하지만, Roof Finish 패밀리는 Roof Finish물량산출을 위한 용도이므로 물량산출 면적 매개변수만 활용 가능하도록 단순 모델링
5.3 | Roof Fnish 방수 마감 |  | ▶Roof Finish 방수 마감 물량 - 방수마감의 Parapet에 감아 올린 물량은 '산출기준' 수식에 반영하여 산출 | ▶ 실행과 동일
5.4 | Roof Slope Mortar | ▶ Roof 마감 Slope 모델링 : 모델링시 도면 표현을 위해 Slope 반영 (구체 Slope일 경우 Floor패밀리로 작성된 Roof Slab에서 적용) | ▶Roof Sloop Mortar 물량 -설계자가 평균두께 Ts, Tp 값을 산정하여 Slope Mortar 물량 수식에 반영 : 산출기준 Roof 참조 ▶구체구배 : Floor 패밀리 Sloop모델링에 따른 V 자동 산출 | ▶ 모델링 : Sloop 반영 선택 ▶ 물량 : 실행과 동일
6 | Wall
6.1 | Skirt | ▶ 도면 표현상 필요하지 않은 경우, No Modeling - Room Family에 Skirt 정보 입력 | ▶ 도면 표현상 필요하지 않은 경우, No Modeling - Room Family에 Skirt 정보 입력
6.2 | Concrete + 마감 Wall | ▶ 실행모델 : 콘크리트 Wall - 마감 Wall (조적, Gypsum 등) Family 분리 | ▶ 실행모델 : 콘크리트 Wall - 마감 Wall (조적, Gypsum 등) Family 분리
6.3 | Exterior Wall Family 구성 |  | ▶ 입찰 - F1 Group : R1 제외한 전체 * Concrete Wall 인 경우, RC물량산출 두께와 동일한 두께 적용 - R1 Group : Room 최종 마감 ▶ 실행 - F1 Group : R1, F2 제외한 전체 - R1 Group : Room 최종 마감 - F2 Group : 외벽 내부 Plaster, 외벽 내부 Tile
6.4 | Interior Wall Family 구성 |  | ▶ 입찰 - F1 Group : R1 제외한 전체 * Concrete Wall 인 경우, RC물량산출 두께와 동일한 두께 적용 - R1 Group : Room 최종 마감 ▶ 실행 - F1 Group : R1, F2 제외한 전체 - R1 Group : Room 최종 마감 - F2 Group : Plaster, Tile
6.5 | Parapet의 Roof방수 누름 Brick |  | ▶Parapet의 Roof방수 누름 Brick : 별도 페밀리 모델링 | ▶Parapet의 Roof방수 누름 Brick : Parapet Wall Family에 Brick WM 반영
6.6 | 외측면에 노출된 Conc. 기둥, 보의 Paint 물량을 Wall에서 할증으로 반영 |  | ▶ 외벽의 외측면 Paint 물량 할증 - 외측면에 노출된 Conc. 기둥, 보의 Paint 물량을 Wall에서 할증으로 반영 ▶ 외부 보, 기둥에서는 외부면 Paint 산출 않함 | ▶ 실행과 동일
7 | Structural Foundation
7.1 | Lean Concrete 입찰 : 실행 | ▶ 실행 모델링 : Foundation과 별개로 Lean Concrete 모델링 * Lean : Foundation Slab Category 적용 | ▶ Lean Concrete 모델링 : Structural Foundation 카테고리로 별도 모델링 ▶ 물량 산출 : 기초와 분리된 별도의 Family Name으로 Family List에 추가 : Lean Family에서 하기 물량 산출 - Lean - Base Course, Sub Base Course - PE Sheet | ▶ Lean Concrete 모델링 : 모델링 생략 ▶ 물량 산출 : 해당 기초와 연계하여 기초 Family에서 하기 물량 산출 - Lean - Base Course, Sub Base Course - PE Sheet
7.2 | Ditch 모델링 | ▶ Model In-Place 기능을 활용하여 작성 ▶ Structural Foundation Category로 설정 | ▶ Model In-Place 기능을 활용하여 작성 ▶ Structural Foundation Category로 설정 ▶물량 : 다이나모 이용하여 산출 |  | * 슬라브에 Ditch 모델링 형상결합하면 중복 슬라브 물량 제외됨 Ditch *Wall 과 Foundation으로 구분하기 어려운 요소
7.3 | Concrete Pit | ▶ Pit Wall과 Pit 바닥을 구분하여 기본 Family Category 적용 - Pit Wall : Family Category Basic Wall 적용 - Pit 바닥 : Family Category Foundation Slab 적용 | ▶ Pit Wall과 Pit 바닥을 구분하여 기본 Family Category 적용 - Pit Wall : Family Category Basic Wall 적용 - Pit 바닥 : Family Category Foundation Slab 적용
7.4 | Concrete Trench | ▶ Pit Wall과 Pit 바닥을 구분하여 기본 Family Category 적용 - Pit Wall : Family Category Basic Wall 적용 - Pit 바닥 : Family Category Foundation Slab 적용 | ▶ Pit Wall과 Pit 바닥을 구분하여 기본 Family Category 적용 - Pit Wall : Family Category Basic Wall 적용 - Pit 바닥 : Family Category Foundation Slab 적용
7.5 | SOG Slab Mat, Mass Lean | ▶ Structural Foundations / Foundation Slab Category 적용 | ▶ Structural Foundations / Foundation Slab Category 적용
7.6 | SOG Haunch 모델링 |  | ▶Model In-Place 기능 적용 예정 |  | Haunch 모델링 - Slab Edge 기능은 Slab 모서리부에 구속되어 형태 조작이 어려움 - Slab Edge는 생성된 모델에 Parameter 추가되지 않아 WBS 입력 한계
7.7 | Ramp & Pathway Haunch Stoop 모델링 |  | ▶Model In-Place 기능 적용 예정 |  | Hunch 모델링 Slope에 적용 시 측면 적용 불가능 기울기 조절 시 하부면 수평 적용 불가능
7.8 | Slab 두께 변화되는 부분 |  | Dynamo Logic으로 물량 산출 해결 - 상하부 별도 작성한 후 Dynamo 활용하여 산출 |  | Slab 두께 변화되는 부분 - 물량 영향없이 작성할 수 있는 방법
7.9 | Slab 두께 변화되는 부분 lean concrete 적용 |  | Lean 자동생성용 Dynamo Tool 개발중 |  | Slab 두께 변화되는 부분 lean concrete 적용
8 | Structural Columns
8.1 | BasePlate |  |  |  | -Plate or Generic Models ?
8.2 | Anchor Bolt |  |  |  | LOD 350에서 Anchor Bolt 모델링 할지 결정 필요
8.3 | Grout |  |  |  | Generic Models에서 작성시 같은 유형임에도 개별로 생성됨
8.4 | Steel Connection - Add in 우측 링크의 Autodesk Add-in 기능 조사 |  |  |  | https://help.autodesk.com/view/RVT/2023/KOR/?guid=GUID-C6E1D473-1B03-4E6F-9CAE-3354FCAE7790
8.5 | Concrete Column Size에 대한 Family 매개변수명 | ▶Concrete Column Size에 대한 Family 매개변수명은 반드시 하기 이름 적용 - 매개변수명 : Width - 매개변수명 : Depth | ▶Concrete Column Size에 대한 Family 매개변수명은 반드시 하기 이름 적용 - 매개변수명 : Width - 매개변수명 : Depth | ▶ 실행과 동일 | Concrete Column 산출기준 참조
9 | Structural Framing
9.1 | Tie Girder | ▶Family Category : Foundation(X), Structural Framing(O) | ▶ Family Category : Foundation(X), Structural Framing(O)
9.2 | Tie Girder |  | ▶ Family Name의 W, T가 산출식과 일치하도록 해야함
9.3 | Steel Member Family 제작 – Connection 오류 |  |  |  | 국가별 Steel 규격 적용을 위해 Family 생성 (Excel Data 연동) - Steel Connection 관련 오류 발생
9.4 | Steel Member Family 제작 – Connection 오류 |  | Revit 기본 Library 활용 - Connection 생성됨. - 해당 Family를 모체로 Steel Family 생성 |  | 1. 오류-1 : Visibility setting 의 Detail level 조정 2. 오류-2 : Revit 제공 Steel Family 활용하여 해결
9.5 | Steel Family 관련 Stick Symbol 등 적용 |  | Symbolic Line 및 Visility Option을 통해 Detail에 따라 single line으로 나타나게 할 수 있음. (기본 Family Library 활용 시 자동 연계되어 있음.) - Rigid Link, Shear Link 의 경우 Symbol 추가하여 양단 접합부 표현 가능함. |  | Steel Structure 관련 Family 에서 Stick Symbol, Rigid Link 등 활용 방법 -Family 제작 시 적용 방법 -도면 작성 시 view setting 방법
9.6 | Family 작성 시 Profile 활용 |  | Family Parameter와 Profile Parameter를 연동하여 활용 가능 -위 기능을 활용할 시 Profile을 생성하여 다방면으로 사용 가능함. |  | Family Edit에서 Load Profile 사용 시 매개변수도 함께 로드되지 않음. - Type parameter로 조정 불가함
9.7 | Steel Connection Symbol |  | 1. Splice용 Symbol Family 추가 : Cut-back 설정에 따라 폭/길이 변경가능하도록 타입 매개변수 추가 2. Connection Symbol 설정에서 Splice Connection 추가 후 Symbol Family 설정 3. 개별 부재에서 Connection Type 지정 |  | STEEL CONNECTION 관련 : Splice 표현 적용 방법
9.8 | Purlin, Girth용 Bracket 물량 산출 |  |  |  | Steel Connection으로 모델에 나타나지만 어떤 Family Category인지, 물량에 어떻게 반영할지 확인 필요
9.9 | Concrete Beam Size에 대한 Family 매개변수명 | ▶Concrete Beam Size에 대한 Family 매개변수명은 반드시 하기 이름 적용 - 매개변수명 : Width - 매개변수명 : Height | ▶Concrete Column Size에 대한 Family 매개변수명은 반드시 하기 이름 적용 - 매개변수명 : Width - 매개변수명 : Height | ▶ 실행과 동일 | Concrete Beam 산출기준 참조
10 | Doors & Windows
10.1 | 인방 모델링 |  | 인방을 패밀리 요소로 반영하는 것은 가능하나 다소 비효율적인 것으로 판단됨. 따라서, 인방 모델링이 반드시 필요한 경우 별도 모델링 권장됨 |  | 창문 상하부 인방(LINTEL)을 패밀리 요소로 포함 필요
11 | Stairs
11.1 | 철골 STAIR Tread & Riser |  | Grating Pattern 가진 재질을 입혀서 Grating Tread로 표현하고, Riser는 아래와 같이 생략가능함 |  | -Assembled Stair의 Grating Tread 적용불가 -Riser 미적용 불가 -Stair 물량 산출 방안
11.2 | RC STAIR Tread & Riser |  | 유형편집 – Run Type – Tread / Riser Material에서 원하는 재료지정 |  | - Cast-in-place stair(Monolithic stair)의 Tread 및 Riser 재료지정 불가 (Paint / Tile 등) -Stair 물량 산출 방안
12 | Generic Model
12.1 | DOWNSPOUT 모델링 패밀리 없음 |  | 신규패밀리 생성하고, Label 및 Formula 조합으로 Downpipe 및 Bracket 형상구현 가능 Reference Line을 기준으로 Sweep Path를 지정하고, Step 및 Bracket Distance는 간단한 산수의 조합으로 길이와 연동되도록 만들수 있다. 복잡한 형상도 원리는 이와 마찬가지임 |  | 업체 BIM모델(BIMobject) 활용하여 패밀리 Import 옵션(Bracket 개수/길이, Head유무, Offset 길이)에 따라 Customizing (작성방법 심화학습)
12.2 | Ladder : CAGE 및 SUPPORT |  | 신규패밀리 생성하고, Label 및 Formula 조합으로 Cage Ladder 형상구현 가능 Reference Line을 기준으로 Sweep Path를 지정하고, Step은 간단한 산수의 조합으로 길이와 연동되도록 만들수 있다. 복잡한 형상도 원리는 이와 마찬가지임 |  | 업체 BIM모델(BIMobject) 활용하여 패밀리 Import 옵션(Bracket 개수/길이, Handrail, Cage여부)에 따라 Customizing 가능
13 | 기타
13.1 | DOOR 상부 캐노피(RC) 패밀리 생성 필요 |  | ▶ 신규패밀리 생성(카테고리 – Structural Stiffener) 길이/폭/돌출길이/두께 등 옵션화 > 유형별 옵션조정

## 적용규칙B
Concrete 체적 - Revit 자동산출 기준
Family | 형상결합 (Join) 기준 | 형상결합 (Join) 기준 | Concrete Volume (Revit 자동산출) | 팀표준 철근비
Column |  |  | V = Width(W) x Depth(D) x Length(H) | RE = 0.30
Beam |  |  | V = Width(W) x Depth(D) x Cut Length | RE = 0.14
Slab |  |  | V = Area(A) x Thickness(T) | Slab RE = 0.10 SOG RE = 0.09
Concrete Wall |  |  | V = Area x Width | RE = 0.12
Foundation : Single, Mat |  |  | V = Width x Length x Foundation Thickness | RE = 0.12
Wall - Floor
Material Takeoff/Schedule : 매개변수를 이용한 산출식 적용 사례
| Formula Name | Formula
1 | Steel : Weight(Ton) | (Material: Volume / 1 m³) * (Material: Unit weight / 9800 Pa/m) | (1 Pa = N/m2) (1 kg = 9.807 N) |  | *Material: Volume : m³ *Material: Unit weight : kN/m³
2 | Concrete : Re-Bar(Ton) | (Material: Volume / 1 m³) * (H_Re Bar Ratio) |  |  | *Material: Volume : m³
3 | Concrete Index | (Material: Volume / 1 m³) / (H_Building Area / 1 m²)
Beam
Slab
D
WB
Column
Slab
H
W
Slab
Beam
Column
Plan
W (X-방향)
D
Beam
Plan
Slab
Plan
Beam Plan
Column
Plan
Column
Elevation
Concrete Wall
Elevation
Area (A) (보, 기둥 제외 면적)
Beam Elevation
R4-적용규칙B 추가
WALL
Slab
Section
Slab

## 유의사항
물량산출 Dynamo Tool 사용을 위한 Family List 작성 유의 사항
<카테고리 별 시트>
자동 연동 구간 (사용자 수정 자제)
사용자 작성 필요구간
사용자 검토 필요구간
0 | 공통 | 어떤 시트의 어떤 셀이라도, '#' 표기가 들어있는 항목은 엑셀 내 자동 입력을 위해 작성된 표식이므로 임의 삭제 절대 금지 | 8.Doors, 9.Windows 시트의 I열 참조
1 | 칼럼 제목 변경 금지 및 열 추가 자제 | 열 추가 가능하나 기존 헤더 명과 중복되지 않도록 작성
2 | 표준 체계 구성명 | [Family Name 분류 체계 Lv3 & Lv4] □ 팀 표준 분류 (Large) / ▶ 팀 표준 분류 (Middle, Small) 'Family_표준_구성도 시트' 와 일치해야 함. 사용자가 신규 그룹 생성시, '표준구성도 시트'에 반영 요망 | STP-PL-EN-AR-PP-001의 2.3항 참조
3 | 표준 구성번호 | [Family Name 분류 체계 Lv5] - 번호 해당 행의 F 열 값과 'Family_표준_구성도 시트' 상의 타입 명들을 비교하여, 일치하는 항목의 번호가 자동으로 기입됨(사용자 수정 자제) * 만약 사용자가 기존타입을 복사하여 신규 타입을 생성하였을 경우에는 해당 항목이 비어있게 되며, 번호를 부여하고 싶다면 표준 구성도 상에 신규 생성한 표준 타입명을 추가한뒤, 번호를 할당해 주어야 함.
4 | Q’ty Cal Type Tag 입력 | 산출기준 태그 입력 (입력시 15번 항목으로 연동되어 태그 설명 자동 기입) | "산출기준 시트" 참조
5 | 표준 타입명 | [Family Name 분류 체계 Lv5] - 이름 * 대소문자 구분 * 'Family_표준_구성도 시트' 와 일치해야 함. * Family Type명에는 Only Under Bar(_)만 적용, Dash(-) 적용하지 말것 (철골은 예외)
6 | 타입 공통 WorkMaster | * Lv5 표준타입이 공통으로 가져야 하는 WM 항목들을 규정. * 프로젝트를 위해 WM 조합의 별도 타입이 필요하다면 신규타입 추가만 가능. 기존의 팀표준 타입을 변경하는 것은 자제. * 추가한 타입은 프로젝트 종료시 BIM 운영 팀으로 변경사항 고지 필. | 예를 들어 예시 그림의 "H_SF_AR_S18_Shallow Fdn_Bitumen" 이라는 타입에, 2가지 별도 WM이 추가된 조합이 필요하다면, 해당 타입의 내용을 수정하지 말고, 타입 전체를 행 복사 한 뒤, "H_SF_AR_S18_Shallow Fdn_Bitumen_onlyPJT" 와 같이 새로운 이름의 타입을 생성하는 것을 권유.
7 | Guage Code | 동일 Work Master Code 내 Spec에 따른 하위 분개 필요시 예) A03AD032-00002 (Concrete Cylinder Strength 20 Mpa < F'c <25Mpa)인 경우, A03AD032-00002 A(Guage Code) F'c = 21 Mpa B(Guage Code) F'c = 24 Mpa
8 | WorkMaster 별 Description(실제 적용 스펙) | * WM 항목별 실 적용 스펙 기입 * 범위형 WM 항목의 경우에는 실제 spec 값 기입 필수
9 | 입찰_물량산출식 | 물량산출 모드가 '입찰'일 경우 WM 항목별로 참조하게 될 다이나모 수식 계산식. * 실행과 달리 모델링 되지 않는 항목들에 대한 WM 할당이 이루어지기 때문에 실행 물량산출식과 항목 구성이 다를 수 있음. | ** 보, 기둥의 경우: - 내측 페인트 물량은 룸 에서 할증을 통해 계산, - 외측 페인트 물량 외측페인트 WM 항목 포함된 분개 타입을 통해 계산
10 | 실행_물량산출식 | 물량산출 모드가 '실행'일 경우 WM 항목별로 참조하게 될 다이나모 수식 계산식. * 입찰에서 모델링 하지 않는 부재들도 모델링이 되므로 입찰 물량산출식과 항목 구성이 다를 수 있음. | ** 보, 기둥의 경우: - 내측 페인트 물량은 룸 에서 할증을 통해 계산, - 외측 페인트 물량 외측페인트 WM 항목 포함된 분개 타입을 통해 계산
11 | Building Tag | Building Tag에 건물명 기입은 선택사항. * 물량산출에 참조되는 데이터는 아님. 프로젝트 전체 패밀리리스트 취합 시의 관리를 위한 입력항목
12 | 실제 적용패밀리 타입 명 | 레빗 모델링 내의 '프로젝트 브라우저' 혹은 '[H_PAB.RT.G1]_Revit RVT Summary.dyn'을 통해 실행된 RVT Summary 웹 페이지 에서 확인할 수 있는 모델링에 실제 적용된 패밀리 타입 명을 입력하는 구간
13 | 실제 적용패밀리 타입 별 단독 WM | 표준 타입의 공통 WM 항목 이외에, 실제 적용 패밀리 타입 별로 개별 WM 할당이 필요한 경우에만 입력 (2개 이상의 입력이 필요한 경우 패밀리 타입 명 중복 입력을 통해 할당)
14 | 산출기준 태그 설명 | 산출타입 설명(only 검토용)
15
<산출기준 시트>
0 | 공통 | 어떤 시트의 어떤 셀이라도, '#' 표기가 들어있는 항목은 엑셀 내 자동 입력을 위해 작성된 표식이므로 임의 삭제 절대 금지 | 8.Doors, 9.Windows 시트의 I열 참조
1 | Q'ty Calc Type Tag | 카테고리마다 부재의 종류별로 물량 산출에 참여하는 항목들을 규정하는 번호체계 부여 | 각 카테고리 시트의 E열에 해당
2 | 산출 타입 별 전체 수식 | 각 타입별로 사용된 모든 수식을 모아서 기입. 여기에 등장하는 약자중 우측 '산출수식 약자' 항목에 없는 것이 있어서는 안됨
3 | 산출수식 약자
4 | 수동 입력 값
5 | Parameter
6 | <물량Param> Sheet상의 항목중, 물량산출 단위가 개수일 경우(산출수식약자가 Q인 항목) | Q 항목의 입력값은 - 페밀리 1개가 1개의 물량으로 산출시에는 "1" 입력 - 페밀리 1개당 2개(필요개수)의 물량으로 산출시에는 "2(필요개수)" 입력 ex) Base Plate Family 1개에 Anchor Bolt가 4개 인경우, BasePlate 수량은 Q=1 Anchor Bolt 수량은 Q=4
7 | <물량Param> Sheet상의 '구분'의 명과 해당 Sheet의 명칭 동일해야 함. | <물량Param> Sheet상의 '구분' : "1.Floors" 는 Sheet명 "1.Floors" 일치해야함 - 띄어쓰기, 대소문자, 철자 일치
3
1
"표준 타입명"
"표준 체계 구성명"
"표준 구성번호"
↑
"산출타입태그"
"실적용패밀리타입명"
"실적용패밀리 only WM"
(필요 시에만 기입)
"타입 공통 WM"
"WM 상세스펙"
"산출타입 명"
2
4
5
6
8
9
7
10
12
14
13
11
"빌딩태그"
↘
1
2
3
4
5

## 회의내용(임시)
2024.05.21 | 1 | 1. 대물량 상시 검토 -Concrete -Steel | Closed | 적용규칙A, 1.14
| 2 | 2. Room Perimeter 값 적용 - 강한호 |  | 적용규칙A, 3.8
| 3 | 3. 형상결합 : Wall - Floor Case 추가 | Closed | 적용규칙B, Wall-Floor
2024.05.23 | 1 | Steel Family 속성값 확인 Teams / 링크 : 지은호 작업 파일 - Column : 강한호 - Beam : 박진영
| 2 | 입찰용 Pit, Trench, Sump 모델 및 Family List - Pit : 강한호 - Trench : 배중혁 - Sump : 권준석 |  | 적용규칙A, 7.2~7.4
| 3 | 헌치 구조물 모델링 및 Form물량 산출 팀 기준 정리 : 강한호 - Floors Slab Edge / ▶ Edge : 삭제 - Structural Foundations 4.1.1.6 ▶ SOG Slab Edge : 기본적으로 Slab Edge는 Floor 카테고리에 속함. (RVT summary도 마찬가지) 토공물량이 관계되는 케이스가 많으므로 공통 WBS에 토공물량 포함시켜야 함. : Slab Edge 객체와 연계된 Profile 매개변수를 찾고, Profile 정보에서 다시 Height(Thickness) 매개변수를 추출함. 이를 활용하여 Length x Thickness로 Form 물량산출 4.1.1.7 ▶ Stoop, Pathway with Haunch : 기존 Load Family는 삭제하고, SOG 패밀리를 수정하여 Stoop, Pathway 용으로 표준템플릿 수정 예정 |  | 적용규칙A, 7.6~7.9
| 4 | Stair 물량 산출 방안 - Concrete Stair : 박진영 - Steel Stair : 강한호 : Steel Stair Template 활용. Dynamo 물량산출에는 문제없으나, Revit Material Takeoff시 해당 부재 누락됨.
| 5 | Suspended Slab 타입 추가
| 6 | ACC 활용 생산성 향상
| 7 | ACC 사용자 지침
| 8 | Equipment pad 용 family type 추가
Pit wall 부재 옆면 (두께 옆면) paint & 거푸집 물량 누락됨
2024.05.30 | 1 | Pit Wall 측면 Bitumen 및 Form 물량 누락 - 권준석
| 2 | Door 면적 수량 미산출 (E-Space는 자동산출됨) - 권준석
| 3 | Grating 객체 인식불가 (Dynamo 오류?) - 배중혁
| 4 | Slab 측면 Protective Coating 누락 - 배중혁
| 5 | Sample Model(Pit, Trench, Sump)을 팀표준 Template에 업데이트 - 강한호

## Family_Name_협력사
| [플랜트건축팀 Family 구성도]- For 협력사 |  |  | 바로가기
|  | ※ Lv5까지의 Full Family Name 반드시 준수 |  | 0.Room | B11 | 1.Floors | B20 | 2.Roofs | B127 | 3.Walls_Ext | B215 | 3.Walls_Int | B365
|  |  |  | 0.Room |  | 1.Floors |  | 2.Roofs |  | 3.Walls_Ext |  | 3.Walls_Int
|  | ※ Lv6 : 사용자 추가 정보는 Family Name Lv6 에 반영 |  | 4.St_Fdn | B456 | 5.St_Col | B551 | 6.St_Framing | B673 | 7.Ceilings | B925 | 8.Doors | B944
|  |  |  | 4.St_Fdn |  | 5.St_Col |  | 6.St_Framing |  | 7.Ceilings |  | 8.Doors
|  |  |  | 9.Windows | B1181 | 10.Stairs | B1343 | 11.Railings | B1362 | 12.Generic | B1375 | 13.Manual_Input | B1436
|  |  |  | 9.Windows |  | 10.Stairs |  | 11.Railings |  | 12.Generic |  | 13.Manual_Input
| No | Category | Project Use
0.Room
| No |  | Project Use
| 0.1 | Basic Room
| 0.1.1 | □ Room - normal
| 0.1.1.1 | ▶ Rooms
Room : Number / Room : Name
1.Floors
| No |  | Project Use
| 1.1 | Floors
| 1.1.1 | □ Concrete Slab
| 1.1.1.1 | ▶ Concrete Slab
| 1.1.1.1.1 | H_FL_AR_S17_RC Slab
H_FL_AR_S17_RC Slab_T150
| 1.1.1.1.2 | H_FL_AR_S17_RC Slab_S Trowel
H_FL_AR_S17_RC Slab_S Trowel_T150
| 1.1.1.2 | ▶ Roof Concrete Slab
| 1.1.1.2.1 | H_FL_AR_S17_Roof RC Slab
H_FL_AR_S17_Roof RC Slab_T150
| 1.1.1.3 | ▶ Turbine Top Deck Slab
| 1.1.1.3.1 | H_FL_AR_S17_STG Top Slab
H_FL_AR_S17_STG Top Slab_T2000
| 1.1.1.4 | ▶ Concrete Deck Slab
| 1.1.1.4.1 | H_FL_AR_S17_RC Deck Slab
H_FL_AR_S17_RC Deck Slab_T200
| 1.1.1.4.2 | H_FL_AR_S17_RC Deck Slab_S Trowel
H_FL_AR_S17_RC Deck Slab_S Trowel_T200
| 1.1.1.5 | ▶ Roof Concrete Deck Slab
| 1.1.1.5.1 | H_RF_AR_S17_Roof RC Deck Slab
H_RF_AR_S17_Roof RC Deck Slab_T200
H_RF_AR_S17_Roof RC Deck Slab_T200_Slope
| 1.1.2 | □ Checkered / Grating
| 1.1.2.1 | ▶ Grating Floor
| 1.1.2.1.1 | H_FL_AR_S05_Grating
H_FL_AR_S05_Grating_T32
| 1.1.2.2 | ▶ Removable Grating Floor
| 1.1.2.2.1 | H_FL_AR_S06_Removable Grating
H_FL_AR_S06_Removable Grating_T32
| 1.1.2.3 | ▶ Checkered Plate Floor
| 1.1.2.3.1 | H_FL_AR_S07_CHK PL
H_FL_AR_S07_CHK PL_T6
| 1.1.3 | □ Finish
| 1.1.3.1 | ▶ Tile
[Ceramic Tile]
| 1.1.3.1.1 | H_FL_AR_B07_Ceramic Tile
H_FL_AR_B07_Ceramic Tile_150x150xT6
| 1.1.3.1.2 | H_FL_AR_B07_Ceramic Tile_L Waterproof
H_FL_AR_B07_Ceramic Tile_L Waterproof_150x150xT6
| 1.1.3.1.3 | H_FL_AR_B07_Ceramic Tile_Memb
H_FL_AR_B07_Ceramic Tile_Memb_150x150xT6
[Acid Resistant Tile]
| 1.1.3.1.4 | H_FL_AR_B07_Acid R Tile
H_FL_AR_B07_Acid R Tile_150x150xT6
| 1.1.3.1.5 | H_FL_AR_B07_Acid R Tile_L Waterproof
H_FL_AR_B07_Acid R Tile_L Waterproof_150x150xT6
[Vinyl Tile]
| 1.1.3.1.6 | H_FL_AR_B07_Vinyl Tile
H_FL_AR_B07_Vinyl Tile_300x300xT3
| 1.1.3.1.7 | H_FL_AR_B07_Vinyl Tile_Screed
H_FL_AR_B07_Vinyl Tile_Screed_300x300xT3
| 1.1.3.1.8 | H_FL_AR_B07_Anti Static Vinyl Tile
H_FL_AR_B07_Anti Static Vinyl Tile_300x300xT3
[Etc. Tile]
| 1.1.3.1.9 | H_FL_AR_B07_Granite Tile
H_FL_AR_B07_Granite Tile_150x150xT12
| 1.1.3.1.10 | H_FL_AR_B07_Marble Tile
H_FL_AR_B07_Marble Tile_150x150xT12
| 1.1.3.1.11 | H_FL_AR_B07_Stone Tile
H_FL_AR_B07_Stone Tile_150x150xT12
| 1.1.3.1.12 | H_FL_AR_B07_Porcelain Tile
H_FL_AR_B07_Porcelain Tile_150x150xT9
| 1.1.3.1.13 | H_FL_AR_B07_Carpet Tile
H_FL_AR_B07_Carpet Tile_150x150xT9
| 1.1.3.2 | ▶ Mat
| 1.1.3.2.1 | H_FL_AR_B07_Carpet
H_FL_AR_B07_Carpet_900x600xT6
| 1.1.3.2.2 | H_FL_AR_B07_Matwell
H_FL_AR_B07_Matwell_900x600xT6
| 1.1.3.2.3 | H_FL_AR_B07_Entrance Floor Mats and Frame
H_FL_AR_B07_Entrance Floor Mats and Frame_900x600xT6
| 1.1.3.3 | ▶ Raised Floor
| 1.1.3.3.1 | H_FL_AR_B10_Raised Floor_600x600
H_FL_AR_B10_Raised Floor_600x600xH1000
| 1.1.3.4 | ▶ UG Insulation
| 1.1.3.4.1 | H_FL_AR_B07_Ground Insulation
H_FL_AR_B07_Ground Insulation_T50
| 1.2 | Slab Edge
| 1.2.1 | □ Edge
| 1.2.1.1 | ▶ Edge
| 1.2.1.1.1 | H_FL_AR_S17_Thickened
H_SF_AR_S17_Thickened_SOG Edge_600x300
2.Roofs
| No |  | Project Use
| 2.1 | Basic Roof
| 2.1.1 | □ For Concrete Roof
| 2.1.1.1 | ▶ Slope < Insulation < Waterproofing
| 2.1.1.1.1 | H_RF_AR_B06_LW Conc(Slope)_XPS_Memb
H_RF_AR_B06_LW Conc(Slope)_XPS_Memb_T120
| 2.1.1.1.2 | H_RF_AR_B06_Mortar(Slope)_XPS_Memb
H_RF_AR_B06_Mortar(Slope)_XPS_Memb_T120
| 2.1.1.1.3 | H_RF_AR_B06_LW Conc(Slope)_XPS_Memb_Gravel
H_RF_AR_B06_LW Conc(Slope)_XPS_Memb_Gravel_T120
| 2.1.1.2 | ▶ Slope < Waterproofing < Insulation < Protection
| 2.1.1.2.1 | H_RF_AR_B06_Memb_XPS_PE_Protective Conc
H_RF_AR_B06_Memb_XPS_PE_Protective Conc_T120
| 2.1.1.2.2 | H_RF_AR_B06_Memb_XPS_PE_Roof Tile
H_RF_AR_B06_Memb_XPS_PE_Roof Tile_T120
| 2.1.1.2.3 | H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_Geot_Gravel
H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_Geot_Gravel_T120
| 2.1.1.2.4 | H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_Geot_Roof Tile
H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_Geot_Roof Tile_T120
| 2.1.1.2.5 | H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_PE_Roof Tile
H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_PE_Roof Tile_T120
| 2.1.1.2.6 | H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_PE_Protective Conc
H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_PE_Protective Conc_T120
| 2.1.1.3 | ▶ Waterproofing < Insulation < Protection & Slope
| 2.1.1.3.1 | H_RF_AR_B06_Memb_XPS_PE_Protective Conc(Slope)
H_RF_AR_B06_Memb_XPS_PE_Protective Conc(Slope)_T120
| 2.1.1.3.2 | H_RF_AR_B06_Memb_XPS_PE_LW Conc(Slope)
H_RF_AR_B06_Memb_XPS_PE_LW Conc(Slope)_T120
| 2.1.2 | □ Cladding Roof
| 2.1.2.1 | ▶ Sandwitch Panel Roof
| 2.1.2.1.1 | H_RF_AR_B05_Roof Panel Steel Mineral Wool
H_RF_AR_B05_Roof Panel Steel Mineral Wool_T200
| 2.1.2.1.2 | H_RF_AR_B05_Roof Panel Steel Glass Wool
H_RF_AR_B05_Roof Panel Steel Glass Wool_T220
| 2.1.2.1.3 | H_RF_AR_B05_Roof Panel AL Mineral Wool
H_RF_AR_B05_Roof Panel AL Mineral Wool_T200
| 2.1.2.1.4 | H_RF_AR_B05_Roof Panel AL Glass Wool
H_RF_AR_B05_Roof Panel AL Glass Wool_T200
| 2.1.2.2 | ▶ Single Metal Sheet Roof
| 2.1.2.2.1 | H_RF_AR_B05_Roof Single Sheet Steel
H_RF_AR_B05_Roof Single Sheet Steel_T0.7
| 2.1.2.2.2 | H_RF_AR_B05_Roof Single Sheet AL
H_RF_AR_B05_Roof Single Sheet AL_T0.7
| 2.2 | Gutter
| 2.2.1 | □ Gutter - general
| 2.2.1.1 | ▶ Gutter
| 2.2.1.1.1 | H_RF_AR_B07_Gutter_Steel_Eave
H_RF_AR_B07_Gutter_Steel_Eave_W250xH300xT0.7
| 2.2.1.1.2 | H_RF_AR_B07_Gutter_Steel_Valley
H_RF_AR_B07_Gutter_Steel_Valley_W250xH300xT0.7
| 2.2.1.1.3 | H_RF_AR_B07_Gutter_AL_Eave
H_RF_AR_B07_Gutter_AL_Eave_W250xH300xT0.7
| 2.2.1.1.4 | H_RF_AR_B07_Gutter_AL_Valley
H_RF_AR_B07_Gutter_AL_Valley_W250xH300xT0.7
| 2.3 | Fascia
| 2.3.1 | □ Fascia - general
| 2.3.1.1 | ▶ Fascia
| 2.3.1.1.1 | H_RF_AR_B07_Fascia-Flat
| 2.4 | Roof Soffit
| 2.4.1 | □ Soffit - general
| 2.4.1.1 | ▶ Soffit
| 2.4.1.1.1 | H_RF_AR_B07_Soffit
| 2.5 | Sloped Glazing
| 2.5.1 | □ Sloped Glazing - general
| 2.5.1.1 | ▶ Sloped Glazing
| 2.5.1.1.1 | H_RF_AR_B07_Sloped Glazing
3.Walls_Ext
| No |  | Project Use
| 3.1 | Basic Wall -Ext
| 3.1.1 | □ Exterior Wall
| 3.1.1.1 | ▶ Gypsum + Concrete (*Concrete Wall은 별도 Family로 분리)
| 3.1.1.1.1 | H_WA_AR_B02_Ext Wall_1L Gypsum_Mineral Wool
H_WA_AR_B02_Ext Wall_1L Gypsum_Mineral Wool_T135
| 3.1.1.1.2 | H_WA_AR_B02_Ext Wall_1L Gypsum_Glass Wool
H_WA_AR_B02_Ext Wall_1L Gypsum_Glass Wool_T135
| 3.1.1.1.3 | H_WA_AR_B02_Ext Wall_2L Gypsum_Glass Wool
H_WA_AR_B02_Ext Wall_2L Gypsum_Glass Wool_T135
| 3.1.1.1.4 | H_WA_AR_B02_Ext Wall_1L Gypsum_Rigid Ins
H_WA_AR_B02_Ext Wall_1L Gypsum_Rigid Ins_T135
| 3.1.1.2 | ▶ Gypsum + Masonry
[Gyp + Block]
| 3.1.1.2.1 | H_WA_AR_B02_Ext Wall_1L Gypsum_T200 Block_Mineral Wool
H_WA_AR_B02_Ext Wall_1L Gypsum_T200 Block_Mineral Wool_T135
| 3.1.1.2.2 | H_WA_AR_B02_Ext Wall_1L Gypsum_T200 Block_Glass Wool
H_WA_AR_B02_Ext Wall_1L Gypsum_T200 Block_Glass Wool_T135
| 3.1.1.2.3 | H_WA_AR_B02_Ext Wall_1L Gypsum_T200 Block_Rigid Ins
H_WA_AR_B02_Ext Wall_1L Gypsum_T200 Block_Rigid Ins_T135
[Gyp + Brick]
| 3.1.1.2.4 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Brick_Mineral Wool
H_WA_AR_B02_Ext Wall_1L Gypsum_1B Brick_Mineral Wool_T135
| 3.1.1.2.5 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Brick_Glass Wool
H_WA_AR_B02_Ext Wall_1L Gypsum_1B Brick_Glass Wool_T135
| 3.1.1.2.6 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Brick_Rigid Ins
H_WA_AR_B02_Ext Wall_1L Gypsum_1B Brick_Rigid Ins_T135
[Gyp + Clay Brick]
| 3.1.1.2.7 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Clay Brick_Mineral Wool
H_WA_AR_B02_Ext Wall_1L Gypsum_1B Clay Brick_Mineral Wool_T135
| 3.1.1.2.8 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Clay Brick_Glass Wool
H_WA_AR_B02_Ext Wall_1L Gypsum_1B Clay Brick_Glass Wool_T135
| 3.1.1.2.9 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Clay Brick_Rigid Ins
H_WA_AR_B02_Ext Wall_1L Gypsum_1B Clay Brick_Rigid Ins_T135
| 3.1.1.3 | ▶ Masonry + Masonry
[Block + Block]
| 3.1.1.3.1 | H_WA_AR_B02_Ext Wall_T100 Block_T200 Block_Mineral Wool
H_WA_AR_B02_Ext Wall_T100 Block_T200 Block_Mineral Wool_T100
| 3.1.1.3.2 | H_WA_AR_B02_Ext Wall_T100 Block_T200 Block_Galss Wool
H_WA_AR_B02_Ext Wall_T100 Block_T200 Block_Galss Wool_T100
| 3.1.1.3.3 | H_WA_AR_B02_Ext Wall_T100 Block_T200 Block_EPS or XPS
H_WA_AR_B02_Ext Wall_T100 Block_T200 Block_EPS_T100
H_WA_AR_B02_Ext Wall_T100 Block_T200 Block_XPS_T100
[Brick + Brick]
| 3.1.1.3.4 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Brick_Mineral Wool
H_WA_AR_B02_Ext Wall_0.5B Brick_1B Brick_Mineral Wool_T100
| 3.1.1.3.5 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Brick_Glass Wool
H_WA_AR_B02_Ext Wall_0.5B Brick_1B Brick_Glass Wool_T100
| 3.1.1.3.6 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Brick_EPS or XPS
H_WA_AR_B02_Ext Wall_0.5B Brick_1B Brick_EPS_T100
H_WA_AR_B02_Ext Wall_0.5B Brick_1B Brick_XPS_T100
[Clay Brick + Clay Brick]
| 3.1.1.3.7 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Clay Brick_Mineral Wool
H_WA_AR_B02_Ext Wall_0.5B Brick_1B Clay Brick_Mineral Wool_T100
| 3.1.1.3.8 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Clay Brick_Glass Wool
H_WA_AR_B02_Ext Wall_0.5B Brick_1B Clay Brick_Glass Wool_T100
| 3.1.1.3.9 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Clay Brick_EPS or XPS
H_WA_AR_B02_Ext Wall_0.5B Brick_1B Clay Brick_EPS_T100
H_WA_AR_B02_Ext Wall_0.5B Brick_1B Clay Brick_XPS_T100
| 3.1.1.4 | ▶ Masonry + Concrete (*Concrete Wall은 별도 Family로 분리)
[Block]
| 3.1.1.4.1 | H_WA_AR_B02_Ext Wall_T100 Block_Mineral Wool
H_WA_AR_B02_Ext Wall_T100 Block_Mineral Wool_T100
| 3.1.1.4.2 | H_WA_AR_B02_Ext Wall_T100 Block_Galss Wool
H_WA_AR_B02_Ext Wall_T100 Block_Galss Wool_T100
| 3.1.1.4.3 | H_WA_AR_B02_Ext Wall_T100 Block_EPS or XPS
H_WA_AR_B02_Ext Wall_T100 Block_EPS_T100
H_WA_AR_B02_Ext Wall_T100 Block_XPS_T100
[Brick]
| 3.1.1.4.4 | H_WA_AR_B02_Ext Wall_0.5B Brick_Mineral Wool
H_WA_AR_B02_Ext Wall_0.5B Brick_Mineral Wool_T100
| 3.1.1.4.5 | H_WA_AR_B02_Ext Wall_0.5B Brick_Galss Wool
H_WA_AR_B02_Ext Wall_0.5B Brick_Galss Wool_T100
| 3.1.1.4.6 | H_WA_AR_B02_Ext Wall_0.5B Brick_EPS or XPS
H_WA_AR_B02_Ext Wall_0.5B Brick_EPS_T100
H_WA_AR_B02_Ext Wall_0.5B Brick_XPS_T100
| 3.1.1.5 | ▶ Single Wall
[Only RC]
| 3.1.1.5.1 | H_WA_AR_B02_Ext Wall_RC
H_WA_AR_B02_Ext Wall_RC_T150
| 3.1.1.5.2 | H_WA_AR_B02_Ext Wall_RC_Exposed
H_WA_AR_B02_Ext Wall_RC_Exposed_T200
| 3.1.1.5.3 | H_WA_AR_B02_Ext Wall_RC_Parapet_Exposed
H_WA_AR_B02_Ext Wall_RC_Parapet_Exposed_T120
[Combined RC]
| 3.1.1.5.4 | H_WA_AR_B02_Ext Wall_RC_Emulsion Paint
H_WA_AR_B02_Ext Wall_RC_Emulsion Paint_T200
| 3.1.1.5.5 | H_WA_AR_B02_Ext Wall_RC_UG_Bitumen
H_WA_AR_B02_Ext Wall_RC_UG_Bitumen_T150
| 3.1.1.5.6 | H_WA_AR_B08_Ext Wall_RC_UG_Pit_Bitumen_Epoxy
H_WA_AR_B08_Ext Wall_RC_UG_Pit_Bitumen_Epoxy_T200
| 3.1.1.5.7 | H_WA_AR_B08_Ext Wall_RC_UG_Trench_Bitumen_Epoxy
H_WA_AR_B08_Ext Wall_RC_UG_Trench_Bitumen_Epoxy_T250
[Combined Masonry]
| 3.1.1.5.8 | H_WA_AR_B02_Ext Wall_Block_Emulsion
H_WA_AR_B02_Ext Wall_Block_Emulsion_T200
| 3.1.1.5.9 | H_WA_AR_B02_Ext Wall_Brick_Emulsion
H_WA_AR_B02_Ext Wall_Brick_Emulsion_1.0B
| 3.1.1.5.10 | H_WA_AR_B02_Ext Wall_Clay Brick
H_WA_AR_B02_Ext Wall_Clay Brick_1.0B
| 3.1.1.5.11 | H_WA_AR_B02_Ext Wall_AAC Block
H_WA_AR_B02_Ext Wall_AAC Block_T200
[Fence]
| 3.1.1.5.12 | H_WA_AR_B02_Ext Wall_Chain Link Fence (Fixed Type)
H_WA_AR_B02_Ext Wall_Chain Link Fence (Fixed Type)_H1200
| 3.1.1.6 | ▶ Cladding Wall
| 3.1.1.6.1 | H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool
H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_T120
| 3.1.1.6.2 | H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Glass Wool
H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Glass Wool_T135
| 3.1.1.6.3 | H_WA_AR_B02_Ext Wall_Single Sheet_Steel
H_WA_AR_B02_Ext Wall_Single Sheet_Steel_T0.7
| 3.1.1.6.4 | H_WA_AR_B02_Ext Wall_Sandwich Panel_AL_Mineral Wool
H_WA_AR_B02_Ext Wall_Sandwich Panel_AL_Mineral Wool_T120
| 3.1.1.6.5 | H_WA_AR_B02_Ext Wall_Sandwich Panel_AL_Glass Wool
H_WA_AR_B02_Ext Wall_Sandwich Panel_AL_Glass Wool_T120
| 3.1.1.7 | ▶ Cladding + Gypsum/Masonry
| 3.1.1.7.1 | H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_1L Gypsum
H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_1L Gypsum_T120
| 3.1.1.7.2 | H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_T100 Block
H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_T100 Block_T120
| 3.1.1.7.3 | H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_1.0B Brick
H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_1.0B Brick_T120
| 3.1.2 | □ Exterior Wall - F2 Group
| 3.1.2.1 | ▶ Exterior Wall Finish Only - F2
[Protection Board]
| 3.1.2.1.1 | H_WA_AR_B07_Ext Wall_Protection Board
H_WA_AR_B07_Ext Wall_Protection Board_T6
[Plaster]
| 3.1.2.1.2 | H_WA_AR_B07_Ext Wall_Int Plaster
H_WA_AR_B07_Ext Wall_Int Plaster_T12
3.Walls_Int
| No |  | Project Use
| 3.2 | Basic Wall - Int
| 3.2.1 | □ Interior Wall
| 3.2.1.1 | ▶ Gypsum
[1L Both Gypsum]
| 3.2.1.1.1 | H_WA_AR_B02_Int Wall_1L Both Gypsum_Mineral Wool
H_WA_AR_B02_Int Wall_1L Both Gypsum_Mineral Wool_T110_No FR
| 3.2.1.1.2 | H_WA_AR_B02_Int Wall_1L Both Gypsum_Glass Wool
H_WA_AR_B02_Int Wall_1L Both Gypsum_Glass Wool_T100_No FR
| 3.2.1.1.3 | H_WA_AR_B02_Int Wall_1L Both Gypsum
H_WA_AR_B02_Int Wall_1L Both Gypsum_No FR
[2L Both Gypsum]
| 3.2.1.1.4 | H_WA_AR_B02_Int Wall_2L Both Gypsum_Mineral Wool
H_WA_AR_B02_Int Wall_2L Both Gypsum_Mineral Wool_T100_FR 2H
| 3.2.1.1.5 | H_WA_AR_B02_Int Wall_2L Both Gypsum_Glass Wool
H_WA_AR_B02_Int Wall_2L Both Gypsum_Glass Wool_T100_FR 2H
| 3.2.1.1.6 | H_WA_AR_B02_Int Wall_2L Both Gypsum
H_WA_AR_B02_Int Wall_2L Both Gypsum_No FR
| 3.2.1.2 | ▶ Masonry
| 3.2.1.2.1 | H_WA_AR_B02_Int Wall_Block
H_WA_AR_B02_Int Wall_Block_T200
| 3.2.1.2.2 | H_WA_AR_B02_Int Wall_Brick
H_WA_AR_B02_Int Wall_Brick_1.0B
| 3.2.1.3 | ▶ Concrete
| 3.2.1.3.1 | H_WA_AR_B02_Int Wall_RC
H_WA_AR_B02_Int Wall_RC_T200
| 3.2.1.4 | ▶ Masonry + Gypsum
[Masonry + 1L One Side Gypsum]
| 3.2.1.4.1 | H_WA_AR_B02_Int Wall_Block T200_1L Gypsum_Mineral Wool
H_WA_AR_B02_Int Wall_Block T200_1L Gypsum_Mineral Wool_T50
| 3.2.1.4.2 | H_WA_AR_B02_Int Wall_Brick 1B_1L Gypsum_Mineral Wool
H_WA_AR_B02_Int Wall_Brick 1B_1L Gypsum_Mineral Wool_T50
[Masonry + 2L One Side Gypsum]
| 3.2.1.4.3 | H_WA_AR_B02_Int Wall_Block T200_2L Gypsum_Mineral Wool
H_WA_AR_B02_Int Wall_Block T200_2L Gypsum_Mineral Wool_T50
| 3.2.1.4.4 | H_WA_AR_B02_Int Wall_Brick 1B_2L Gypsum_Mineral Wool
H_WA_AR_B02_Int Wall_Brick 1B_2L Gypsum_Mineral Wool_T50
| 3.2.2 | □ Interior Wall - F2
| 3.2.2.1 | ▶ Interior Wall Finish Only
[Plaster]
| 3.2.2.1.1 | H_WA_AR_B07_Int Wall_Plaster
H_WA_AR_B07_Int Wall_Plaster_T12
[Ceramic Tile]
| 3.2.2.1.2 | H_WA_AR_B07_Int Wall_Ceramic Tile
H_WA_AR_B07_Int Wall_Ceramic Tile_150x150xT6
| 3.2.2.1.3 | H_WA_AR_B07_Int Wall_Ceramic Tile_L Waterproof
H_WA_AR_B07_Int Wall_Ceramic Tile_L Waterproof_150x150xT6
| 3.2.2.1.4 | H_WA_AR_B07_Int Wall_Ceramic Tile_Membrane
H_WA_AR_B07_Int Wall_Ceramic Tile_Membrane_150x150xT6
[Acide Resistant Tile]
| 3.2.2.1.5 | H_WA_AR_B07_Int Wall_Acid R Tile
H_WA_AR_B07_Int Wall_Acid R Tile_150x150xT6
| 3.2.2.1.6 | H_WA_AR_B07_Int Wall_Acid R Tile_L Waterproof
H_WA_AR_B07_Int Wall_Acid R Tile_L Waterproof_150x150xT6
[Etc. Tile]
| 3.2.2.1.7 | H_WA_AR_B07_Int Wall_Granite Tile
H_WA_AR_B07_Int Wall_Granite Tile_300x300xT9
| 3.2.2.1.8 | H_WA_AR_B07_Int Wall_Marble Tile
H_WA_AR_B07_Int Wall_Marble Tile_300x300xT9
| 3.3 | Curtain Wall
| 3.3.1 | □ Curtain Wall - normal
| 3.3.1.1 | ▶ Curtain Wall
| 3.3.1.1.1 | H_WA_AR_B02_Exterior Curtain Wall
| 3.3.1.1.2 | H_WA_AR_B02_Pavillion Curtain Wall
| 3.3.1.1.3 | H_WA_AR_B02_Storefront Curtain Wall
| 3.4 | Stacked Wall
| 3.4.1 | □ Stacked Wall - normal
| 3.4.1.1 | ▶ Stacked Wall
| 3.4.1.1.1 | H_WA_AR_B02_Exterior-Brick Over CMU w Metal Stud
4.St_Fdn
| No |  | Project Use
| 4.1 | Foundation Slab
| 4.1.1 | □ Slab
| 4.1.1.1 | ▶ Mat Foundation for Building
| 4.1.1.1.1 | H_SF_AR_S18_MAT_Bitumen
H_SF_AR_S18_MAT_Bitumen_T500
| 4.1.1.2 | ▶ Mat Foundation for Equipment
| 4.1.1.2.1 | H_SF_AR_B01_EQ FDN_Bitumen
H_SF_AR_B01_EQ FDN_Bitumen_Mat T600
| 4.1.1.2.2 | H_SF_AR_B01_EQ FDN_CEP Can_Bitumen
H_SF_AR_B01_EQ FDN_CEP Can_Bitumen_Mat T1000
| 4.1.1.3 | ▶ Mass Concrete (Temperature Control) for Equipment
| 4.1.1.3.1 | H_SF_AR_B01_Mass_Bitumen
H_SF_AR_B01_Mass_Bitumen_STG Mat T2500
| 4.1.1.4 | ▶ SOG Slab
| 4.1.1.4.1 | H_SF_AR_S17_SOG
H_SF_AR_S17_SOG T200_GS1
| 4.1.1.4.2 | H_SF_AR_S17_SOG_S Trowel
H_SF_AR_S17_SOG_S Trowel_T200_GS1
| 4.1.1.5 | ▶ Pit, Trench Slab
| 4.1.1.5.1 | H_FL_AR_B08_UG RC Slab_Pit
H_FL_AR_B08_UG RC Slab_Pit_T150_Bitumen_Epoxy
| 4.1.1.5.2 | H_FL_AR_B08_UG RC Slab_Trench
H_FL_AR_B08_UG RC Slab_Trench_T200_Bitumen_Epoxy
| 4.1.1.6 | ▶ SOG Slab Edge
| 4.1.1.6.1 | H_SF_AR_S17_SOG Edge
H_SF_AR_S17_SOG Edge_600x300
| 4.1.1.7 | ▶ Stoop, Pathway with Haunch
| 4.1.1.7.1 | H_SF_AR_B08_Stoop
H_SF_AR_B08_Stoop_T450
| 4.1.1.7.2 | H_SF_AR_B08_Ramp
H_SF_AR_B08_ Ramp_T200
| 4.1.1.8 | ▶ Lean Concrete
| 4.1.1.8.1 | H_SF_AR_S18_Lean
H_SF_AR_S18_Lean_T100
| 4.1.1.8.2 | H_SF_AR_S18_Lean_Base_Subbase
H_SF_AR_S18_Lean_Base_Subbase_T100
| 4.1.1.8.3 | H_SF_AR_S18_Lean_Bitumen_PE_Base_Subbase
H_SF_AR_S18_Lean_Bitumen_PE_Base_Subbase_T100
| 4.2 | Wall Foundation
| 4.2.1 | □ Wall Foundation - normal
| 4.2.1.1 | ▶ Wall Foundation
| 4.2.1.1.1 | H_SF_AR_S18_Wall Foundation
H_SF_AR_S18_Wall Foundation_Bitumen_T150
| 4.3 | Stacked Wall
| 4.3.1 | □ Stacked Wall - normal
| 4.3.1.1 | ▶ Stacked Wall
| 4.3.1.1.1 | H_SF_AR_S18_Stacked Wall
| 4.4 | Foundation Rectangular
| 4.4.1 | □ Foundation Rectangular (Non-Pile)
| 4.4.1.1 | ▶ Shallow Foundation / Pile Cap(Pile 별도모델링)
| 4.4.1.1.1 | H_SF_AR_S18_Shallow Fdn_Bitumen
H_SF_AR_S18_Shallow Fdn_Bitumen_1500x1500xT500_F1
| 4.5 | Pile
| 4.5.1 | □ Pile - normal
| 4.5.1.1 | ▶ Only Pile
| 4.5.1.1.1 | H_SF_AR_S19_Steel Pile
H_SF_AR_S19_Steel Pile_D508x12t_L10
| 4.5.1.1.2 | H_SF_AR_S19_PHC Pile_Driven
H_SF_AR_S19_PHC Pile_Driven_D500_L30
| 4.5.1.1.3 | H_SF_AR_S19_PHC Pile_Pre-boring
H_SF_AR_S19_PHC Pile_Pre-boring_D500_L30
Common User Input
Steel Common User Input
단위중량 기준 ( KG/M )
| Extra Heavy Steel | 200
| Heavy Steel | 90
Medium Steel
| Light Steel | 30
| Extra Light Steel | 10
5.St_Col
| No |  | Project Use
| 5.1 | RC Columns
| 5.1.1 | □ RC_UG Pedestal
| 5.1.1.1 | ▶ RC_UG Pedestal
| 5.1.1.1.1 | H_SC_AR_S15_UG PED_Bit
H_SC_AR_S15_UG PED_Bit_500x500_PD1
| 5.1.1.1.2 | H_SC_AR_S15_UG PED_Bit_Anchor
H_SC_AR_S15_UG PED_Bit_Anchor_1000x1800_PD2
| 5.1.1.1.3 | H_SC_AR_S15_UG PED_Grout only
H_SC_AR_S15_UG PED_Grout only_500x500_PD1
| 5.1.2 | □ RC_Column_Rectangular
| 5.1.2.1 | ▶ RC_Column Rectangular
| 5.1.2.1.1 | H_SC_AR_S15_AG Column
H_SC_AR_S15_AG Column_500x500_C1
| 5.2 | Steel Column
| 5.2.1 | □ Steel Column_W
| 5.2.1.1 | ▶ Steel Column_W_ASTM A6M
[Extra Heavy Steel]
| 5.2.1.1.1 | H_SC_AR_S01_W (Extra Heavy)
[Heavy Steel]
| 5.2.1.1.2 | H_SC_AR_S01_W (Medium)
H_SC_AR_S01_W-360x91
[Medium Steel]
| 5.2.1.1.3 | H_SC_AR_S01_W (Medium)
H_SC_AR_S01_W-200x31.3
[Light Steel]
| 5.2.1.1.4 | H_SC_AR_S01_W (Light)
H_SC_AR_S01_W-200x22.5
[Extra Light Steel]
| 5.2.1.1.5 | H_SC_AR_S01_W (Extra Light)
| 5.2.2 | □ Steel Column_H
| 5.2.2.1 | ▶ Steel Column_H_KSD3502
[H-Extra Heavy Steel]
| 5.2.2.1.1 | H_SC_AR_S01_H (Extra Heavy)
[H-Heavy Steel]
| 5.2.2.1.2 | H_SC_AR_S01_H (Heavy)
H_SC_AR_S01_H-400x400x13x21_SC1
[H-Medium Steel]
| 5.2.2.1.3 | H_SC_AR_S01_H (Medium)
H_SC_AR_S01_H-200x200x8x12_C2
[H-Light Steel]
| 5.2.2.1.4 | H_SC_AR_S01_H (Light)
H_SC_AR_S01_H-100x100x6x8
[H-Extra Light Steel]
| 5.2.2.1.5 | H_SC_AR_S01_H (Extra Light)
| 5.2.3 | □ Steel Column_H_Built Up
| 5.2.3.1 | ▶ Steel Column_H_Built Up
[H-Extra Heavy Steel]
| 5.2.3.1.1 | H_SC_AR_S01_BH (Extra Heavy)
H_SC_AR_S01_BH-1000x300x20x40_SC1
[H-Heavy Steel]
| 5.2.3.1.2 | H_SC_AR_S01_BH (Heavy)
[H-Medium Steel]
| 5.2.3.1.3 | H_SC_AR_S01_BH (Medium)
| 5.2.4 | □ Steel Column_SHS (Square Hollow Section)
| 5.2.4.1 | ▶ Steel Column_SHS_KSD3502
[SHS-Heavy Steel]
| 5.2.4.1.1 | H_SC_AR_S01_SHS (Heavy)
H_SC_AR_S01_SHS-350x350x12_SC1
[SHS-Medium Steel]
| 5.2.4.1.2 | H_SC_AR_S01_SHS (Medium)
H_SC_AR_S01_SHS-250x250x12_SC2
[SHS-Light Steel]
| 5.2.4.1.3 | H_SC_AR_S01_SHS (Light)
H_SC_AR_S01_SHS-100x100x9_SC3
[SHS-Extra Light Steel]
| 5.2.4.1.4 | H_SC_AR_S01_SHS (Extra Light)
H_SC_AR_S01_SHS-40x40x1.6_SC4
| 5.2.5 | □ Steel Column_RHS (Rectangular Hollow Section)
| 5.2.5.1 | ▶ Steel Column_RHS_KSD3502
[SHS-Heavy Steel]
| 5.2.5.1.1 | H_SC_AR_S01_RHS (Heavy)
H_SC_AR_S01_RHS-400x200x12_SC1
[SHS-Medium Steel]
| 5.2.5.1.2 | H_SC_AR_S01_RHS (Medium)
H_SC_AR_S01_RHS-250x150x12_SC2
[SHS-Light Steel]
| 5.2.5.1.3 | H_SC_AR_S01_RHS (Light)
H_SC_AR_S01_RHS-200x100x4.5_SC3
[SHS-Extra Light Steel]
| 5.2.5.1.4 | H_SC_AR_S01_RHS (Extra Light)
H_SC_AR_S01_RHS-50x20x1.6_SC4
| 5.2.6 | □ Steel Column_CHS (Circular Hollow Section)
| 5.2.6.1 | ▶ Steel Column_CHS_KSD3502
[CHS-Extra Heavy Steel]
| 5.2.6.1.1 | H_SC_AR_S01_CHS (Extra Heavy)
H_SC_AR_S01_CHS-1016x16_SC1
[CHS-Heavy Steel]
| 5.2.6.1.2 | H_SC_AR_S01_CHS (Heavy)
H_SC_AR_S01_CHS-558.8x9.5_SC2
[CHS-Medium Steel]
| 5.2.6.1.3 | H_SC_AR_S01_CHS (Medium)
H_SC_AR_S01_CHS-267.4x6.6_SC3
[CHS-Light Steel]
| 5.2.6.1.4 | H_SC_AR_S01_CHS (Light)
H_SC_AR_S01_CHS-165.2x4.5_SC4
[CHS-Extra Light Steel]
| 5.2.6.1.5 | H_SC_AR_S01_CHS (Extra Light)
H_SC_AR_S01_CHS-21.7x1.9_SC5
6.St_Framing
| No |  | Project Use
| 6.1 | RC_Tie Girder
| 6.1.1 | □ RC_Beam / Girder
| 6.1.1.1 | ▶ Tie Girder
| 6.1.1.1.1 | H_SB_AR_S16_TG
H_SB_AR_S16_TG_400x600_TG1
| 6.1.1.2 | ▶ RC Beam / Girder
| 6.1.1.2.1 | H_SB_AR_S16_AG
H_SB_AR_S16_AG_300x600_RG1
| 6.2 | Steel Beam
| 6.2.1 | □ Steel Beam_W
| 6.2.1.1 | ▶ Steel Beam_W_ASTM A6 M
[W-Extra Heavy Steel]
| 6.2.1.1.1 | H_SB_AR_S02_W (Heavy)
H_SB_AR_S02_W-1100x400x499_SG1
[W-Heavy Steel]
| 6.2.1.1.2 | H_SB_AR_S02_W (Heavy)
H_SB_AR_S02_W-530x210x101_SG2
[W-Medium Steel]
| 6.2.1.1.3 | H_SB_AR_S02_W (Medium)
H_SB_AR_S02_W-310x200x60_SG3
[W-Light Steel]
| 6.2.1.1.4 | H_SB_AR_S02_W (Light)
H_SB_AR_S02_W-250x100x22.3_SG4
[W-Extra Light Steel]
| 6.2.1.1.5 | H_SB_AR_S02_W (Extra Light)
| 6.2.2 | □ Steel Beam_H
| 6.2.2.1 | ▶ Steel Beam_H-KSD3502
[H-Extra Heavy Steel]
| 6.2.2.1.1 | H_SB_AR_S02_H (Extra Heavy)
H_SB_AR_S02_H-900x300x16x28_RSG1
[H-Heavy Steel]
| 6.2.2.1.2 | H_SB_AR_S02_H (Heavy)
H_SB_AR_S02_H-588x300x12x20_RSG2
[H-Medium Steel]
| 6.2.2.1.3 | H_SB_AR_S02_H (Medium)
H_SB_AR_S02_H-400x200x8x13_RSG1
[H-Light Steel]
| 6.2.2.1.4 | H_SB_AR_S02_H (Light)
H_SB_AR_S02_H-100x100x6x8_RSG3
[H-Extra Light Steel]
| 6.2.2.1.5 | H_SB_AR_S02_H (Extra Light)
| 6.2.3 | □ Steel Beam_BH
| 6.2.3.1 | ▶ Steel Beam_H-Built Up
[H-Extra Heavy Steel]
| 6.2.3.1.1 | H_SB_AR_S02_BH (Extra Heavy Steel)
H_SB_AR_S02_BH-1000x300x20x40_SG1
[H-Heavy Steel]
| 6.2.3.1.2 | H_SB_AR_S02_BH (Heavy Steel)
[H-Medium Steel]
| 6.2.3.1.3 | H_SB_AR_S02_BH (Medium Steel)
| 6.2.4 | □ Steel Beam_SHS (Square Hollow Section)
| 6.2.4.1 | ▶ Steel Beam_SHS_KSD
[SHS-Heavy Steel]
| 6.2.4.1.1 | H_SB_AR_S02_SHS (Heavy)
H_SB_AR_S02_SHS-350x350x12_SG1
[SHS-Medium Steel]
| 6.2.4.1.2 | H_SB_AR_S02_SHS (Medium)
H_SB_AR_S02_SHS-250x250x12_SG2
[SHS-Light Steel]
| 6.2.4.1.3 | H_SB_AR_S02_SHS (Light)
H_SB_AR_S02_SHS-100x100x9_SG3
[SHS-Extra Light Steel]
| 6.2.4.1.4 | H_SB_AR_S02_SHS (Extra Light)
H_SB_AR_S02_SHS-40x40x1.6_SG4
| 6.2.5 | □ Steel Beam_RHS (Rectangular Hollow Section)
| 6.2.5.1 | ▶ Steel Beam_RHS_KSD
[RHS-Heavy Steel]
| 6.2.5.1.1 | H_SB_AR_S02_RHS (Heavy)
H_SB_AR_S02_RHS-400x200x12_SG1
[RHS-Medium Steel]
| 6.2.5.1.2 | H_SB_AR_S02_RHS (Medium)
H_SB_AR_S02_RHS-250x150x12_SG2
[RHS-Light Steel]
| 6.2.5.1.3 | H_SB_AR_S02_RHS (Light)
H_SBC_AR_S02_RHS-200x100x4.5_SG3
[RHS-Extra Light Steel]
| 6.2.5.1.4 | H_SB_AR_S02_RHS (Extra Light)
H_SB_AR_S02_RHS-50x20x1.6_SG4
| 6.2.6 | □ Steel Beam_CHS (Circular Hollow Section)
| 6.2.6.1 | ▶ Steel Beam_CHS_KSD
[CHS-Extra Heavy Steel]
| 6.2.6.1.1 | H_SB_AR_S02_CHS (Extra Heavy)
H_SB_AR_S02_CHS-1016x16_SG1
[CHS-Heavy Steel]
| 6.2.6.1.2 | H_SB_AR_S02_CHS (Heavy)
H_SB_AR_S02_CHS-558.8x9.5_SG2
[CHS-Medium Steel]
| 6.2.6.1.3 | H_SB_AR_S02_CHS (Medium)
H_SB_AR_S02_CHS-267.4x6.6_SG3
[CHS-Light Steel]
| 6.2.6.1.4 | H_SB_AR_S02_CHS (Light)
H_SB_AR_S02_CHS-165.2x4.5_SG4
[CHS-Extra Light Steel]
| 6.2.6.1.5 | H_SB_AR_S02_CHS (Extra Light)
H_SB_AR_S02_CHS-21.7x1.9_SG5
| 6.2.7 | □ Steel Beam_Channel
| 6.2.7.1 | ▶ Steel Beam_Channel_KSD
[C-Heavy Steel]
| 6.2.7.1.1 | H_SB_AR_S02_C (Heavy)
[C-Medium Steel]
| 6.2.7.1.2 | H_SB_AR_S02_C (Medium)
H_SB_AR_S02_C-250x90x9x13_PB1
[C-Light Steel]
| 6.2.7.1.3 | H_SB_AR_S02_C (Light)
H_SB_AR_S02_C-125x65x6x8_PB2
| 6.2.8 | □ Steel Beam_Angle
| 6.2.8.1 | ▶ Steel Beam_Angle_KSD
[L-Heavy Steel]
| 6.2.8.1.1 | H_SB_AR_S02_L (Heavy)
H_SB_AR_S02_L-250x250x35_PB1
[L-Medium Steel]
| 6.2.8.1.2 | H_SB_AR_S02_L (Medium)
H_SB_AR_S02_L-175x175x12_PB2
[L-Light Steel]
| 6.2.8.1.3 | H_SB_AR_S02_L (Light)
H_SB_AR_S02_L-100x100x10_PB3
| 6.2.9 | □ Steel Beam_Tee
| 6.2.9.1 | ▶ Steel Beam_Tee_KSD
[CT-Heavy Steel]
| 6.2.9.1.1 | H_SB_AR_S02_CT (Heavy)
[CT-Medium Steel]
| 6.2.9.1.2 | H_SB_AR_S02_CT (Medium)
H_SB_AR_S02_CT-170x250x9x14_PB2
[CT-Light Steel]
| 6.2.9.1.3 | H_SB_AR_S02_CT (Light)
H_SB_AR_S02_CT-125x125x6x9_PB3
| 6.3 | Steel Hori. Brace
| 6.3.1 | □ Steel Hori. Brace_Angle
| 6.3.1.1 | ▶ Steel Hori. Brace_Angle_KSD
[L-B-Heavy Steel]
| 6.3.1.1.1 | H_SB_AR_S03_L (Heavy)
H_SB_AR_S03_L-250x250x35_HBR1
[L-B-Medium Steel]
| 6.3.1.1.2 | H_SB_AR_S03_L (Medium)
H_SB_AR_S03_L-175x175x12_HBR2
[L-B-Light Steel]
| 6.3.1.1.3 | H_SB_AR_S03_L (Light)
H_SB_AR_S03_L-100x100x10_HBR3
| 6.3.2 | □ Steel Hori. Brace_CHS (Circular Hollow Section)
| 6.3.2.1 | ▶ Steel Hori. Brace_CHS_KSD
[CHS-HB-Heavy Steel]
| 6.3.2.1.1 | H_SB_AR_S03_CHS (Heavy)
H_SB_AR_S03_CHS-558.8x9.5_HBR1
[CHS-HB-Medium Steel]
| 6.3.2.1.2 | H_SB_AR_S03_CHS (Medium)
H_SB_AR_S03_CHS-267.4x6.6_HBR2
[CHS-HB-Light Steel]
| 6.3.2.1.3 | H_SB_AR_S03_CHS (Light)
H_SB_AR_S03_CHS-165.2x4.5_HBR3
| 6.3.3 | □ Steel Hori. Brace_Double Angle
| 6.3.3.1 | ▶ Steel Hori. Brace_2Ls_KSD
[2Ls-HB-Heavy Steel]
| 6.3.3.1.1 | H_SB_AR_S03_2Ls (Heavy)
H_SB_AR_S03_2Ls-200x200x15_HBR1
[2Ls-HB-Medium Steel]
| 6.3.3.1.2 | H_SB_AR_S03_2Ls (Medium)
H_SB_AR_S03_2Ls-100x100x13_HBR2
[2Ls-HB-Light Steel]
| 6.3.3.1.3 | H_SB_AR_S03_2Ls (Light)
H_SB_AR_S03_2Ls-75x75x6_HBR3
| 6.4 | Steel Ver. Brace
| 6.4.1 | □ Steel Ver. Brace_Angle
| 6.4.1.1 | ▶ Steel Ver. Brace_Angle_KSD
[L-VB-Heavy Steel]
| 6.4.1.1.1 | H_SB_AR_S04_L (Heavy)
H_SB_AR_S04_L-250x250x35_VBR1
[L-VB-Medium Steel]
| 6.4.1.1.2 | H_SB_AR_S04_L (Medium)
H_SB_AR_S04_L-175x175x12_VBR2
[L-VB-Light Steel]
| 6.4.1.1.3 | H_SB_AR_S04_L (Light)
H_SB_AR_S04_L-100x100x10_VBR3
| 6.4.2 | □ Steel Ver. Brace_CHS (Circular Hollow Section)
| 6.4.2.1 | ▶ Steel Ver. Brace_CHS_KSD
[CHS-VB-Heavy Steel]
| 6.4.2.1.1 | H_SB_AR_S04_CHS (Heavy)
H_SB_AR_S04_CHS-558.8x9.5_VBR1
[CHS-VB-Medium Steel]
| 6.4.2.1.2 | H_SB_AR_S04_CHS (Medium)
H_SB_AR_S04_CHS-267.4x6.6_VBR2
[CHS-VB-Light Steel]
| 6.4.2.1.3 | H_SB_AR_S04_CHS (Light)
H_SB_AR_S04_CHS-165.2x4.5_VBR3
| 6.4.3 | □ Steel Ver. Brace_Double Angle
| 6.4.3.1 | ▶ Steel Ver. Brace_2Ls_KSD
[2Ls-VB-Heavy Steel]
| 6.4.3.1.1 | H_SB_AR_S04_2Ls (Medium)
H_SB_AR_S04_2Ls-200x200x15_VBR1
[2Ls-VB-Medium Steel]
| 6.4.3.1.2 | H_SB_AR_S04_2Ls (Medium)
H_SB_AR_S04_2Ls-100x100x13_VBR2
[2Ls-VB-Light Steel]
| 6.4.3.1.3 | H_SB_AR_S04_2Ls (Light)
H_SB_AR_S04_2Ls-75x75x6_VBR3
| 6.5 | Steel Purlin
| 6.5.1 | □ Steel Purlin_LC
| 6.5.1.1 | ▶ Steel Purlin_LC_KSD
| 6.5.1.1.1 | H_SB_AR_B03_LC
H_SB_AR_B03_LC-200x75x25x4.0_Purlin
| 6.6 | Steel Girth
| 6.6.1 | □ Steel Girth_LC
| 6.6.1.1 | ▶ Steel Girth_LC_KSD
| 6.6.1.1.1 | H_SB_AR_B04_LC
H_SB_AR_B04_LC-200x75x25x4.0_Girth
7.Ceilings
| No |  | Project Use
| 7.1 | Ceiling
| 7.1.1 | □ Basic Ceiling
| 7.1.1.1 | ▶ Simple Ceiling
| 7.1.1.1.1 | H_CE_AR_B09_Acrylic Emulsion Paint
H_CE_AR_B09_Acrylic Emulsion Paint
| 7.1.2 | □ Compound Ceiling - normal
| 7.1.2.1 | ▶ Compound Ceiling
| 7.1.2.1.1 | H_CE_AR_B09_Acoustic Ceiling_T Bar
H_CE_AR_B09_Acoustic Ceiling_T Bar_600x600x9T
| 7.1.2.1.2 | H_CE_AR_B09_Moisture Resistant Ceiling_M Bar
H_CE_AR_B09_Moisture Resistant Ceiling_M Bar_600x1200x9T
8.Doors
| No |  | Project Use
| 8.1 | Single Door
| 8.1.1 | □ Single Door - normal
| 8.1.1.1 | ▶ Single Door_Steel
| 8.1.1.1.1 | H_DR_AR_B12_Single Door_Steel
H_DR_AR_B12_Single Door_Steel_W1000xH2100_No FR
H_DR_AR_B12_Single Door_Steel_W1000xH2100_FR 0.5H
| 8.1.1.1.2 | H_DR_AR_B12_Single Door_Steel_Vision
H_DR_AR_B12_Single Door_Steel_Vision_W1000xH2100_No FR
H_DR_AR_B12_Single Door_Steel_Vision_W1000xH2100_FR 1.0H
| 8.1.1.1.3 | H_DR_AR_B12_Single Door_Steel_Panic
H_DR_AR_B12_Single Door_Steel_Panic_W1000xH2100_No FR
H_DR_AR_B12_Single Door_Steel_Panic_W1000xH2100_FR 1.5H
| 8.1.1.1.4 | H_DR_AR_B12_Single Door_Steel_Vision_Panic
H_DR_AR_B12_Single Door_Steel_Vision_Panic_W1000xH2100_No FR
H_DR_AR_B12_Single Door_Steel_Vision_Panic_W1000xH2100_FR 2.0H
| 8.1.1.2 | ▶ Single Door_Blast
| 8.1.1.2.1 | H_DR_AR_B12_Single Door_Blast
H_DR_AR_B12_Single Door_Blast_W1000xH2100_No FR
H_DR_AR_B12_Single Door_Blast_W1000xH2100_FR 1.0H
| 8.1.1.2.2 | H_DR_AR_B12_Single Door_Blast_Panic
H_DR_AR_B12_Single Door_Blast_Panic_W1000xH2100_No FR
H_DR_AR_B12_Single Door_Blast_Panic_W1000xH2100_FR 1.5H
| 8.1.1.3 | ▶ Single Door_Aluminum
| 8.1.1.3.1 | H_DR_AR_B12_Single Door_AL
H_DR_AR_B12_Single Door_Blast_Panic_W1000xH2100_No FR
H_DR_AR_B12_Single Door_Blast_Panic_W1000xH2100_FR 1.5H
| 8.1.1.3.2 | H_DR_AR_B12_Single Door_AL_Vision
H_DR_AR_B12_Single Door_Blast_Panic_W1000xH2100_No FR
H_DR_AR_B12_Single Door_Blast_Panic_W1000xH2100_FR 1.5H
| 8.1.1.3.3 | H_DR_AR_B12_Single Door_AL_Panic
H_DR_AR_B12_Single Door_Blast_Panic_W1000xH2100_No FR
H_DR_AR_B12_Single Door_Blast_Panic_W1000xH2100_FR 1.5H
| 8.1.1.3.4 | H_DR_AR_B12_Single Door_AL_Vision_Panic
H_DR_AR_B12_Single Door_Blast_Panic_W1000xH2100_No FR
H_DR_AR_B12_Single Door_Blast_Panic_W1000xH2100_FR 1.5H
| 8.1.1.4 | ▶ Single Door_Glass
| 8.1.1.4.1 | H_DR_AR_B12_Single Door_Glass
H_DR_AR_B12_Single Door_Glass_W1000xH2100
| 8.1.1.5 | ▶ Single Door_SST
| 8.1.1.5.1 | H_DR_AR_B12_Single Door_SST
H_DR_AR_B12_Single Door_SST_W1000xH2100
| 8.1.1.6 | ▶ Single Door_Wood
| 8.1.1.6.1 | H_DR_AR_B12_Single Door_Wood
H_DR_AR_B12_Single Door_Wood_W1000xH2100
| 8.1.1.6.2 | H_DR_AR_B12_Single Door_Wood_Vision
H_DR_AR_B12_Single Door_Wood_Vision_W1000xH2100
| 8.1.1.7 | ▶ Single Door_uPVC
| 8.1.1.7.1 | H_DR_AR_B12_Single Door_uPVC
H_DR_AR_B12_Single Door_uPVC_W1000xH2100
| 8.2 | Double Door
| 8.2.1 | □ Double Door - normal
| 8.2.1.1 | ▶ Double Door_Steel
| 8.2.1.1.1 | H_DR_AR_B12_Double Door_Steel
H_DR_AR_B12_Double Door_Steel_W2000xH2100_No FR
H_DR_AR_B12_Double Door_Steel_W2000xH2100_FR 1.0H
| 8.2.1.1.2 | H_DR_AR_B12_Double Door_Steel_Vision
H_DR_AR_B12_Double Door_Steel_Vision_W2000xH2100_No FR
H_DR_AR_B12_Double Door_Steel_Vision_W2000xH2100_FR 1.0H
| 8.2.1.1.3 | H_DR_AR_B12_Double Door_Steel_Panic
H_DR_AR_B12_Double Door_Steel_Panic_W2000xH2100_No FR
H_DR_AR_B12_Double Door_Steel_Panic_W2000xH2100_FR 2.0H
| 8.2.1.1.4 | H_DR_AR_B12_Double Door_Steel_Vision_Panic
H_DR_AR_B12_Double Door_Steel_Vision_Panic_W2000xH2100_No FR
H_DR_AR_B12_Double Door_Steel_Vision_Panic_W2000xH2100_FR 1.0H
| 8.2.1.2 | ▶ Double Door_Blast
| 8.2.1.2.1 | H_DR_AR_B12_Double Door_Blast
H_DR_AR_B12_Single Door_Blast_W1000xH2100_No FR
H_DR_AR_B12_Single Door_Blast_W1000xH2100_FR 1.0H
| 8.2.1.2.2 | H_DR_AR_B12_Double Door_Blast_Panic
H_DR_AR_B12_Double Door_Blast_Panic_W2000xH2100_No FR
H_DR_AR_B12_Double Door_Blast_Panic_W2000xH2100_FR 1.0H
| 8.2.1.3 | ▶ Double Door_Aluminum
| 8.2.1.3.1 | H_DR_AR_B12_Double Door_AL
H_DR_AR_B12_Double Door_AL_W2000xH2100_No FR
H_DR_AR_B12_Double Door_AL_W2000xH2100_FR 1.0H
| 8.2.1.3.2 | H_DR_AR_B12_Double Door_AL_Vision
H_DR_AR_B12_Double Door_AL_Vision_W2000xH2100_No FR
H_DR_AR_B12_Double Door_AL_Vision_W2000xH2100_FR 1.0H
| 8.2.1.3.3 | H_DR_AR_B12_Double Door_AL_Panic
H_DR_AR_B12_Double Door_AL_Panic_W2000xH2100_No FR
H_DR_AR_B12_Double Door_AL_Panic_W2000xH2100_FR 1.0H
| 8.2.1.3.4 | H_DR_AR_B12_Double Door_AL_Vision_Panic
H_DR_AR_B12_Double Door_AL_Vision_Panic_W2000xH2100_No FR
H_DR_AR_B12_Double Door_AL_Vision_Panic_W2000xH2100_FR 1.0H
| 8.2.1.4 | ▶ Double Door_Glass
| 8.2.1.4.1 | H_DR_AR_B12_Double Door_Glass
H_DR_AR_B12_Double Door_Glass_W2000xH2100
| 8.2.1.5 | ▶ Double Door_SST
| 8.2.1.5.1 | H_DR_AR_B12_Double Door_SST
H_DR_AR_B12_Double Door_SST_W2000xH2100
| 8.2.1.6 | ▶ Double Door_Wood
| 8.2.1.6.1 | H_DR_AR_B12_Double Door_Wood
H_DR_AR_B12_Double Door_Wood_W2000xH2100
| 8.2.1.6.2 | H_DR_AR_B12_Double Door_Wood_Vision
H_DR_AR_B12_Double Door_Wood_Vision_W2000xH2100
| 8.3 | Double Door + Transsom
| 8.3.1 | □ Double Door + Transsom - normal
| 8.3.1.1 | ▶ Double Door_Steel_Transsom
| 8.3.1.1.1 | H_DR_AR_B12_Double Door_Steel_Transsom
H_DR_AR_B12_Double Door_Steel_Transsom_W2000xH3000_No FR
H_DR_AR_B12_Double Door_Steel_Transsom_W2000xH3000_FR 1.0H
| 8.3.1.1.2 | H_DR_AR_B12_Double Door_Steel_Vision_Transsom
H_DR_AR_B12_Double Door_Steel_Vision_Transsom_W2000xH3000_No FR
H_DR_AR_B12_Double Door_Steel_Vision_Transsom_W2000xH3000_FR 1.0H
| 8.3.1.1.3 | H_DR_AR_B12_Double Door_Steel_Panic_Transsom
H_DR_AR_B12_Double Door_Steel_Panic_Transsom_W2000xH3000_No FR
H_DR_AR_B12_Double Door_Steel_Panic_Transsom_W2000xH3000_FR 1.0H
| 8.3.1.1.4 | H_DR_AR_B12_Double Door_Steel_Vision_Panic_Transsom
H_DR_AR_B12_Double Door_Steel_Vision_Panic_Transsom_W2000xH3000_No FR
H_DR_AR_B12_Double Door_Steel_Vision_Panic_Transsom_W2000xH3000_FR 1.0H
| 8.3.1.2 | ▶ Double Door_Blast_Transsom
| 8.3.1.2.1 | H_DR_AR_B12_Double Door_Blast_Transsom
H_DR_AR_B12_Double Door_Blast_Transsom_W2000xH3000_No FR
H_DR_AR_B12_Double Door_Blast_Transsom_W2000xH3000_FR 1.0H
| 8.3.1.2.2 | H_DR_AR_B12_Double Door_Blast_Panic_Transsom
H_DR_AR_B12_Double Door_Blast_Panic_Transsom_W2000xH3000_No FR
H_DR_AR_B12_Double Door_Blast_Panic_Transsom_W2000xH3000_FR 2.0H
| 8.4 | Etc.
| 8.4.1 | □ Etc. - normal
| 8.4.1.1 | ▶ Shutter
[Roll up Steel]
| 8.4.1.1.1 | H_DR_AR_B12_Roll up Door_Steel_Manual
H_DR_AR_B12_Roll up Door_Steel_Manual_W5000xH6000_No FR
H_DR_AR_B12_Roll up Door_Steel_Manual_W5000xH6000_FR 1.0H
| 8.4.1.1.2 | H_DR_AR_B12_Roll up Door_Steel_Motor
H_DR_AR_B12_Roll up Door_Steel_Motor_W5000xH6000_No FR
H_DR_AR_B12_Roll up Door_Steel_Motor_W5000xH6000_FR 1.0H
[Roll up Blast]
| 8.4.1.1.3 | H_DR_AR_B12_Roll up Door_Blast_Manual
H_DR_AR_B12_Roll up Door_Blast_Manual_W5000xH6000_No FR
H_DR_AR_B12_Roll up Door_Blast_Manual_W5000xH6000_FR 2.0H
| 8.4.1.1.4 | H_DR_AR_B12_Roll up Door_Blast_Motor
H_DR_AR_B12_Roll up Door_Blast_Motor_W5000xH6000_No FR
H_DR_AR_B12_Roll up Door_Blast_Motor_W5000xH6000_FR 2.0H
[Roll up Aluminum]
| 8.4.1.1.5 | H_DR_AR_B12_Roll up Door_AL_Manual
H_DR_AR_B12_Roll up Door_AL_Manual_W5000xH6000
| 8.4.1.1.6 | H_DR_AR_B12_Roll up Door_AL_Motor
H_DR_AR_B12_Roll up Door_AL_Mortor_W5000xH6000
| 8.4.1.2 | ▶ Sliding
[Sliding Door Steel]
| 8.4.1.2.1 | H_DR_AR_B12_Sliding Door_Steel_Manual
H_DR_AR_B12_Sliding Door_Steel_Manual_W5000xH6000
| 8.4.1.2.2 | H_DR_AR_B12_Sliding Door_Steel_Motor
H_DR_AR_B12_Sliding Door_Steel_Mortor_W5000xH6000
[Sliding Door Aluminum]
| 8.4.1.2.3 | H_DR_AR_B12_Sliding Door_AL_Manual
H_DR_AR_B12_Sliding Door_AL_Manual_W5000xH6000
| 8.4.1.2.4 | H_DR_AR_B12_Sliding Door_AL_Motor
H_DR_AR_B12_Sliding Door_AL_Mortor_W5000xH6000
[Sliding Door Glass]
| 8.4.1.2.5 | H_DR_AR_B12_Sliding Door_Glass_Manual
H_DR_AR_B12_Sliding Door_Glass_Manual_W1000xH2100
| 8.4.1.2.6 | H_DR_AR_B12_Sliding Door_Glass_Motor
H_DR_AR_B12_Sliding Door_Glass_Motor_W1000xH2100
| 8.4.1.3 | ▶ Hanger
| 8.4.1.3.1 | H_DR_AR_B12_Hanger Door_Steel
H_DR_AR_B12_Hanger Door_Steel_W5000xH6000
| 8.4.1.4 | ▶ Swing
| 8.4.1.4.1 | H_DR_AR_B12_Swing Door_Steel
H_DR_AR_B12_Swing Door_Steel_W5000xH6000
| 8.4.1.4.2 | H_DR_AR_B12_Swing Door_AL
H_DR_AR_B12_Swing Door_AL_W5000xH6000
| 8.4.1.5 | ▶ Revolving
| 8.4.1.5.1 | H_DR_AR_B12_Revolving Door_Manual
H_DR_AR_B12_Revolving Door_Manual_W5000xH6000
| 8.4.1.5.2 | H_DR_AR_B12_Revolving Door_Auto
H_DR_AR_B12_Revolving Door_Auto_W5000xH6000
| 8.4.1.6 | ▶ Folding
[Folding Door Steel]
| 8.4.1.6.1 | H_DR_AR_B12_Folding Door_Steel_Manual
H_DR_AR_B12_Folding Door_Steel_Manual_W5000xH6000
| 8.4.1.6.2 | H_DR_AR_B12_Folding Door_Steel_Motor
H_DR_AR_B12_Folding Door_Steel_Mortor_W5000xH6000
[Folding Door Aluminum]
| 8.4.1.6.3 | H_DR_AR_B12_Folding Door_AL_Manual
H_DR_AR_B12_Folding Door_AL_Manual_W5000xH6000
| 8.4.1.6.4 | H_DR_AR_B12_Folding Door_AL_Motor
H_DR_AR_B12_Folding Door_AL_Mortor_W5000xH6000
[Folding Door Etc.]
| 8.4.1.6.5 | H_DR_AR_B12_Folding Door_PVC_Manual
H_DR_AR_B12_Folding Door_PVC_Manual_W5000xH6000
| 8.4.1.6.6 | H_DR_AR_B12_Folding Door_Glass_Manual
H_DR_AR_B12_Folding Door_Glass_Manual_W5000xH6000
9.Windows
| No |  | Project Use
| 9.1 | Sliding Type Window
| 9.1.1 | □ Sliding Type
| 9.1.1.1 | ▶ Steel Window (Sliding)
| 9.1.1.1.1 | H_WD_AR_B11_Sliding_Steel Window
H_WD_AR_B11_Sliding_Steel Window_SG_W2000xH1000
H_WD_AR_B11_Sliding_Steel Window_DG_W2000xH1000
| 9.1.1.2 | ▶ Aluminum Window (Sliding)
| 9.1.1.2.1 | H_WD_AR_B11_Sliding_AL Window
H_WD_AR_B11_Sliding_AL Window_SG_W2000xH1000
H_WD_AR_B11_Sliding_AL Window_DG_W2000xH1000
| 9.1.1.3 | ▶ uPVC Window (Sliding)
| 9.1.1.3.1 | H_WD_AR_B11_Sliding_uPVC Window
H_WD_AR_B11_Sliding_uPVC Window_SG_W2000xH1000
H_WD_AR_B11_Sliding_uPVC Window_DG_W2000xH1000
| 9.1.1.4 | ▶ Blast Resistant Window (Sliding)
| 9.1.1.4.1 | H_WD_AR_B11_Sliding_Blast Window
H_WD_AR_B11_Sliding_Blast Window_W2000xH1000
| 9.1.1.5 | ▶ Bullet-Proof Steel Window (Sliding)
| 9.1.1.5.1 | H_WD_AR_B11_Sliding_Bullet-Proof Steel Window
H_WD_AR_B11_Sliding_Bullet-Proof Steel Window_W2000xH1000
| 9.2 | Awning Type Window
| 9.2.1 | □ Awning Type
| 9.2.1.1 | ▶ Steel Window (Awning)
| 9.2.1.1.1 | H_WD_AR_B11_Awning_Steel Window
H_WD_AR_B11_Awining_ Steel Window_SG_W2000xH1000
H_WD_AR_B11_Awining_ Steel Window_DG_W2000xH1000
| 9.2.1.2 | ▶ Aluminum Window (Awning)
| 9.2.1.2.1 | H_WD_AR_B11_Awning_AL Window
H_WD_AR_B11_Awining_ AL Window_SG_W2000xH1000
H_WD_AR_B11_Awining_ AL Window_DG_W2000xH1000
| 9.2.1.3 | ▶ uPVC Window (Awning)
| 9.2.1.3.1 | H_WD_AR_B11_Awning_uPVC Window
H_WD_AR_B11_Awining_uPVC Window_SG_W2000xH1000
H_WD_AR_B11_Awining_uPVC Window_DG_W2000xH1000
| 9.2.1.4 | ▶ Blast Resistant Window (Awning)
| 9.2.1.4.1 | H_WD_AR_B11_Awning_Blast Window
H_WD_AR_B11_Awining_Blast Window_W2000xH1000
| 9.2.1.5 | ▶ Bullet-Proof Steel Window (Awning)
| 9.2.1.5.1 | H_WD_AR_B11_Awning_Bullet-Proof Steel Window
H_WD_AR_B11_Awining_Bullet-Proof Steel Window_W2000xH1000
| 9.3 | Fix Type Window
| 9.3.1 | □ Fix Type
| 9.3.1.1 | ▶ Steel Window (Fix)
| 9.3.1.1.1 | H_WD_AR_B11_Fix_Steel Window
H_WD_AR_B11_Fix_Steel Window_SG_W2000xH1000
H_WD_AR_B11_Fix_Steel Window_DG_W2000xH1000
| 9.3.1.2 | ▶ Aluminum Window (Fix)
| 9.3.1.2.1 | H_WD_AR_B11_Fix_AL Window
H_WD_AR_B11_Fix_AL Window_SG_W2000xH1000
H_WD_AR_B11_Fix_AL Window_DG_W2000xH1000
H_WD_AR_B11_Fix_AL Window_DG LowE_W2000xH1000
| 9.3.1.3 | ▶ uPVC Window (Fix)
| 9.3.1.3.1 | H_WD_AR_B11_Fix_uPVC Window
H_WD_AR_B11_Fix_uPVC Window_SG_W2000xH1000
H_WD_AR_B11_Fix_uPVC Window_DG_W2000xH1000
| 9.3.1.4 | ▶ Blast Resistant Window (Fix)
| 9.3.1.4.1 | H_WD_AR_B11_Fix_Blast Window
H_WD_AR_B11_Fix_Blast Window_W2000xH1000
| 9.3.1.5 | ▶ Bullet-Proof Steel Window (Fix)
| 9.3.1.5.1 | H_WD_AR_B11_Fix_Bullet-Proof Steel Window
H_WD_AR_B11_Fix_Bullet-Proof Steel Window_W2000xH1000
| 9.4 | Combination Type Window
| 9.4.1 | □ Fix + Awning
| 9.4.1.1 | ▶ Steel Window (Fix + Awning)
| 9.4.1.1.1 | H_WD_AR_B11_Fix_Awning_Steel Window
H_WD_AR_B11_Fix_Awning_Steel Window_SG_W2000xH1000
H_WD_AR_B11_Fix_Awning_Steel Window_DG_W2000xH1000
| 9.4.1.2 | ▶ Aluminum Window (Fix + Awning)
| 9.4.1.2.1 | H_WD_AR_B11_Fix_Awning_AL Window
H_WD_AR_B11_Fix_Awning_AL Window_SG_W2000xH1000
H_WD_AR_B11_Fix_Awning_AL Window_DG_W2000xH1000
H_WD_AR_B11_Fix_Awning_AL Window_DG LowE_W2000xH1000
| 9.4.1.3 | ▶ uPVC Window (Fix + Awning)
| 9.4.1.3.1 | H_WD_AR_B11_Fix_Awning_uPVC Window
H_WD_AR_B11_Fix_Awning_uPVC Window_SG_W2000xH1000
H_WD_AR_B11_Fix_Awning_uPVC Window_DG_W2000xH1000
| 9.5 | Skylight
| 9.5.1 | □ Skylight - normal
| 9.5.1.1 | ▶ Skylight
| 9.5.1.1.1 | H_WD_AR_B11_Skylight
H_WD_AR_B11_Skylight_FRP_W2000xH1000
H_WD_AR_B11_Skylight_Acrylic_W2000xH1000
| 9.6 | MISC Window
| 9.6.1 | □ MISC
| 9.6.1.1 | ▶ Casement_Aluminum Window
| 9.6.1.1.1 | H_WD_AR_B11_Casement_AL Window
H_WD_AR_B11_Casement_AL Window_DG_W2000xH1000
| 9.6.1.2 | ▶ Hung_Aluminum Window
| 9.6.1.2.1 | H_WD_AR_B11_Hung_AL Window
H_WD_AR_B11_Hung_AL Window_Single_DG_W2000xH1000
H_WD_AR_B11_Hung_AL Window_Single_DG_Low E_W2000xH1000
H_WD_AR_B11_Hung_AL Window_Double_DG_W2000xH1000
| 9.6.1.3 | ▶ Tilt_Aluminum Window
| 9.6.1.3.1 | H_WD_AR_B11_Tilt_AL Window
H_WD_AR_B11_Tilt_AL Window_DG_W2000xH1000
| 9.6.1.4 | ▶ Center Pivotilt_Aluminum Window
| 9.6.1.4.1 | H_WD_AR_B11_Center Pivot_AL Window
H_WD_AR_B11_Center Pivot_AL Window_DG_W2000xH1000
| 9.7 | Louver
| 9.7.1 | □ Louver - normal
| 9.7.1.1 | ▶ Louver
| 9.7.1.1.1 | H_WD_AR_B11_Louver
H_WD_AR_B11_Louver_Steel_W2000xH1000
H_WD_AR_B11_Louver_AL_W1000xH500
10.Stairs
| No |  | Project Use
| 10.1 | Assembled Stair
| 10.1.1 | □ Assembled Stair - normal
| 10.1.1.1 | ▶ Assembled Stair
| 10.1.1.1.1 | H_SR_AR_S09_Steel Stair
H_SR_AR_S09_Steel Stair_W1000
| 10.2 | Precast Stair
| 10.2.1 | □ Precast Stair - normal
| 10.2.1.1 | ▶ Precast Stair
| 10.2.1.1.1 | H_SR_AR_B08_Concrete Stair_Outdoor
H_SR_AR_B08_Concrete Stair_Outdoor_W1000
11.Railings
| No |  | Project Use
| 11.1 | Railing
| 11.1.1 | □ Railing - normal
| 11.1.1.1 | ▶ Steel Handrail
| 11.1.1.1.1 | H_RL_AR_S10_Steel Handrail
H_RL_AR_S10_Steel Handrail_H1100
| 11.1.1.1.2 | H_RL_AR_S11_Steel Removable Handrail
H_RL_AR_S11_Steel Removable Handrail_H1100
12.Generic
| No |  | Project Use
| 12.1 | Ladder
| 12.1.1 | □ Ladder - normal
| 12.1.1.1 | ▶ Caged Ladder
| 12.1.1.1.1 | H_GM_AR_S08_Caged Ladder
H_GM_AR_S08_Caged Ladder_Bracket Set 150
| 12.1.1.2 | ▶ Non Caged Ladder
| 12.1.1.2.1 | H_GM_AR_S08_Non Caged Ladder
H_GM_AR_S08_Non Caged Ladder_Bracket Set 150_H1250
| 12.2 | Bollard
| 12.2.1 | □ Bollard - normal
| 12.2.1.1 | ▶ Steel Bollard
| 12.2.1.1.1 | H_GM_AR_B07_Steel Bollard
H_GM_AR_B07_Steel Bollard_D150
| 12.3 | Rain Drainage
| 12.3.1 | □ Roof Drain - normal
| 12.3.1.1 | ▶ Roof Drain
| 12.3.1.1.1 | H_GM_AR_B07_Roof Drain
H_GM_AR_B07_Roof Drain_D150
| 12.3.2 | □ Downspout & Splash Block
| 12.3.2.1 | ▶ Downspout
| 12.3.2.1.1 | H_GM_AR_B07_Steel Downspout
H_GM_AR_B07_Steel Downspout_D150
| 12.3.2.2 | ▶ Splash Block
| 12.3.2.2.1 | H_GM_AR_B07_Splash Block
H_GM_AR_B07_Splash Block_200x300
| 12.4 | Grout
| 12.4.1 | □ Grout - normal
| 12.4.1.1 | ▶ Grouting
| 12.4.1.1.1 | H_GM_AR_B07_Grouting
H_GM_AR_B07_Grouting_T50
| 12.5 | MISC
| 12.5.1 | □ MISC - normal
| 12.5.1.1 | ▶ Room Signage
| 12.5.1.1.1 | H_GM_AR_B07_Room Signage
H_GM_AR_B07_Room Signage
Lv1 | 13.Manual_Input | (모델링 없이 직접 산출한 물량 입력)
| No |  | Project Use
Lv2 | 13.1 | Ladder
Lv3 | 13.1.1 | □ Ladder - normal
Lv4 | 13.1.1.1 | ▶ Caged Ladder
| 13.1.1.1.1 | H_MI_AR_S08_Caged Ladder
H_MI_AR_S08_Caged Ladder_Bracket Set 150
| 13.1.1.2 | ▶ Non Caged Ladder
| 13.1.1.2.1 | H_MI_AR_S08_Non Caged Ladder
H_MI_AR_S08_Non Caged Ladder_Bracket Set 150_H1250
Lv2 | 13.2 | Bollard
Lv3 | 13.2.1 | □ Bollard - normal
Lv4 | 13.2.1.1 | ▶ Steel Bollard
| 13.2.1.1.1 | H_MI_AR_B07_Steel Bollard
H_MI_AR_B07_Steel Bollard_Fix_D150
H_MI_AR_B07_Steel Bollard_Removable_D150
Lv2 | 13.3 | Rain Drainage
Lv3 | 13.3.1 | □ Rain Drainage
Lv4 | 13.3.1.1 | ▶ Roof Drain
| 13.3.1.1.1 | H_MI_AR_B07_Roof Drain
H_MI_AR_B07_Roof Drain_D100
Lv4 | 13.3.1.2 | ▶ Downspout
| 13.3.1.2.1 | H_MI_AR_B07_Steel Downspout
H_MI_AR_B07_Steel Downspout_D150
Lv4 | 13.3.1.3 | ▶ Gutter
| 13.3.1.3.1 | H_MI_AR_B07_Steel Eave Gutter
H_MI_AR_B07_Steel Eave Gutter_200x200
Lv4 | 13.3.1.4 | ▶ Splash Block
| 13.3.1.4.1 | H_MI_AR_B07_Splash Block
H_MI_AR_B07_Splash Block_200x300
Lv2 | 13.4 | Grout
Lv3 | 13.4.1 | □ Grout
Lv4 | 13.4.1.1 | ▶ Grouting
| 13.4.1.1.1 | H_MI_AR_B07_Grouting
H_MI_AR_B07_Grouting_T50
Lv2 | 13.5 | Anchor Bolt
Lv3 | 13.5.1 | □ Anchor Bolt
Lv4 | 13.5.1.1 | ▶ Anchor Bolt - Substructure
| 13.5.1.1.1 | H_MI_AR_B07_Anchor Bolt_Substructure
H_MI_AR_B07_Anchor Bolt_Substructure_M12
H_MI_AR_B07_Anchor Bolt_Substructure_M16
H_MI_AR_B07_Anchor Bolt_Substructure_M20
H_MI_AR_B07_Anchor Bolt_Substructure_Chemical_M10
H_MI_AR_B07_Anchor Bolt_Substructure_Chemical_M12
H_MI_AR_B07_Anchor Bolt_Substructure_Chemical_M16
H_MI_AR_B07_Anchor Bolt_Substructure_Expansion_M10
H_MI_AR_B07_Anchor Bolt_Substructure_Expansion_M12
H_MI_AR_B07_Anchor Bolt_Substructure_Expansion_M16
Lv4 | 13.5.1.2 | ▶ Anchor Bolt - Equipment Foundation
| 13.5.1.2.1 | H_MI_AR_B07_Anchor Bolt_Equipment Foundation
H_MI_AR_B07_Anchor Bolt_Equipment Foundation_M12
H_MI_AR_B07_Anchor Bolt_Equipment Foundation_M16
H_MI_AR_B07_Anchor Bolt_Equipment Foundation_M20
Lv4 | 13.5.1.3 | ▶ Anchor Bolt - Mass Concrete
| 13.5.1.3.1 | H_MI_AR_B07_Anchor Bolt_Mass Concrete
H_MI_AR_B07_Anchor Bolt_Mass Concrete_M12
H_MI_AR_B07_Anchor Bolt_Mass Concrete_M16
H_MI_AR_B07_Anchor Bolt_Mass Concrete_M20
Lv2 | 13.6 | Embedded Steel
Lv3 | 13.6.1 | □ Embedded Steel
Lv4 | 13.6.1.1 | ▶ Embedded Steel
| 13.6.1.1.1 | H_MI_AR_B07_Embedded Steel
H_MI_AR_B07_Embedded Steel_Galva.
H_MI_AR_B07_Embedded Steel_SUS 304
H_MI_AR_B07_Embedded Steel_SUS 316L
Lv2 | 13.7 | Room, Toilt, Shower
Lv3 | 13.7.1 | □ Room, Toilt, Shower
Lv4 | 13.7.1.1 | ▶ Signage
| 13.7.1.1.1 | H_MI_AR_B07_Signage
H_MI_AR_B07_Signage_Room
H_MI_AR_B07_Signage_Building
Lv4 | 13.7.1.2 | ▶ Toilet Accessories
| 13.7.1.2.1 | H_MI_AR_B07_Toilet Accessories
H_MI_AR_B07_Toilet Accessories_Mirror_W750xH800
H_MI_AR_B07_Toilet Accessories_Soap Dish
H_MI_AR_B07_Toilet Accessories_Towel Bar
H_MI_AR_B07_Toilet Accessories_Paper Tower Dispenser
H_MI_AR_B07_Toilet Accessories_Urinal Partition
H_MI_AR_B07_Toilet Accessories_Marble Washstand
Lv4 | 13.7.1.3 | ▶ Septic Tank
| 13.7.1.3.1 | H_MI_AR_B07_Septic Tank
H_MI_AR_B07_Septic Tank_FRP
Lv2 | 13.8 | Furniture Installation
Lv3 | 13.8.1 | □ Furniture Installation
Lv4 | 13.8.1.1 | ▶ Furniture Installation
| 13.8.1.1.1 | H_MI_AR_B07_Furniture Installation
H_MI_AR_B07_Furniture Installation_Desk
H_MI_AR_B07_Furniture Installation_Washing Unit
[Family Name 분류 체계]
- Lv1 : Family Category 1단계
- LV2 : Family Category 2단계, Standard Hierarchy
- Lv3 : □ / 팀 표준 설계 정보 (Large)
- Lv4 : ▶ / 팀 표준 설계 정보 (Middle, Small)
- Lv5 : 동일 WM Group
- Lv6 : User 추가
R4- 협력사 배포 기준 수립 후 수정 필요

## Family_표준_구성도
| [플랜트건축팀 Family 구성도] |  |  | 표준 |  | 바로가기
|  | ※ Lv5까지의 Full Family Name 반드시 준수 |  |  |  | 0.Room | B11 | 1.Floors | B20 | 2.Roofs | B97 | 3.Walls_Ext | B164 | 3.Walls_Int | B261
[6 empty] | 0.Room |  | 1.Floors |  | 2.Roofs |  | 3.Walls_Ext |  | 3.Walls_Int
|  | ※ Lv6 : 사용자 추가 정보는 Family Name Lv6 에 반영 |  |  |  | 4.St_Fdn | B339 | 5.St_Col | B420 | 6.St_Framing | B515 | 7.Ceilings | B714 | 8.Doors | B730
[6 empty] | 4.St_Fdn |  | 5.St_Col |  | 6.St_Framing |  | 7.Ceilings |  | 8.Doors
[6 empty] | 9.Windows | B879 | 10.Stairs | B999 | 11.Railings | B1016 | 12.Generic | B1027 | 13.Manual_Input | B1081
[6 empty] | 9.Windows |  | 10.Stairs |  | 11.Railings |  | 12.Generic |  | 13.Manual_Input
| No | Category | 행위치 | 이동버튼 | Check Slot
0.Room
| No |  | 행위치 |  | Check Slot
| 0.1 | Basic Room
| 0.1.1 | □ Room - normal
| 0.1.1.1 | ▶ Rooms
General Rooms
1.Floors
| No |  | 행위치 |  | Check Slot
| 1.1 | Floors
| 1.1.1 | □ Concrete Slab
| 1.1.1.1 | ▶ Concrete Slab | F6 | 위치로 이동 | O
| 1.1.1.1.1 | H_FL_AR_S17_RC Slab | F8
| 1.1.1.1.2 | H_FL_AR_S17_RC Slab_S Trowel | F24
| 1.1.1.2 | ▶ Roof Concrete Slab | F46 | 위치로 이동 | O
| 1.1.1.2.1 | H_FL_AR_S17_Roof RC Slab | F48
| 1.1.1.3 | ▶ Turbine Top Deck Slab | F57 | 위치로 이동
| 1.1.1.3.1 | H_FL_AR_S17_STG Top Slab | F59
| 1.1.1.4 | ▶ Concrete Deck Slab | F67 | 위치로 이동 | O
| 1.1.1.4.1 | H_FL_AR_S17_RC Deck Slab | F69
| 1.1.1.4.2 | H_FL_AR_S17_RC Deck Slab_S Trowel | F78
| 1.1.1.5 | ▶ Roof Concrete Deck Slab | F88 | 위치로 이동 | O
| 1.1.1.5.1 | H_RF_AR_S17_Roof RC Deck Slab | F90
| 1.1.2 | □ Checkered / Grating
| 1.1.2.1 | ▶ Grating Floor | F99 | 위치로 이동
| 1.1.2.1.1 | H_FL_AR_S05_Grating | F101
| 1.1.2.2 | ▶ Removable Grating Floor | F110 | 위치로 이동
| 1.1.2.2.1 | H_FL_AR_S06_Removable Grating | F112
| 1.1.2.3 | ▶ Checkered Plate Floor | F119 | 위치로 이동
| 1.1.2.3.1 | H_FL_AR_S07_CHK PL | F121
| 1.1.3 | □ Finish - F2 Group (실행 모델에서만 적용)
| 1.1.3.1 | ▶ Tile | F128
|  | [Ceramic Tile] | F129 | 위치로 이동
| 1.1.3.1.1 | H_FL_AR_B07_Ceramic Tile | F131
| 1.1.3.1.2 | H_FL_AR_B07_Ceramic Tile_L Waterproof | F137
| 1.1.3.1.3 | H_FL_AR_B07_Ceramic Tile_Memb | F145
|  | [Acid Resistant Tile] | F154 | 위치로 이동
| 1.1.3.1.4 | H_FL_AR_B07_Acid R Tile | F156
| 1.1.3.1.5 | H_FL_AR_B07_Acid R Tile_L Waterproof | F162
|  | [Vinyl Tile] | F171 | 위치로 이동
| 1.1.3.1.6 | H_FL_AR_B07_Vinyl Tile | F173
| 1.1.3.1.7 | H_FL_AR_B07_Vinyl Tile_Screed | F179
| 1.1.3.1.8 | H_FL_AR_B07_Anti Static Vinyl Tile | F186
|  | [Etc. Tile] | F193 | 위치로 이동
| 1.1.3.1.9 | H_FL_AR_B07_Granite Tile | F201
| 1.1.3.1.10 | H_FL_AR_B07_Marble Tile | F207
| 1.1.3.1.11 | H_FL_AR_B07_Stone Tile | F213
| 1.1.3.1.12 | H_FL_AR_B07_Porcelain Tile | F219
| 1.1.3.1.13 | H_FL_AR_B07_Carpet Tile | F225
| 1.1.3.2 | ▶ Mat | F231 | 위치로 이동
| 1.1.3.2.1 | H_FL_AR_B07_Carpet | F233
| 1.1.3.2.2 | H_FL_AR_B07_Matwell | F239
| 1.1.3.2.3 | H_FL_AR_B07_Entrance Floor Mats and Frame | F245
| 1.1.3.3 | ▶ Raised Floor | F251 | 위치로 이동 |  | Room family 산출과 중복됨 적용 케이스 확인 필요
| 1.1.3.3.1 | H_FL_AR_B10_Raised Floor_600x600 | F253
| 1.1.3.4 | ▶ UG Insulation | F260 | 위치로 이동
| 1.1.3.4.1 | H_FL_AR_B07_Ground Insulation | F262
| 1.2 | Slab Edge
| 1.2.1 | □ Edge
| 1.2.1.1 | ▶ Edge | F270 | 위치로 이동
| 1.2.1.1.1 | H_FL_AR_S17_Thickened | F272
2.Roofs
| No |  | 행위치 |  | Check Slot
| 2.1 | Basic Roof
| 2.1.1 | □ For Concrete Roof
| 2.1.1.1 | ▶ Slope < Insulation < Waterproofing | F6 | 위치로 이동
| 2.1.1.1.1 | H_RF_AR_B06_LW Conc(Slope)_XPS_Memb | F8
| 2.1.1.1.2 | H_RF_AR_B06_Mortar(Slope)_XPS_Memb | F17
| 2.1.1.1.3 | H_RF_AR_B06_LW Conc(Slope)_XPS_Memb_Gravel | F27
| 2.1.1.2 | ▶ Slope < Waterproofing < Insulation < Protection | F37 | 위치로 이동
| 2.1.1.2.1 | H_RF_AR_B06_Memb_XPS_PE_Protective Conc | F39
| 2.1.1.2.2 | H_RF_AR_B06_Memb_XPS_PE_Roof Tile | F48
| 2.1.1.2.3 | H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_Geot_Gravel | F57
| 2.1.1.2.4 | H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_Geot_Roof Tile | F67
| 2.1.1.2.5 | H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_PE_Roof Tile | F77
| 2.1.1.2.6 | H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_PE_Protective Conc | F87
| 2.1.1.3 | ▶ Waterproofing < Insulation < Protection & Slope | F97 | 위치로 이동 | O
| 2.1.1.3.1 | H_RF_AR_B06_Memb_XPS_PE_Protective Conc(Slope) | F99
| 2.1.1.3.2 | H_RF_AR_B06_Memb_XPS_PE_LW Conc(Slope) | F108
| 2.1.2 | □ Cladding Roof
| 2.1.2.1 | ▶ Sandwitch Panel Roof | F117 | 위치로 이동
| 2.1.2.1.1 | H_RF_AR_B05_Roof Panel Steel Mineral Wool | F119
| 2.1.2.1.2 | H_RF_AR_B05_Roof Panel Steel Glass Wool | F125
| 2.1.2.1.3 | H_RF_AR_B05_Roof Panel AL Mineral Wool | F131
| 2.1.2.1.4 | H_RF_AR_B05_Roof Panel AL Glass Wool | F137
| 2.1.2.2 | ▶ Single Metal Sheet Roof | F143 | 위치로 이동
| 2.1.2.2.1 | H_RF_AR_B05_Roof Single Sheet Steel | F145
| 2.1.2.2.2 | H_RF_AR_B05_Roof Single Sheet AL | F151
| 2.2 | Gutter
| 2.2.1 | □ Gutter - general
| 2.2.1.1 | ▶ Gutter | F159 | 위치로 이동
| 2.2.1.1.1 | H_RF_AR_B07_Gutter_Steel_Eave | F161
| 2.2.1.1.2 | H_RF_AR_B07_Gutter_Steel_Valley | F167
| 2.2.1.1.3 | H_RF_AR_B07_Gutter_AL_Eave | F173
| 2.2.1.1.4 | H_RF_AR_B07_Gutter_AL_Valley | F179
| 2.3 | Fascia
| 2.3.1 | □ Fascia - general
| 2.3.1.1 | ▶ Fascia | F187 | 위치로 이동
| 2.3.1.1.1 | H_RF_AR_B07_Fascia-Flat | F189
| 2.4 | Roof Soffit
| 2.4.1 | □ Soffit - general
| 2.4.1.1 | ▶ Soffit | F197 | 위치로 이동
| 2.4.1.1.1 | H_RF_AR_B07_Soffit | F199
| 2.5 | Sloped Glazing
| 2.5.1 | □ Sloped Glazing - general
| 2.5.1.1 | ▶ Sloped Glazing | F207 | 위치로 이동
| 2.5.1.1.1 | H_RF_AR_B07_Sloped Glazing | F209
3.Walls_Ext
| No |  | 행위치 |  | Check Slot
| 3.1 | Basic Wall -Ext
| 3.1.1 | □ Exterior Wall
| 3.1.1.1 | ▶ Gypsum + Concrete (*Concrete Wall은 별도 Family로 분리) | F6 | 위치로 이동
| 3.1.1.1.1 | H_WA_AR_B02_Ext Wall_1L Gypsum_Mineral Wool | F8
| 3.1.1.1.2 | H_WA_AR_B02_Ext Wall_1L Gypsum_Glass Wool | F15
| 3.1.1.1.3 | H_WA_AR_B02_Ext Wall_2L Gypsum_Glass Wool | F22
| 3.1.1.1.4 | H_WA_AR_B02_Ext Wall_1L Gypsum_Rigid Ins | F30
| 3.1.1.2 | ▶ Gypsum + Masonry | F37
|  | [Gyp + Block] | F38 | 위치로 이동
| 3.1.1.2.1 | H_WA_AR_B02_Ext Wall_1L Gypsum_T200 Block_Mineral Wool | F39
| 3.1.1.2.2 | H_WA_AR_B02_Ext Wall_1L Gypsum_T200 Block_Glass Wool | F49
| 3.1.1.2.3 | H_WA_AR_B02_Ext Wall_1L Gypsum_T200 Block_Rigid Ins | F59
|  | [Gyp + Brick] | F70 | 위치로 이동
| 3.1.1.2.4 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Brick_Mineral Wool | F71
| 3.1.1.2.5 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Brick_Glass Wool | F81
| 3.1.1.2.6 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Brick_Rigid Ins | F91
|  | [Gyp + Clay Brick] | F102 | 위치로 이동
| 3.1.1.2.7 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Clay Brick_Mineral Wool | F103
| 3.1.1.2.8 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Clay Brick_Glass Wool | F113
| 3.1.1.2.9 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Clay Brick_Rigid Ins | F123
| 3.1.1.3 | ▶ Masonry + Masonry | F133
|  | [Block + Block] | F134 | 위치로 이동
| 3.1.1.3.1 | H_WA_AR_B02_Ext Wall_T100 Block_T200 Block_Mineral Wool | F135
| 3.1.1.3.2 | H_WA_AR_B02_Ext Wall_T100 Block_T200 Block_Galss Wool | F146
| 3.1.1.3.3 | H_WA_AR_B02_Ext Wall_T100 Block_T200 Block_EPS or XPS | F157
|  | [Brick + Brick] | F169 | 위치로 이동
| 3.1.1.3.4 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Brick_Mineral Wool | F170
| 3.1.1.3.5 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Brick_Glass Wool | F181
| 3.1.1.3.6 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Brick_EPS or XPS | F192
|  | [Clay Brick + Clay Brick] | F204 | 위치로 이동
| 3.1.1.3.7 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Clay Brick_Mineral Wool | F205
| 3.1.1.3.8 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Clay Brick_Glass Wool | F216
| 3.1.1.3.9 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Clay Brick_EPS or XPS | F227
| 3.1.1.4 | ▶ Masonry + Concrete (*Concrete Wall은 별도 Family로 분리) | F238
|  | [Block] | F239 | 위치로 이동
| 3.1.1.4.1 | H_WA_AR_B02_Ext Wall_T100 Block_Mineral Wool | F240
| 3.1.1.4.2 | H_WA_AR_B02_Ext Wall_T100 Block_Galss Wool | F248
| 3.1.1.4.3 | H_WA_AR_B02_Ext Wall_T100 Block_EPS or XPS | F256
|  | [Brick] | F265 | 위치로 이동
| 3.1.1.4.4 | H_WA_AR_B02_Ext Wall_0.5B Brick_Mineral Wool | F266
| 3.1.1.4.5 | H_WA_AR_B02_Ext Wall_0.5B Brick_Galss Wool | F274
| 3.1.1.4.6 | H_WA_AR_B02_Ext Wall_0.5B Brick_EPS or XPS | F282
| 3.1.1.5 | ▶ Single Wall | F290
|  | [Only RC] | F291 | 위치로 이동
| 3.1.1.5.1 | H_WA_AR_B02_Ext Wall_RC | F292
| 3.1.1.5.2 | H_WA_AR_B02_Ext Wall_RC_Exposed | F300
| 3.1.1.5.3 | H_WA_AR_B02_Ext Wall_RC_Parapet_Exposed | F308
|  | [Combined RC] | F317 | 위치로 이동
| 3.1.1.5.4 | H_WA_AR_B02_Ext Wall_RC_Emulsion Paint | F327
| 3.1.1.5.5 | H_WA_AR_B02_Ext Wall_RC_UG_Bitumen | F346
| 3.1.1.5.6 | H_WA_AR_B08_Ext Wall_RC_UG_Pit_Bitumen_Epoxy | F355
| 3.1.1.5.7 | H_WA_AR_B08_Ext Wall_RC_UG_Trench_Bitumen_Epoxy | F381
|  | [Combined Masonry] | F392 | 위치로 이동
| 3.1.1.5.8 | H_WA_AR_B02_Ext Wall_Block_Emulsion | F393
| 3.1.1.5.9 | H_WA_AR_B02_Ext Wall_Brick_Emulsion | F401
| 3.1.1.5.10 | H_WA_AR_B02_Ext Wall_Clay Brick | F409
| 3.1.1.5.11 | H_WA_AR_B02_Ext Wall_AAC Block | F415
|  | [Fence] | F422 | 위치로 이동
| 3.1.1.5.12 | H_WA_AR_B02_Ext Wall_Chain Link Fence (Fixed Type) | F423
| 3.1.1.6 | ▶ Cladding Wall | F429 | 위치로 이동
| 3.1.1.6.1 | H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool | F431
| 3.1.1.6.2 | H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Glass Wool | F437
| 3.1.1.6.3 | H_WA_AR_B02_Ext Wall_Single Sheet_Steel | F443
| 3.1.1.6.4 | H_WA_AR_B02_Ext Wall_Sandwich Panel_AL_Mineral Wool | F449
| 3.1.1.6.5 | H_WA_AR_B02_Ext Wall_Sandwich Panel_AL_Glass Wool | F455
| 3.1.1.7 | ▶ Cladding + Gypsum/Masonry | F461 | 위치로 이동
| 3.1.1.7.1 | H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_1L Gypsum | F463
| 3.1.1.7.2 | H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_T100 Block | F470
| 3.1.1.7.3 | H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_1.0B Brick | F477
| 3.1.2 | □ Exterior Wall - F2 Group
| 3.1.2.1 | ▶ Exterior Wall Finish Only - F2 | F484 | 위치로 이동
[Protection Board]
| 3.1.2.1.1 | H_WA_AR_B07_Ext Wall_Protection Board | F486
|  | [Plaster] | F494
| 3.1.2.1.2 | H_WA_AR_B07_Ext Wall_Int Plaster | F495
3.Walls_Int
| No |  | 행위치 |  | Check Slot
| 3.2 | Basic Wall - Int
| 3.2.1 | □ Interior Wall
| 3.2.1.1 | ▶ Gypsum | F6
|  | [1L Both Gypsum] | F7 | 위치로 이동
| 3.2.1.1.1 | H_WA_AR_B02_Int Wall_1L Both Gypsum_Mineral Wool | F8
| 3.2.1.1.2 | H_WA_AR_B02_Int Wall_1L Both Gypsum_Glass Wool | F14
| 3.2.1.1.3 | H_WA_AR_B02_Int Wall_1L Both Gypsum | F20
|  | [2L Both Gypsum] | F27 | 위치로 이동
| 3.2.1.1.4 | H_WA_AR_B02_Int Wall_2L Both Gypsum_Mineral Wool | F28
| 3.2.1.1.5 | H_WA_AR_B02_Int Wall_2L Both Gypsum_Glass Wool | F34
| 3.2.1.1.6 | H_WA_AR_B02_Int Wall_2L Both Gypsum | F40
| 3.2.1.2 | ▶ Masonry | F46 | 위치로 이동
| 3.2.1.2.1 | H_WA_AR_B02_Int Wall_Block | F48
| 3.2.1.2.2 | H_WA_AR_B02_Int Wall_Brick | F54
| 3.2.1.3 | ▶ Concrete | F60 | 위치로 이동
| 3.2.1.3.1 | H_WA_AR_B02_Int Wall_RC | F62
| 3.2.1.4 | ▶ Masonry + Gypsum | F70
|  | [Masonry + 1L One Side Gypsum] | F71 | 위치로 이동
| 3.2.1.4.1 | H_WA_AR_B02_Int Wall_Block T200_1L Gypsum_Mineral Wool | F72
| 3.2.1.4.2 | H_WA_AR_B02_Int Wall_Brick 1B_1L Gypsum_Mineral Wool | F80
|  | [Masonry + 2L One Side Gypsum] | F89 | 위치로 이동
| 3.2.1.4.3 | H_WA_AR_B02_Int Wall_Block T200_2L Gypsum_Mineral Wool | F90
| 3.2.1.4.4 | H_WA_AR_B02_Int Wall_Brick 1B_2L Gypsum_Mineral Wool | F98
Glass Wall - Wall Family F1
WM 찾기
| 3.2.2 | □ Interior Wall - F2 Group
| 3.2.2.1 | ▶ Interior Wall Finish Only | F114
|  | [Plaster] | F115 | 위치로 이동
| 3.2.2.1.1 | H_WA_AR_B07_Int Wall_Plaster | F116
|  | [Ceramic Tile] | F123 | 위치로 이동
| 3.2.2.1.2 | H_WA_AR_B07_Int Wall_Ceramic Tile | F124
| 3.2.2.1.3 | H_WA_AR_B07_Int Wall_Ceramic Tile_L Waterproof | F130
| 3.2.2.1.4 | H_WA_AR_B07_Int Wall_Ceramic Tile_Membrane | F137
|  | [Acide Resistant Tile] | F145 | 위치로 이동
| 3.2.2.1.5 | H_WA_AR_B07_Int Wall_Acid R Tile | F146
| 3.2.2.1.6 | H_WA_AR_B07_Int Wall_Acid R Tile_L Waterproof | F152
|  | [Etc. Tile] | F160 | 위치로 이동
| 3.2.2.1.7 | H_WA_AR_B07_Int Wall_Granite Tile | F161
| 3.2.2.1.8 | H_WA_AR_B07_Int Wall_Marble Tile | F167
|  | [Insulation + Gypsum] | F174 | 위치로 이동
| 3.2.2.1.7 | H_WA_AR_B07_Int Wall_Insulation_Gypsum
3.2.2.1.8
|  | [ETC] | F183 | 위치로 이동
| 3.2.2.1.7 | H_WA_AR_B07_Int Wall_Insulation | F184
3.2.2.1.8
| 3.3 | Curtain Wall
| 3.3.1 | □ Curtain Wall - normal
| 3.3.1.1 | ▶ Curtain Wall | F194 | 위치로 이동
| 3.3.1.1.1 | H_WA_AR_B02_Exterior Curtain Wall | F196
| 3.3.1.1.2 | H_WA_AR_B02_Pavillion Curtain Wall | F202
| 3.3.1.1.3 | H_WA_AR_B02_Storefront Curtain Wall | F208
| 3.4 | Stacked Wall
| 3.4.1 | □ Stacked Wall - normal
| 3.4.1.1 | ▶ Stacked Wall | F217 | 위치로 이동
| 3.4.1.1.1 | H_WA_AR_B02_Exterior-Brick Over CMU w Metal Stud | F219
4.St_Fdn
| No |  | 행위치 |  | Check Slot
| 4.1 | Foundation Slab
| 4.1.1 | □ Slab
| 4.1.1.1 | ▶ Mat Foundation for Building | F6 | 위치로 이동
| 4.1.1.1.1 | H_SF_AR_S18_MAT_Bitumen | F8
| 4.1.1.2 | ▶ Mat Foundation for Equipment | F28 | 위치로 이동
| 4.1.1.2.1 | H_SF_AR_B01_EQ FDN_Bitumen | F30
| 4.1.1.2.2 | H_SF_AR_B01_EQ FDN_CEP Can_Bitumen | F60
| 4.1.1.3 | ▶ Mass Concrete (Temperature Control) for Equipment | F77 | 위치로 이동
| 4.1.1.3.1 | H_SF_AR_B01_Mass_Bitumen | F79
| 4.1.1.4 | ▶ SOG Slab | F97 | 위치로 이동
| 4.1.1.4.1 | H_SF_AR_S17_SOG | F99
| 4.1.1.4.2 | H_SF_AR_S17_SOG_S Trowel | F121
| 4.1.1.4.2 | H_SF_AR_S17_Suspended | F141
| 4.1.1.4.2 | H_SF_AR_S17_Suspended_S Trowel | F163
| 4.1.1.5 | ▶ Pit, Trench Slab | F182 | 위치로 이동 | O
| 4.1.1.5.1 | H_FL_AR_B08_UG RC Slab_Pit | F184
| 4.1.1.5.2 | H_FL_AR_B08_UG RC Slab_Trench | F208
| 4.1.1.6 | ▶ SOG Slab Edge | F226 | 위치로 이동
| 4.1.1.6.1 | H_SF_AR_S17_SOG Edge | F228
| 4.1.1.7 | ▶ Stoop, Pathway with Haunch | F245 | 위치로 이동
| 4.1.1.7.1 | H_SF_AR_B08_Stoop | F247
| 4.1.1.7.2 | H_SF_AR_B08_Ramp | F260
| 4.1.1.8 | ▶ Lean Concrete | F273 | 위치로 이동
| 4.1.1.8.1 | H_SF_AR_S18_Lean | F275
| 4.1.1.8.2 | H_SF_AR_S18_Lean_Base_Subbase | F281
| 4.1.1.8.3 | H_SF_AR_S18_Lean_Bitumen_PE_Base_Subbase | F289
| 4.2 | Wall Foundation
| 4.2.1 | □ Wall Foundation - normal
| 4.2.1.1 | ▶ Wall Foundation | F301 | 위치로 이동
| 4.2.1.1.1 | H_SF_AR_S18_Wall Foundation
| 4.3 | Stacked Wall
| 4.3.1 | □ Stacked Wall - normal
| 4.3.1.1 | ▶ Stacked Wall | F337 | 위치로 이동
| 4.3.1.1.1 | H_SF_AR_S18_Stacked Wall | F339
| 4.4 | Foundation Rectangular
| 4.4.1 | □ Foundation Rectangular (Non-Pile)
| 4.4.1.1 | ▶ Shallow Foundation / Pile Cap(Pile 별도모델링) | F346 | 위치로 이동
| 4.4.1.1.1 | H_SF_AR_S18_Shallow Fdn_Bitumen | F348
| 4.5 | Pile
| 4.5.1 | □ Pile - normal
| 4.5.1.1 | ▶ Only Pile | F390 | 위치로 이동
| 4.5.1.1.1 | H_SF_AR_S19_Steel Pile | F392
| 4.5.1.1.2 | H_SF_AR_S19_PHC Pile_Driven | F399
| 4.5.1.1.3 | H_SF_AR_S19_PHC Pile_Pre-boring | F406
| 4.5.1.1.3 | H_SF_AR_S19_PHC Pile_Direct Driving | F413
Common User Input
Steel Common User Input
단위중량 기준 ( KG/M )
| Extra Heavy Steel | 200
| Heavy Steel | 90
Medium Steel
| Light Steel | 30
| Extra Light Steel | 10
5.St_Col
| No |  | 행위치 |  | Check Slot
| 5.1 | RC Columns
| 5.1.1 | □ RC_UG Pedestal
| 5.1.1.1 | ▶ RC_UG Pedestal | F6 | 위치로 이동
| 5.1.1.1.1 | H_SC_AR_S15_UG PED_Bit | F8
| 5.1.1.1.2 | H_SC_AR_S15_UG PED_Bit_Anchor | F21
| 5.1.1.1.3 | H_SC_AR_S15_UG PED_Grout only | F34
| 5.1.2 | □ RC_Column_Rectangular
| 5.1.2.1 | ▶ RC_Column Rectangular | F40 | 위치로 이동
| 5.1.2.1.1 | H_SC_AR_S15_AG Column | F42
| 5.2 | Steel Column
| 5.2.1 | □ Steel Column_W
| 5.2.1.1 | ▶ Steel Column_W_ASTM A6M | F60 | 위치로 이동
|  | [W-Extra Heavy Steel] | F61 | 위치로 이동
| 5.2.1.1.1 | H_SC_AR_S01_W (Extra Heavy)
|  | [W-Heavy Steel] | F72 | 위치로 이동
| 5.2.1.1.2 | H_SC_AR_S01_W (Heavy)
|  | [W-Medium Steel] | F83 | 위치로 이동
| 5.2.1.1.3 | H_SC_AR_S01_W (Medium)
|  | [W-Light Steel] | F94 | 위치로 이동
| 5.2.1.1.4 | H_SC_AR_S01_W (Light)
|  | [W-Extra Light Steel] | F105 | 위치로 이동
| 5.2.1.1.5 | H_SC_AR_S01_W (Extra Light)
| 5.2.2 | □ Steel Column_H
| 5.2.2.1 | ▶ Steel Column_H_KSD3502 | F117 | 위치로 이동
|  | [H-Extra Heavy Steel] | F118 | 위치로 이동
| 5.2.2.1.1 | H_SC_AR_S01_H (Extra Heavy)
|  | [H-Heavy Steel] | F129 | 위치로 이동
| 5.2.2.1.2 | H_SC_AR_S01_H (Heavy)
|  | [H-Medium Steel] | F140 | 위치로 이동
| 5.2.2.1.3 | H_SC_AR_S01_H (Medium)
|  | [H-Light Steel] | F151 | 위치로 이동
| 5.2.2.1.4 | H_SC_AR_S01_H (Light)
|  | [H-Extra Light Steel] | F162 | 위치로 이동
| 5.2.2.1.5 | H_SC_AR_S01_H (Extra Light)
| 5.2.3 | □ Steel Column_H_Built Up
| 5.2.3.1 | ▶ Steel Column_H_Built Up | F174 | 위치로 이동
|  | [BH-Extra Heavy Steel] | F175 | 위치로 이동
| 5.2.3.1.1 | H_SC_AR_S01_BH (Extra Heavy)
|  | [BH-Heavy Steel] | F184 | 위치로 이동
| 5.2.3.1.2 | H_SC_AR_S01_BH (Heavy)
|  | [BH-Medium Steel] | F193 | 위치로 이동
| 5.2.3.1.3 | H_SC_AR_S01_BH (Medium)
| 5.2.4 | □ Steel Column_SHS (Square Hollow Section)
| 5.2.4.1 | ▶ Steel Column_SHS_KSD3502 | F203 | 위치로 이동
|  | [SHS-Heavy Steel] | F204 | 위치로 이동
| 5.2.4.1.1 | H_SC_AR_S01_SHS (Heavy)
|  | [SHS-Medium Steel] | F213 | 위치로 이동
| 5.2.4.1.2 | H_SC_AR_S01_SHS (Medium)
|  | [SHS-Light Steel] | F222 | 위치로 이동
| 5.2.4.1.3 | H_SC_AR_S01_SHS (Light)
|  | [SHS-Extra Light Steel] | F231 | 위치로 이동
| 5.2.4.1.4 | H_SC_AR_S01_SHS (Extra Light)
| 5.2.5 | □ Steel Column_RHS (Rectangular Hollow Section)
| 5.2.5.1 | ▶ Steel Column_RHS_KSD3502 | F241 | 위치로 이동
|  | [RHS-Heavy Steel] | F242 | 위치로 이동
| 5.2.5.1.1 | H_SC_AR_S01_RHS (Heavy)
|  | [RHS-Medium Steel] | F251 | 위치로 이동
| 5.2.5.1.2 | H_SC_AR_S01_RHS (Medium)
|  | [RHS-Light Steel] | F260 | 위치로 이동
| 5.2.5.1.3 | H_SC_AR_S01_RHS (Light)
|  | [RHS-Extra Light Steel] | F269 | 위치로 이동
| 5.2.5.1.4 | H_SC_AR_S01_RHS (Extra Light)
| 5.2.6 | □ Steel Column_CHS (Circular Hollow Section)
| 5.2.6.1 | ▶ Steel Column_CHS_KSD3502 | F279 | 위치로 이동
|  | [CHS-Extra Heavy Steel] | F280 | 위치로 이동
| 5.2.6.1.1 | H_SC_AR_S01_CHS (Extra Heavy)
|  | [CHS-Heavy Steel] | F289 | 위치로 이동
| 5.2.6.1.2 | H_SC_AR_S01_CHS (Heavy)
|  | [CHS-Medium Steel] | F298 | 위치로 이동
| 5.2.6.1.3 | H_SC_AR_S01_CHS (Medium)
|  | [CHS-Light Steel] | F307 | 위치로 이동
| 5.2.6.1.4 | H_SC_AR_S01_CHS (Light)
|  | [CHS-Extra Light Steel] | F316 | 위치로 이동
| 5.2.6.1.5 | H_SC_AR_S01_CHS (Extra Light)
6.St_Framing
| No |  | 행위치 |  | Check Slot
| 6.1 | RC_Tie Girder
| 6.1.1 | □ RC_Beam / Girder
| 6.1.1.1 | ▶ Tie Girder | F6 | 위치로 이동
| 6.1.1.1.1 | H_SB_AR_S16_TG | F8
| 6.1.1.2 | ▶ RC Beam / Girder | F32 | 위치로 이동
| 6.1.1.2.1 | H_SB_AR_S16_AG | F34
| 6.2 | Steel Beam
| 6.2.1 | □ Steel Beam_W
| 6.2.1.1 | ▶ Steel Beam_W_ASTM A6 M | F83 | 위치로 이동
|  | [W-Extra Heavy Steel] | F84 | 위치로 이동
| 6.2.1.1.1 | H_SB_AR_S02_W (Extra Heavy)
|  | [W-Heavy Steel] | F96 | 위치로 이동
| 6.2.1.1.2 | H_SB_AR_S02_W (Heavy)
|  | [W-Medium Steel] | F108 | 위치로 이동
| 6.2.1.1.3 | H_SB_AR_S02_W (Medium)
|  | [W-Light Steel] | F120 | 위치로 이동
| 6.2.1.1.4 | H_SB_AR_S02_W (Light)
|  | [W-Extra Light Steel] | F132 | 위치로 이동
| 6.2.1.1.5 | H_SB_AR_S02_W (Extra Light)
| 6.2.2 | □ Steel Beam_H
| 6.2.2.1 | ▶ Steel Beam_H-KSD3502 | F145 | 위치로 이동
|  | [H-Extra Heavy Steel] | F146 | 위치로 이동
| 6.2.2.1.1 | H_SB_AR_S02_H (Extra Heavy)
|  | [H-Heavy Steel] | F158 | 위치로 이동
| 6.2.2.1.2 | H_SB_AR_S02_H (Heavy)
|  | [H-Medium Steel] | F170 | 위치로 이동
| 6.2.2.1.3 | H_SB_AR_S02_H (Medium)
|  | [H-Light Steel] | F186 | 위치로 이동
| 6.2.2.1.4 | H_SB_AR_S02_H (Light)
|  | [H-Extra Light Steel] | F198 | 위치로 이동
| 6.2.2.1.5 | H_SB_AR_S02_H (Extra Light)
| 6.2.3 | □ Steel Beam_BH
| 6.2.3.1 | ▶ Steel Beam_H-Built Up | F211 | 위치로 이동
|  | [BH-Extra Heavy Steel] | F212 | 위치로 이동
| 6.2.3.1.1 | H_SB_AR_S02_BH (Extra Heavy)
|  | [BH-Heavy Steel] | F224 | 위치로 이동
| 6.2.3.1.2 | H_SB_AR_S02_BH (Heavy)
|  | [BH-Medium Steel] | F236 | 위치로 이동
| 6.2.3.1.3 | H_SB_AR_S02_BH (Medium)
| 6.2.4 | □ Steel Beam_SHS (Square Hollow Section)
| 6.2.4.1 | ▶ Steel Beam_SHS_KSD | F249 | 위치로 이동
|  | [SHS-Heavy Steel] | F250 | 위치로 이동
| 6.2.4.1.1 | H_SB_AR_S02_SHS (Heavy)
|  | [SHS-Medium Steel] | F262 | 위치로 이동
| 6.2.4.1.2 | H_SB_AR_S02_SHS (Medium)
|  | [SHS-Light Steel] | F274 | 위치로 이동
| 6.2.4.1.3 | H_SB_AR_S02_SHS (Light)
|  | [SHS-Extra Light Steel] | F286 | 위치로 이동
| 6.2.4.1.4 | H_SB_AR_S02_SHS (Extra Light)
| 6.2.5 | □ Steel Beam_RHS (Rectangular Hollow Section)
| 6.2.5.1 | ▶ Steel Beam_RHS_KSD | F299 | 위치로 이동
|  | [RHS-Heavy Steel] | F300 | 위치로 이동
| 6.2.5.1.1 | H_SB_AR_S02_RHS (Heavy)
|  | [RHS-Medium Steel] | F312 | 위치로 이동
| 6.2.5.1.2 | H_SB_AR_S02_RHS (Medium)
|  | [RHS-Light Steel] | F324 | 위치로 이동
| 6.2.5.1.3 | H_SB_AR_S02_RHS (Light)
|  | [RHS-Extra Light Steel] | F336 | 위치로 이동
| 6.2.5.1.4 | H_SB_AR_S02_RHS (Extra Light)
| 6.2.6 | □ Steel Beam_CHS (Circular Hollow Section)
| 6.2.6.1 | ▶ Steel Beam_CHS_KSD | F349 | 위치로 이동
|  | [CHS-Extra Heavy Steel] | F350 | 위치로 이동
| 6.2.6.1.1 | H_SB_AR_S02_CHS (Extra Heavy)
|  | [CHS-Heavy Steel] | F364 | 위치로 이동
| 6.2.6.1.2 | H_SB_AR_S02_CHS (Heavy)
|  | [CHS-Medium Steel] | F378 | 위치로 이동
| 6.2.6.1.3 | H_SB_AR_S02_CHS (Medium)
|  | [CHS-Light Steel] | F392 | 위치로 이동
| 6.2.6.1.4 | H_SB_AR_S02_CHS (Light)
|  | [CHS-Extra Light Steel] | F406 | 위치로 이동
| 6.2.6.1.5 | H_SB_AR_S02_CHS (Extra Light)
| 6.2.7 | □ Steel Beam_Channel
| 6.2.7.1 | ▶ Steel Beam_Channel_KSD | F421 | 위치로 이동
|  | [C-Heavy Steel] | F422 | 위치로 이동
| 6.2.7.1.1 | H_SB_AR_S02_C (Heavy)
|  | [C-Medium Steel] | F434 | 위치로 이동
| 6.2.7.1.2 | H_SB_AR_S02_C (Medium)
|  | [C-Light Steel] | F446 | 위치로 이동
| 6.2.7.1.3 | H_SB_AR_S02_C (Light)
| 6.2.8 | □ Steel Beam_Angle
| 6.2.8.1 | ▶ Steel Beam_Angle_KSD | F459 | 위치로 이동
|  | [L-Heavy Steel] | F460 | 위치로 이동
| 6.2.8.1.1 | H_SB_AR_S02_L (Heavy)
|  | [L-Medium Steel] | F472 | 위치로 이동
| 6.2.8.1.2 | H_SB_AR_S02_L (Medium)
|  | [L-Light Steel] | F484 | 위치로 이동
| 6.2.8.1.3 | H_SB_AR_S02_L (Light)
| 6.2.9 | □ Steel Beam_Tee
| 6.2.9.1 | ▶ Steel Beam_Tee_KSD | F497 | 위치로 이동
|  | [CT-Heavy Steel] | F498 | 위치로 이동
| 6.2.9.1.1 | H_SB_AR_S02_CT (Heavy)
|  | [CT-Medium Steel] | F510 | 위치로 이동
| 6.2.9.1.2 | H_SB_AR_S02_CT (Medium)
|  | [CT-Light Steel] | F522 | 위치로 이동
| 6.2.9.1.3 | H_SB_AR_S02_CT (Light)
| 6.3 | Steel Hori. Brace
| 6.3.1 | □ Steel Hori. Brace_Angle
| 6.3.1.1 | ▶ Steel Hori. Brace_Angle_KSD | F545 | 위치로 이동
|  | [L-HB-Heavy Steel] | F546 | 위치로 이동
| 6.3.1.1.1 | H_SB_AR_S03_L (Heavy)
|  | [L-HB-Medium Steel] | F555 | 위치로 이동
| 6.3.1.1.2 | H_SB_AR_S03_L (Medium)
|  | [L-HB-Light Steel] | F564 | 위치로 이동
| 6.3.1.1.3 | H_SB_AR_S03_L (Light)
| 6.3.2 | □ Steel Hori. Brace_CHS (Circular Hollow Section)
| 6.3.2.1 | ▶ Steel Hori. Brace_CHS_KSD | F574 | 위치로 이동
|  | [CHS-HB-Heavy Steel] | F575 | 위치로 이동
| 6.3.2.1.1 | H_SB_AR_S03_CHS (Heavy)
|  | [CHS-HB-Medium Steel] | F584 | 위치로 이동
| 6.3.2.1.2 | H_SB_AR_S03_CHS (Medium)
|  | [CHS-HB-Light Steel] | F593 | 위치로 이동
| 6.3.2.1.3 | H_SB_AR_S03_CHS (Light)
| 6.3.3 | □ Steel Hori. Brace_Double Angle
| 6.3.3.1 | ▶ Steel Hori. Brace_2Ls_KSD | F603 | 위치로 이동
|  | [2Ls-HB-Heavy Steel] | F604 | 위치로 이동
| 6.3.3.1.1 | H_SB_AR_S03_2Ls (Heavy)
|  | [2Ls-HB-Medium Steel] | F613 | 위치로 이동
| 6.3.3.1.2 | H_SB_AR_S03_2Ls (Medium)
|  | [2Ls-HB-Light Steel] | F622 | 위치로 이동
| 6.3.3.1.3 | H_SB_AR_S03_2Ls (Light)
| 6.4 | Steel Ver. Brace
| 6.4.1 | □ Steel Ver. Brace_Angle
| 6.4.1.1 | ▶ Steel Ver. Brace_Angle_KSD | F642 | 위치로 이동
|  | [L-VB-Heavy Steel] | F643 | 위치로 이동
| 6.4.1.1.1 | H_SB_AR_S04_L (Heavy)
|  | [L-VB-Medium Steel] | F652 | 위치로 이동
| 6.4.1.1.2 | H_SB_AR_S04_L (Medium)
|  | [L-VB-Light Steel] | F661 | 위치로 이동
| 6.4.1.1.3 | H_SB_AR_S04_L (Light)
| 6.4.2 | □ Steel Ver. Brace_CHS (Circular Hollow Section)
| 6.4.2.1 | ▶ Steel Ver. Brace_CHS_KSD | F671 | 위치로 이동
|  | [CHS-VB-Heavy Steel] | F672 | 위치로 이동
| 6.4.2.1.1 | H_SB_AR_S04_CHS (Heavy)
|  | [CHS-VB-Medium Steel] | F681 | 위치로 이동
| 6.4.2.1.2 | H_SB_AR_S04_CHS (Medium)
|  | [CHS-VB-Light Steel] | F690 | 위치로 이동
| 6.4.2.1.3 | H_SB_AR_S04_CHS (Light)
| 6.4.3 | □ Steel Ver. Brace_Double Angle
| 6.4.3.1 | ▶ Steel Ver. Brace_2Ls_KSD | F700 | 위치로 이동
|  | [2Ls-VB-Heavy Steel] | F701 | 위치로 이동
| 6.4.3.1.1 | H_SB_AR_S04_2Ls (Heavy)
|  | [2Ls-VB-Medium Steel] | F710 | 위치로 이동
| 6.4.3.1.2 | H_SB_AR_S04_2Ls (Medium)
|  | [2Ls-VB-Light Steel] | F719 | 위치로 이동
| 6.4.3.1.3 | H_SB_AR_S04_2Ls (Light)
| 6.5 | Steel Purlin
| 6.5.1 | □ Steel Purlin_LC
| 6.5.1.1 | ▶ Steel Purlin_LC_KSD | F732 | 위치로 이동
| 6.5.1.1.1 | H_SB_AR_B03_LC | F734
| 6.6 | Steel Girth
| 6.6.1 | □ Steel Girth_LC
| 6.6.1.1 | ▶ Steel Girth_LC_KSD | F745 | 위치로 이동
| 6.6.1.1.1 | H_SB_AR_B04_LC | F747
7.Ceilings
| No |  | 행위치 |  | Check Slot
| 7.1 | Ceiling
| 7.1.1 | □ Basic Ceiling
| 7.1.1.1 | ▶ Simple Ceiling | F6 | 위치로 이동
| 7.1.1.1.1 | H_CE_AR_B09_Acrylic Emulsion Paint | F8
| 7.1.2 | □ Compound Ceiling - normal
| 7.1.2.1 | ▶ Compound Ceiling | F14 | 위치로 이동
| 7.1.2.1.1 | H_CE_AR_B09_Acoustic Ceiling_T Bar | F16
| 7.1.2.1.2 | H_CE_AR_B09_Moisture Resistant Ceiling_M Bar | F22
8.Doors
| No |  | 행위치 |  | Check Slot
| 8.1 | Single Door
| 8.1.1 | □ Single Door - normal
| 8.1.1.1 | ▶ Single Door_Steel | F6 | 위치로 이동
| 8.1.1.1.1 | H_DR_AR_B12_Single Door_Steel | F8
| 8.1.1.1.2 | H_DR_AR_B12_Single Door_Steel_Vision | F16
| 8.1.1.1.3 | H_DR_AR_B12_Single Door_Steel_Panic | F24
| 8.1.1.1.4 | H_DR_AR_B12_Single Door_Steel_Vision_Panic | F32
| 8.1.1.2 | ▶ Single Door_Blast | F40 | 위치로 이동
| 8.1.1.2.1 | H_DR_AR_B12_Single Door_Blast | F42
| 8.1.1.2.2 | H_DR_AR_B12_Single Door_Blast_Panic | F50
| 8.1.1.3 | ▶ Single Door_Aluminum | F58 | 위치로 이동
| 8.1.1.3.1 | H_DR_AR_B12_Single Door_AL | F60
| 8.1.1.3.2 | H_DR_AR_B12_Single Door_AL_Vision | F68
| 8.1.1.3.3 | H_DR_AR_B12_Single Door_AL_Panic | F76
| 8.1.1.3.4 | H_DR_AR_B12_Single Door_AL_Vision_Panic | F84
| 8.1.1.4 | ▶ Single Door_Glass | F92 | 위치로 이동
| 8.1.1.4.1 | H_DR_AR_B12_Single Door_Glass | F94
| 8.1.1.5 | ▶ Single Door_SST | F102 | 위치로 이동
| 8.1.1.5.1 | H_DR_AR_B12_Single Door_SST | F104
| 8.1.1.6 | ▶ Single Door_Wood | F112 | 위치로 이동
| 8.1.1.6.1 | H_DR_AR_B12_Single Door_Wood | F114
| 8.1.1.6.2 | H_DR_AR_B12_Single Door_Wood_Vision | F122
| 8.1.1.7 | ▶ Single Door_uPVC | F130 | 위치로 이동
| 8.1.1.7.1 | H_DR_AR_B12_Single Door_uPVC | F132
| 8.2 | Double Door
| 8.2.1 | □ Double Door - normal
| 8.2.1.1 | ▶ Double Door_Steel | F143 | 위치로 이동
| 8.2.1.1.1 | H_DR_AR_B12_Double Door_Steel | F145
| 8.2.1.1.2 | H_DR_AR_B12_Double Door_Steel_Vision | F153
| 8.2.1.1.3 | H_DR_AR_B12_Double Door_Steel_Panic | F161
| 8.2.1.1.4 | H_DR_AR_B12_Double Door_Steel_Vision_Panic | F169
| 8.2.1.2 | ▶ Double Door_Blast | F177 | 위치로 이동
| 8.2.1.2.1 | H_DR_AR_B12_Double Door_Blast | F179
| 8.2.1.2.2 | H_DR_AR_B12_Double Door_Blast_Panic | F187
| 8.2.1.3 | ▶ Double Door_Aluminum | F195 | 위치로 이동
| 8.2.1.3.1 | H_DR_AR_B12_Double Door_AL | F197
| 8.2.1.3.2 | H_DR_AR_B12_Double Door_AL_Vision | F205
| 8.2.1.3.3 | H_DR_AR_B12_Double Door_AL_Panic | F213
| 8.2.1.3.4 | H_DR_AR_B12_Double Door_AL_Vision_Panic | F221
| 8.2.1.4 | ▶ Double Door_Glass | F229 | 위치로 이동
| 8.2.1.4.1 | H_DR_AR_B12_Double Door_Glass | F231
| 8.2.1.5 | ▶ Double Door_SST | F239 | 위치로 이동
| 8.2.1.5.1 | H_DR_AR_B12_Double Door_SST | F241
| 8.2.1.6 | ▶ Double Door_Wood | F249 | 위치로 이동
| 8.2.1.6.1 | H_DR_AR_B12_Double Door_Wood | F251
| 8.2.1.6.2 | H_DR_AR_B12_Double Door_Wood_Vision | F259
| 8.3 | Double Door + Transsom
| 8.3.1 | □ Double Door + Transsom - normal
| 8.3.1.1 | ▶ Double Door_Steel_Transsom | F270 | 위치로 이동
| 8.3.1.1.1 | H_DR_AR_B12_Double Door_Steel_Transsom | F272
| 8.3.1.1.2 | H_DR_AR_B12_Double Door_Steel_Vision_Transsom | F280
| 8.3.1.1.3 | H_DR_AR_B12_Double Door_Steel_Panic_Transsom | F288
| 8.3.1.1.4 | H_DR_AR_B12_Double Door_Steel_Vision_Panic_Transsom | F296
| 8.3.1.2 | ▶ Double Door_Blast_Transsom | F304 | 위치로 이동
| 8.3.1.2.1 | H_DR_AR_B12_Double Door_Blast_Transsom | F306
| 8.3.1.2.2 | H_DR_AR_B12_Double Door_Blast_Panic_Transsom | F314
| 8.4 | Etc.
| 8.4.1 | □ Etc. - normal
| 8.4.1.1 | ▶ Shutter | F325
|  | [Roll up Steel] | F326 | 위치로 이동
| 8.4.1.1.1 | H_DR_AR_B12_Roll up Door_Steel_Manual | F327
| 8.4.1.1.2 | H_DR_AR_B12_Roll up Door_Steel_Motor | F335
|  | [Roll up Blast] | F344 | 위치로 이동
| 8.4.1.1.3 | H_DR_AR_B12_Roll up Door_Blast_Manual | F345
| 8.4.1.1.4 | H_DR_AR_B12_Roll up Door_Blast_Motor | F353
|  | [Roll up Aluminum] | F362 | 위치로 이동
| 8.4.1.1.5 | H_DR_AR_B12_Roll up Door_AL_Manual | F363
| 8.4.1.1.6 | H_DR_AR_B12_Roll up Door_AL_Motor | F371
| 8.4.1.2 | ▶ Sliding | F379
|  | [Sliding Door Steel] | F380 | 위치로 이동
| 8.4.1.2.1 | H_DR_AR_B12_Sliding Door_Steel_Manual | F381
| 8.4.1.2.2 | H_DR_AR_B12_Sliding Door_Steel_Motor | F387
|  | [Sliding Door Aluminum] | F394 | 위치로 이동
| 8.4.1.2.3 | H_DR_AR_B12_Sliding Door_AL_Manual | F395
| 8.4.1.2.4 | H_DR_AR_B12_Sliding Door_AL_Motor | F401
|  | [Sliding Door Glass] | F408 | 위치로 이동
| 8.4.1.2.5 | H_DR_AR_B12_Sliding Door_Glass_Manual | F409
| 8.4.1.2.6 | H_DR_AR_B12_Sliding Door_Glass_Motor | F415
| 8.4.1.3 | ▶ Hanger | F421 | 위치로 이동
| 8.4.1.3.1 | H_DR_AR_B12_Hanger Door_Steel | F423
| 8.4.1.4 | ▶ Swing | F429 | 위치로 이동
| 8.4.1.4.1 | H_DR_AR_B12_Swing Door_Steel | F431
| 8.4.1.4.2 | H_DR_AR_B12_Swing Door_AL | F437
| 8.4.1.5 | ▶ Revolving | F443 | 위치로 이동
| 8.4.1.5.1 | H_DR_AR_B12_Revolving Door_Manual | F445
| 8.4.1.5.2 | H_DR_AR_B12_Revolving Door_Auto | F451
| 8.4.1.6 | ▶ Folding | F457
|  | [Folding Door Steel] | F458 | 위치로 이동
| 8.4.1.6.1 | H_DR_AR_B12_Folding Door_Steel_Manual | F459
| 8.4.1.6.2 | H_DR_AR_B12_Folding Door_Steel_Motor | F465
|  | [Folding Door Aluminum] | F472 | 위치로 이동
| 8.4.1.6.3 | H_DR_AR_B12_Folding Door_AL_Manual | F473
| 8.4.1.6.4 | H_DR_AR_B12_Folding Door_AL_Motor | F479
|  | [Folding Door Etc.] | F486 | 위치로 이동
| 8.4.1.6.5 | H_DR_AR_B12_Folding Door_PVC_Manual | F487
| 8.4.1.6.6 | H_DR_AR_B12_Folding Door_Glass_Manual | F493
9.Windows
| No |  | 행위치 |  | Check Slot
| 9.1 | Sliding Type Window
| 9.1.1 | □ Sliding Type
| 9.1.1.1 | ▶ Steel Window (Sliding) | F6 | 위치로 이동
| 9.1.1.1.1 | H_WD_AR_B11_Sliding_Steel Window | F8
| 9.1.1.2 | ▶ Aluminum Window (Sliding) | F16 | 위치로 이동
| 9.1.1.2.1 | H_WD_AR_B11_Sliding_AL Window | F18
| 9.1.1.3 | ▶ uPVC Window (Sliding) | F26 | 위치로 이동
| 9.1.1.3.1 | H_WD_AR_B11_Sliding_uPVC Window | F28
| 9.1.1.4 | ▶ Blast Resistant Window (Sliding) | F36 | 위치로 이동
| 9.1.1.4.1 | H_WD_AR_B11_Sliding_Blast Window | F38
| 9.1.1.5 | ▶ Bullet-Proof Steel Window (Sliding) | F46 | 위치로 이동
| 9.1.1.5.1 | H_WD_AR_B11_Sliding_Bullet-Proof Steel Window | F48
| 9.2 | Awning Type Window
| 9.2.1 | □ Awning Type
| 9.2.1.1 | ▶ Steel Window (Awning) | F59 | 위치로 이동
| 9.2.1.1.1 | H_WD_AR_B11_Awning_Steel Window | F61
| 9.2.1.2 | ▶ Aluminum Window (Awning) | F69 | 위치로 이동
| 9.2.1.2.1 | H_WD_AR_B11_Awning_AL Window | F71
| 9.2.1.3 | ▶ uPVC Window (Awning) | F79 | 위치로 이동
| 9.2.1.3.1 | H_WD_AR_B11_Awning_uPVC Window | F81
| 9.2.1.4 | ▶ Blast Resistant Window (Awning) | F89 | 위치로 이동
| 9.2.1.4.1 | H_WD_AR_B11_Awning_Blast Window | F91
| 9.2.1.5 | ▶ Bullet-Proof Steel Window (Awning) | F99 | 위치로 이동
| 9.2.1.5.1 | H_WD_AR_B11_Awning_Bullet-Proof Steel Window | F101
| 9.3 | Fix Type Window
| 9.3.1 | □ Fix Type
| 9.3.1.1 | ▶ Steel Window (Fix) | F112 | 위치로 이동
| 9.3.1.1.1 | H_WD_AR_B11_Fix_Steel Window | F114
| 9.3.1.2 | ▶ Aluminum Window (Fix) | F122 | 위치로 이동
| 9.3.1.2.1 | H_WD_AR_B11_Fix_AL Window | F124
| 9.3.1.3 | ▶ uPVC Window (Fix) | F132 | 위치로 이동
| 9.3.1.3.1 | H_WD_AR_B11_Fix_uPVC Window | F134
| 9.3.1.4 | ▶ Blast Resistant Window (Fix) | F142 | 위치로 이동
| 9.3.1.4.1 | H_WD_AR_B11_Fix_Blast R Window
| 9.3.1.5 | ▶ Bullet-Proof Steel Window (Fix) | F152 | 위치로 이동
| 9.3.1.5.1 | H_WD_AR_B11_Fix_Bullet-Proof Steel Window | F154
| 9.4 | Combination Type Window
| 9.4.1 | □ Fix + Awning
| 9.4.1.1 | ▶ Steel Window (Fix + Awning) | F165 | 위치로 이동
| 9.4.1.1.1 | H_WD_AR_B11_Fix_Awning_Steel Window | F167
| 9.4.1.2 | ▶ Aluminum Window (Fix + Awning) | F175 | 위치로 이동
| 9.4.1.2.1 | H_WD_AR_B11_Fix_Awning_AL Window | F177
| 9.4.1.3 | ▶ uPVC Window (Fix + Awning) | F185 | 위치로 이동
| 9.4.1.3.1 | H_WD_AR_B11_Fix_Awning_uPVC Window | F187
| 9.5 | Skylight
| 9.5.1 | □ Skylight - normal
| 9.5.1.1 | ▶ Skylight | F198 | 위치로 이동
| 9.5.1.1.1 | H_WD_AR_B11_Skylight | F200
| 9.6 | MISC Window
| 9.6.1 | □ MISC
| 9.6.1.1 | ▶ Casement_Aluminum Window | F211 | 위치로 이동
| 9.6.1.1.1 | H_WD_AR_B11_Casement_AL Window | F213
| 9.6.1.2 | ▶ Hung_Aluminum Window | F219 | 위치로 이동
| 9.6.1.2.1 | H_WD_AR_B11_Hung_AL Window | F221
| 9.6.1.3 | ▶ Tilt_Aluminum Window | F229 | 위치로 이동
| 9.6.1.3.1 | H_WD_AR_B11_Tilt_AL Window | F231
| 9.6.1.4 | ▶ Center Pivotilt_Aluminum Window | F239 | 위치로 이동
| 9.6.1.4.1 | H_WD_AR_B11_Center Pivot_AL Window | F241
| 9.7 | Louver
| 9.7.1 | □ Louver - normal
| 9.7.1.1 | ▶ Louver | F252 | 위치로 이동
| 9.7.1.1.1 | H_WD_AR_B11_Louver | F254
10.Stairs
| No |  | 행위치 |  | Check Slot
| 10.1 | Assembled Stair
| 10.1.1 | □ Assembled Stair - normal
| 10.1.1.1 | ▶ Assembled Stair | F6 | 위치로 이동
| 10.1.1.1.1 | H_SR_AR_S09_Steel Stair | F8
| 10.2 | Precast Stair
| 10.2.1 | □ Precast Stair - normal
| 10.2.1.1 | ▶ Precast Stair | F18 | 위치로 이동
| 10.2.1.1.1 | H_SR_AR_B08_Concrete Stair_Outdoor | F20
11.Railings
| No |  | 행위치 |  | Check Slot
| 11.1 | Railing
| 11.1.1 | □ Railing - normal
| 11.1.1.1 | ▶ Steel Handrail | F6 | 위치로 이동
| 11.1.1.1.1 | H_RL_AR_S10_Steel Handrail | F8
| 11.1.1.1.2 | H_RL_AR_S11_Steel Removable Handrail | F19
12.Generic
| No |  | 행위치 |  | Check Slot
| 12.1 | Ladder
| 12.1.1 | □ Ladder - normal
| 12.1.1.1 | ▶ Caged Ladder | F6 | 위치로 이동
| 12.1.1.1.1 | H_GM_AR_S08_Caged Ladder | F8
| 12.1.1.2 | ▶ Non Caged Ladder | F17 | 위치로 이동
| 12.1.1.2.1 | H_GM_AR_S08_Non Caged Ladder | F19
| 12.2 | Bollard
| 12.2.1 | □ Bollard - normal
| 12.2.1.1 | ▶ Steel Bollard | F30 | 위치로 이동
| 12.2.1.1.1 | H_GM_AR_B07_Steel Bollard | F32
| 12.3 | Rain Drainage
| 12.3.1 | □ Roof Drain - normal
| 12.3.1.1 | ▶ Roof Drain | F41 | 위치로 이동
| 12.3.1.1.1 | H_GM_AR_B07_Roof Drain | F43
| 12.3.2 | □ Downspout & Splash Block
| 12.3.2.1 | ▶ Downspout | F49 | 위치로 이동
| 12.3.2.1.1 | H_GM_AR_B07_Steel Downspout | F51
| 12.3.2.2 | ▶ Splash Block | F57
| 12.3.2.2.1 | H_GM_AR_B07_Splash Block | F59
| 12.4 | Grout
| 12.4.1 | □ Grout - normal
| 12.4.1.1 | ▶ Grouting | F68 | 위치로 이동
| 12.4.1.1.1 | H_GM_AR_B07_Grouting | F70
| 12.5 | MISC
| 12.5.1 | □ MISC - normal
| 12.5.1.1 | ▶ Room Signage | F79 | 위치로 이동
| 12.5.1.1.1 | H_GM_AR_B07_Room Signage | F81
Lv1 | 13.Manual_Input | (모델링 없이 직접 산출한 물량 입력)
| No |  | 행위치 |  | Check Slot
Lv2 | 13.1 | Ladder
Lv3 | 13.1.1 | □ Ladder - normal
Lv4 | 13.1.1.1 | ▶ Caged Ladder | F6 | 위치로 이동
| 13.1.1.1.1 | H_MI_AR_S08_Caged Ladder | F8
| 13.1.1.2 | ▶ Non Caged Ladder | F16 | 위치로 이동
| 13.1.1.2.1 | H_MI_AR_S08_Non Caged Ladder | F18
Lv2 | 13.2 | Bollard
Lv3 | 13.2.1 | □ Bollard - normal
Lv4 | 13.2.1.1 | ▶ Steel Bollard | F29 | 위치로 이동
| 13.2.1.1.1 | H_MI_AR_B07_Steel Bollard | F31
Lv2 | 13.3 | Rain Drainage
Lv3 | 13.3.1 | □ Rain Drainage
Lv4 | 13.3.1.1 | ▶ Roof Drain | F40 | 위치로 이동
| 13.3.1.1.1 | H_MI_AR_B07_Roof Drain | F42
Lv4 | 13.3.1.2 | ▶ Downspout | F47 | 위치로 이동
| 13.3.1.2.1 | H_MI_AR_B07_Steel Downspout | F49
Lv4 | 13.3.1.3 | ▶ Gutter | F54 | 위치로 이동
| 13.3.1.3.1 | H_MI_AR_B07_Steel Eave Gutter | F56
Lv4 | 13.3.1.4 | ▶ Splash Block | F61 | 위치로 이동
| 13.3.1.4.1 | H_MI_AR_B07_Splash Block | F63
Lv2 | 13.4 | Grout
Lv3 | 13.4.1 | □ Grout
Lv4 | 13.4.1.1 | ▶ Grouting | F71 | 위치로 이동
| 13.4.1.1.1 | H_MI_AR_B07_Grouting | F73
Lv2 | 13.5 | Anchor Bolt
Lv3 | 13.5.1 | □ Anchor Bolt
Lv4 | 13.5.1.1 | ▶ Anchor Bolt - Substructure | F81 | 위치로 이동
| 13.5.1.1.1 | H_MI_AR_B07_Anchor Bolt_Substructure | F83
Lv4 | 13.5.1.2 | ▶ Anchor Bolt - Equipment Foundation | F95 | 위치로 이동
| 13.5.1.2.1 | H_MI_AR_B07_Anchor Bolt_Equipment Foundation | F97
Lv4 | 13.5.1.3 | ▶ Anchor Bolt - Mass Concrete | F103 | 위치로 이동
| 13.5.1.3.1 | H_MI_AR_B07_Anchor Bolt_Mass Concrete | F105
Lv2 | 13.6 | Embedded Steel
Lv3 | 13.6.1 | □ Embedded Steel
Lv4 | 13.6.1.1 | ▶ Embedded Steel | F114 | 위치로 이동
| 13.6.1.1.1 | H_MI_AR_B07_Embedded Steel | F116
Lv2 | 13.7 | Room, Toilt, Shower
Lv3 | 13.7.1 | □ Room, Toilt, Shower
Lv4 | 13.7.1.1 | ▶ Signage | F125 | 위치로 이동
| 13.7.1.1.1 | H_MI_AR_B07_Signage | F127
Lv4 | 13.7.1.2 | ▶ Toilet Accessories | F134 | 위치로 이동
| 13.7.1.2.1 | H_MI_AR_B07_Toilet Accessories | F136
Lv4 | 13.7.1.3 | ▶ Septic Tank | F146 | 위치로 이동
| 13.7.1.3.1 | H_MI_AR_B07_Septic Tank | F148
Lv2 | 13.8 | Furniture Installation
Lv3 | 13.8.1 | □ Furniture Installation
Lv4 | 13.8.1.1 | ▶ Furniture Installation | F156 | 위치로 이동
| 13.8.1.1.1 | H_MI_AR_B07_Furniture Installation | F158
[Family Name 분류 체계]
- Lv1 : Family Category 1단계
- LV2 : Family Category 2단계, Standard Hierarchy
- Lv3 : □ / 팀 표준 설계 정보 (Large)
- Lv4 : ▶ / 팀 표준 설계 정보 (Middle, Small)
- Lv5 : 동일 WM Group
- Lv6 : User 추가
R4-Fence 추가
R4- Plaster 추가
R4-13. Manual Input 추가
항목 추가
패밀리는 표준템플릿에서 삭제하되 STOOP, RAMP용 분류는 유지.
SOG 패밀리 이용
Suspended Slab 타입 추가
Equipment Pad 타입 추가

## 참조용_Int Finish_Style-WM_DB
(숨김 시트)"링크용_Int Finish Style-WM DB"에서 붙여넣기 |  | 스타일 선택 용 데이터 유효성 처리 구간
F01 | ¦ A04AM080-00001 ¦ ¦ | F01 | B01 | W01A | C01 | TRUE | FALSE | FALSE | FALSE
F01-1 | ¦ A04AM080-00001 ¦ ¦ A04AS168-00003 | F01-1 | B02 | W01B | C02 | TRUE | FALSE | FALSE | FALSE
F02 | ¦ A04AM080-00002 ¦ ¦ | F02 | B03 | W01C | C03 | TRUE | FALSE | FALSE | FALSE
F03 | ¦ A04AM080-00003 ¦ ¦ | F03 | B04 | W02A | C04 | TRUE | FALSE | FALSE | FALSE
F04 | ¦ A04AM080-00004 ¦ ¦ | F04 | B31 | W02B | C05 | TRUE | FALSE | FALSE | FALSE
F05 | ¦ A04AM080-00005 ¦ ¦ | F05 | B32 | W02C | C06 | TRUE | FALSE | FALSE | FALSE
F06A | ¦ A04AM080-00006 ¦ ¦ | F06A | B33 | W03A | C91A | TRUE | FALSE | FALSE | FALSE
F06B | ¦ A04AM080-00006 ¦ ¦ A04AS168-00003 | F06B | B34 | W03B | C91B | TRUE | FALSE | FALSE | FALSE
F07A | ¦ A04AM080-00007 ¦ ¦ | F07A | B35 | W03C | C92 | TRUE | FALSE | FALSE | FALSE
F07B | ¦ A04AM080-00007 ¦ ¦ | F07B | B36 | W04A | C93 | TRUE | FALSE | FALSE | FALSE
F07C | ¦ A04AM080-00007 ¦ ¦ | F07C | B37 | W04B | C94A | TRUE | FALSE | FALSE | FALSE
F08 | ¦ A04AM080-00008 ¦ ¦ | F08 | B38 | W04C | C94B | TRUE | FALSE | FALSE | FALSE
F09 | ¦ A04AM080-00009 ¦ ¦ | F09 | B39 | W05A | C95A | TRUE | FALSE | FALSE | FALSE
F10 | ¦ A04AM080-00010 ¦ ¦ | F10 | B40 | W05B | C95B | TRUE | FALSE | FALSE | FALSE
F11 | ¦ A04AM080-00011 ¦ ¦ | F11 | B41 | W05C | C96A | TRUE | FALSE | FALSE | FALSE
F31A | ¦ A04AN083-00001 ¦ ¦ | F31A | B42 | W06 | C96B | TRUE | FALSE | FALSE | FALSE
F31B | ¦ A04AN083-00001 ¦ A04AP085-00001 ¦ A04AS168-00003 | F31B |  | W07 | C97 | TRUE | FALSE | FALSE | FALSE
F31C | ¦ A04AN083-00001 ¦ A04AP310-00001 ¦ A04AS168-00003 | F31C |  | W08 | C98 | TRUE | FALSE | FALSE | FALSE
F32A | ¦ A04AN083-00002 ¦ ¦ | F32A |  | W09A |  | TRUE | FALSE | FALSE | FALSE
F32B | ¦ A04AN083-00002 ¦ A04AP085-00001 ¦ A04AS168-00003 | F32B |  | W09B |  | TRUE | FALSE | FALSE | FALSE
F33 | ¦ A04AN083-00003 ¦ ¦ | F33 |  | W09C |  | TRUE | FALSE | FALSE | FALSE
F34A | ¦ A04AN083-00004 ¦ ¦ | F34A |  | W31A |  | TRUE | FALSE | FALSE | FALSE
F34B | ¦ A04AN083-00004 ¦ ¦ A04AS168-00003 | F34B |  | W31B |  | TRUE | FALSE | FALSE | FALSE
F35 | ¦ A04AN083-00005 ¦ ¦ | F35 |  | W32A |  | TRUE | FALSE | FALSE | FALSE
F36 | ¦ A04AN083-00006 ¦ ¦ | F36 |  | W32B |  | TRUE | FALSE | FALSE | FALSE
F37 | ¦ A04AN083-00007 ¦ ¦ | F37 |  | W32C |  | TRUE | FALSE | FALSE | FALSE
F38 | ¦ A04AN083-00008 ¦ ¦ | F38 |  | W32D |  | TRUE | FALSE | FALSE | FALSE
F39 | ¦ A04AN083-00009 ¦ ¦ | F39 |  | W32E |  | TRUE | FALSE | FALSE | FALSE
F40 | ¦ A04AN083-00010 ¦ ¦ | F40 |  | W32F |  | TRUE | FALSE | FALSE | FALSE
F41 | ¦ A04AN083-00011 ¦ ¦ | F41 |  | W33A |  | TRUE | FALSE | FALSE | FALSE
F42 | ¦ A04AN083-00012 ¦ ¦ | F42 |  | W33B |  | TRUE | FALSE | FALSE | FALSE
F43 | ¦ A04AS170-00001 ¦ ¦ | F43 |  | W33C |  | TRUE | FALSE | FALSE | FALSE
F51 | ¦ ¦ ¦ | F51 |  | W33D |  | TRUE | FALSE | FALSE | FALSE
F52 | ¦ A04AS173-00002 ¦ ¦ | F52 |  | W33E |  | TRUE | FALSE | FALSE | FALSE
F53A | ¦ A04AS173-00003 ¦ ¦ | F53A |  | W33F |  | TRUE | FALSE | FALSE | FALSE
F53B | A04AM080-00006 ¦ A04AS173-00003 ¦ ¦ | F53B |  | W34A |  | TRUE | FALSE | FALSE | FALSE
F54A | ¦ A04AS173-00004 ¦ ¦ | F54A |  | W34B |  | TRUE | FALSE | FALSE | FALSE
F54B | A04AM080-00006 ¦ A04AS173-00004 ¦ ¦ | F54B |  | W34C |  | TRUE | FALSE | FALSE | FALSE
F71 | ¦ ¦ ¦ | F71 |  | W34D |  | TRUE | FALSE | FALSE | FALSE
F72 | ¦ ¦ ¦ | F72 |  | W34E |  | TRUE | FALSE | FALSE | FALSE
F73 | ¦ ¦ ¦ | F73 |  | W34F |  | TRUE | FALSE | FALSE | FALSE
F91 | A04AS174-00002 ¦ ¦ A04AM080-00005 ¦ | F91 |  | W35A |  | TRUE | FALSE | FALSE | FALSE
F92 | A04AS174-00005 ¦ ¦ A04AM080-00005 ¦ | F92 |  | W35B |  | TRUE | FALSE | FALSE | FALSE
F93 | A04AS174-00008 ¦ ¦ A04AM080-00005 ¦ | F93 |  | W36A |  | TRUE | FALSE | FALSE | FALSE
B01 | ¦ A04AM081-00001 ¦ ¦ |  |  | W36B |  | FALSE | TRUE | FALSE | FALSE
B02 | ¦ A04AM081-00004 ¦ ¦ |  |  | W41 |  | FALSE | TRUE | FALSE | FALSE
B03 | ¦ A04AM081-00007 ¦ ¦ |  |  | W42 |  | FALSE | TRUE | FALSE | FALSE
B04 | ¦ A04AM081-00010 ¦ ¦ |  |  | W43 |  | FALSE | TRUE | FALSE | FALSE
B31 | ¦ A04AN084-00001 ¦ ¦ |  |  | W44 |  | FALSE | TRUE | FALSE | FALSE
B32 | ¦ A04AN084-00004 ¦ ¦ |  |  | W45 |  | FALSE | TRUE | FALSE | FALSE
B33 | ¦ A04AN084-00007 ¦ ¦ |  |  | W46 |  | FALSE | TRUE | FALSE | FALSE
B34 | ¦ A04AN084-00010 ¦ ¦ |  |  |  |  | FALSE | TRUE | FALSE | FALSE
B35 | ¦ A04AN084-00013 ¦ ¦ |  |  |  |  | FALSE | TRUE | FALSE | FALSE
B36 | ¦ A04AN084-00016 ¦ ¦ |  |  |  |  | FALSE | TRUE | FALSE | FALSE
B37 | ¦ A04AN084-00019 ¦ ¦ |  |  |  |  | FALSE | TRUE | FALSE | FALSE
B38 | ¦ A04AN084-00022 ¦ ¦ |  |  |  |  | FALSE | TRUE | FALSE | FALSE
B39 | ¦ A04AN084-00025 ¦ ¦ |  |  |  |  | FALSE | TRUE | FALSE | FALSE
B40 | ¦ A04AN084-00028 ¦ ¦ |  |  |  |  | FALSE | TRUE | FALSE | FALSE
B41 | ¦ A04AN084-00031 ¦ ¦ |  |  |  |  | FALSE | TRUE | FALSE | FALSE
B42 | ¦ A04AS185-00001 ¦ ¦ |  |  |  |  | FALSE | TRUE | FALSE | FALSE
W01A | ¦ A04AM078-00001 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W01B | ¦ A04AM078-00001 ¦ ¦ A04AT198-00002 |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W01C | ¦ A04AM078-00001 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W02A | ¦ A04AM078-00002 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W02B | ¦ A04AM078-00002 ¦ ¦ A04AT198-00002 |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W02C | ¦ A04AM078-00002 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W03A | ¦ A04AM078-00003 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W03B | ¦ A04AM078-00003 ¦ ¦ A04AT198-00002 |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W03C | ¦ A04AM078-00003 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W04A | ¦ A04AM078-00004 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W04B | ¦ A04AM078-00004 ¦ ¦ A04AT198-00002 |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W04C | ¦ ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W05A | ¦ A04AM078-00005 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W05B | ¦ A04AM078-00005 ¦ ¦ A04AT198-00002 |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W05C | ¦ ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W06 | ¦ A04AM078-00006 ¦ ¦ A04AT198-00002 |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W07 | ¦ A04AM078-00007 ¦ ¦ A04AT198-00002 |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W08 | ¦ A04AM078-00008 ¦ ¦ A04AT198-00002 |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W09A | ¦ A04AM078-00009 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W09B | ¦ A04AM078-00009 ¦ ¦ A04AT198-00002 |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W09C | ¦ A04AM078-00009 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W31A | ¦ A04AN082-00001 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W31B | ¦ A04AN082-00001 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W32A | ¦ A04AN082-00002 ¦ A04AP085-00002 ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W32B | ¦ A04AN082-00002 ¦ A04AP085-00002 ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W32C | ¦ A04AN082-00002 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W32D | ¦ A04AN082-00002 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W32E | ¦ A04AN082-00002 ¦ A04AP310-00001 ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W32F | ¦ A04AN082-00002 ¦ A04AP310-00001 ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W33A | ¦ A04AN082-00002 ¦ A04AP085-00002 ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W33B | ¦ A04AN082-00002 ¦ A04AP085-00002 ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W33C | ¦ A04AN082-00002 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W33D | ¦ A04AN082-00002 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W33E | ¦ A04AN082-00002 ¦ A04AP310-00001 ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W33F | ¦ A04AN082-00002 ¦ A04AP310-00001 ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W34A | ¦ A04AN082-00002 ¦ A04AP085-00002 ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W34B | ¦ A04AN082-00002 ¦ A04AP085-00002 ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W34C | ¦ A04AN082-00002 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W34D | ¦ A04AN082-00002 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W34E | ¦ A04AN082-00002 ¦ A04AP310-00001 ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W34F | ¦ A04AN082-00002 ¦ A04AP310-00001 ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W35A | ¦ A04AN082-00003 ¦ A04AP085-00002 ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W35B | ¦ A04AN082-00003 ¦ A04AP085-00002 ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W36A | ¦ A04AN082-00003 ¦ A04AP085-00002 ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W36B | ¦ A04AN082-00003 ¦ A04AP085-00002 ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W41 | ¦ A04AN082-00004 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W42 | ¦ A04AN082-00005 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W43 | ¦ A04AN082-00006 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W44 | ¦ A04AN082-00007 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W45 | ¦ A04AN082-00008 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
W46 | ¦ A04AN082-00009 ¦ ¦ |  |  |  |  | FALSE | FALSE | TRUE | FALSE
C01 | ¦ A04AM079-00001 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C02 | ¦ A04AM079-00002 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C03 | ¦ A04AM079-00003 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C04 | ¦ A04AM079-00004 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C05 | ¦ A04AM079-00005 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C06 | ¦ A04AM079-00006 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C91A | ¦ A04AS186-00001 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C91B | ¦ A04AS186-00002 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C92 | ¦ A04AS187-00001 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C93 | ¦ A04AS188-00001 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C94A | ¦ A04AS189-00001 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C94B | ¦ A04AS189-00002 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C95A | ¦ A04AS190-00001 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C95B | ¦ A04AS190-00002 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C96A | ¦ A04AS191-00001 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C96B | ¦ A04AS191-00002 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C97 | ¦ A04AS192-00001 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
C98 | ¦ A04AS193-00001 ¦ ¦ |  |  |  |  | FALSE | FALSE | FALSE | TRUE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE
[6 empty] | FALSE | FALSE | FALSE | FALSE

## 링크용_Int Finish_Style-WM_DB
F01 | ¦ A04AM080-00001 ¦ ¦
F02 | ¦ A04AM080-00002 ¦ ¦
F03 | ¦ A04AM080-00003 ¦ ¦
F04 | ¦ A04AM080-00004 ¦ ¦
F05 | ¦ A04AM080-00005 ¦ ¦
F06A | ¦ A04AM080-00006 ¦ ¦
F06B | ¦ A04AM080-00006 ¦ ¦ A04AS168-00003
F07A | ¦ A04AM080-00007 ¦ ¦
F07B | ¦ A04AM080-00007 ¦ ¦
F07C | ¦ A04AM080-00007 ¦ ¦
F08 | ¦ A04AM080-00008 ¦ ¦
F09 | ¦ A04AM080-00009 ¦ ¦
F10 | ¦ A04AM080-00010 ¦ ¦
F11 | ¦ A04AM080-00011 ¦ ¦
F31A | ¦ A04AN083-00001 ¦ ¦
F31B | ¦ A04AN083-00001 ¦ A04AP085-00001 ¦ A04AS168-00003
F31C | ¦ A04AN083-00001 ¦ A04AP310-00001 ¦ A04AS168-00003
F32A | ¦ A04AN083-00002 ¦ ¦
F32B | ¦ A04AN083-00002 ¦ A04AP085-00001 ¦ A04AS168-00003
F33 | ¦ A04AN083-00003 ¦ ¦
F34A | ¦ A04AN083-00004 ¦ ¦
F34B | ¦ A04AN083-00004 ¦ ¦ A04AS168-00003
F35 | ¦ A04AN083-00005 ¦ ¦
F36 | ¦ A04AN083-00006 ¦ ¦
F37 | ¦ A04AN083-00007 ¦ ¦
F38 | ¦ A04AN083-00008 ¦ ¦
F39 | ¦ A04AN083-00009 ¦ ¦
F40 | ¦ A04AN083-00010 ¦ ¦
F41 | ¦ A04AN083-00011 ¦ ¦
F42 | ¦ A04AN083-00012 ¦ ¦
F43 | ¦ A04AS170-00001 ¦ ¦
F51 | ¦ ¦ ¦
F52 | ¦ A04AS173-00002 ¦ ¦
F53A | ¦ A04AS173-00003 ¦ ¦
F53B | A04AM080-00006 ¦ A04AS173-00003 ¦ ¦
F54A | ¦ A04AS173-00004 ¦ ¦
F54B | A04AM080-00006 ¦ A04AS173-00004 ¦ ¦
F71 | ¦ ¦ ¦
F72 | ¦ ¦ ¦
F73 | ¦ ¦ ¦
F91 | A04AS174-00002 ¦ ¦ A04AM080-00005 ¦
F92 | A04AS174-00005 ¦ ¦ A04AM080-00005 ¦
F93 | A04AS174-00008 ¦ ¦ A04AM080-00005 ¦
B01 | ¦ A04AM081-00001 ¦ ¦
B02 | ¦ A04AM081-00004 ¦ ¦
B03 | ¦ A04AM081-00007 ¦ ¦
B04 | ¦ A04AM081-00010 ¦ ¦
B31 | ¦ A04AN084-00001 ¦ ¦
B32 | ¦ A04AN084-00004 ¦ ¦
B33 | ¦ A04AN084-00007 ¦ ¦
B34 | ¦ A04AN084-00010 ¦ ¦
B35 | ¦ A04AN084-00013 ¦ ¦
B36 | ¦ A04AN084-00016 ¦ ¦
B37 | ¦ A04AN084-00019 ¦ ¦
B38 | ¦ A04AN084-00022 ¦ ¦
B39 | ¦ A04AN084-00025 ¦ ¦
B40 | ¦ A04AN084-00028 ¦ ¦
B41 | ¦ A04AN084-00031 ¦ ¦
B42 | ¦ A04AS185-00001 ¦ ¦
W01A | ¦ A04AM078-00001 ¦ ¦
W01B | ¦ A04AM078-00001 ¦ ¦ A04AT198-00002
W01C | ¦ A04AM078-00001 ¦ ¦
W02A | ¦ A04AM078-00002 ¦ ¦
W02B | ¦ A04AM078-00002 ¦ ¦ A04AT198-00002
W02C | ¦ A04AM078-00002 ¦ ¦
W03A | ¦ A04AM078-00003 ¦ ¦
W03B | ¦ A04AM078-00003 ¦ ¦ A04AT198-00002
W03C | ¦ A04AM078-00003 ¦ ¦
W04A | ¦ A04AM078-00004 ¦ ¦
W04B | ¦ A04AM078-00004 ¦ ¦ A04AT198-00002
W04C | ¦ ¦ ¦
W05A | ¦ A04AM078-00005 ¦ ¦
W05B | ¦ A04AM078-00005 ¦ ¦ A04AT198-00002
W05C | ¦ ¦ ¦
W06 | ¦ A04AM078-00006 ¦ ¦ A04AT198-00002
W07 | ¦ A04AM078-00007 ¦ ¦ A04AT198-00002
W08 | ¦ A04AM078-00008 ¦ ¦ A04AT198-00002
W09A | ¦ A04AM078-00009 ¦ ¦
W09B | ¦ A04AM078-00009 ¦ ¦ A04AT198-00002
W09C | ¦ A04AM078-00009 ¦ ¦
W31A | ¦ A04AN082-00001 ¦ ¦
W31B | ¦ A04AN082-00001 ¦ ¦
W32A | ¦ A04AN082-00002 ¦ A04AP085-00002 ¦
W32B | ¦ A04AN082-00002 ¦ A04AP085-00002 ¦
W32C | ¦ A04AN082-00002 ¦ ¦
W32D | ¦ A04AN082-00002 ¦ ¦
W32E | ¦ A04AN082-00002 ¦ A04AP310-00001 ¦
W32F | ¦ A04AN082-00002 ¦ A04AP310-00001 ¦
W33A | ¦ A04AN082-00002 ¦ A04AP085-00002 ¦
W33B | ¦ A04AN082-00002 ¦ A04AP085-00002 ¦
W33C | ¦ A04AN082-00002 ¦ ¦
W33D | ¦ A04AN082-00002 ¦ ¦
W33E | ¦ A04AN082-00002 ¦ A04AP310-00001 ¦
W33F | ¦ A04AN082-00002 ¦ A04AP310-00001 ¦
W34A | ¦ A04AN082-00002 ¦ A04AP085-00002 ¦
W34B | ¦ A04AN082-00002 ¦ A04AP085-00002 ¦
W34C | ¦ A04AN082-00002 ¦ ¦
W34D | ¦ A04AN082-00002 ¦ ¦
W34E | ¦ A04AN082-00002 ¦ A04AP310-00001 ¦
W34F | ¦ A04AN082-00002 ¦ A04AP310-00001 ¦
W35A | ¦ A04AN082-00003 ¦ A04AP085-00002 ¦
W35B | ¦ A04AN082-00003 ¦ A04AP085-00002 ¦
W36A | ¦ A04AN082-00003 ¦ A04AP085-00002 ¦
W36B | ¦ A04AN082-00003 ¦ A04AP085-00002 ¦
W41 | ¦ A04AN082-00004 ¦ ¦
W42 | ¦ A04AN082-00005 ¦ ¦
W43 | ¦ A04AN082-00006 ¦ ¦
W44 | ¦ A04AN082-00007 ¦ ¦
W45 | ¦ A04AN082-00008 ¦ ¦
W46 | ¦ A04AN082-00009 ¦ ¦
C01 | ¦ A04AM079-00001 ¦ ¦
C02 | ¦ A04AM079-00002 ¦ ¦
C03 | ¦ A04AM079-00003 ¦ ¦
C04 | ¦ A04AM079-00004 ¦ ¦
C05 | ¦ A04AM079-00005 ¦ ¦
C06 | ¦ A04AM079-00006 ¦ ¦
C91A | ¦ A04AS186-00001 ¦ ¦
C91B | ¦ A04AS186-00002 ¦ ¦
C92 | ¦ A04AS187-00001 ¦ ¦
C93 | ¦ A04AS188-00001 ¦ ¦
C94A | ¦ A04AS189-00001 ¦ ¦
C94B | ¦ A04AS189-00002 ¦ ¦
C95A | ¦ A04AS190-00001 ¦ ¦
C95B | ¦ A04AS190-00002 ¦ ¦
C96A | ¦ A04AS191-00001 ¦ ¦
C96B | ¦ A04AS191-00002 ¦ ¦
C97 | ¦ A04AS192-00001 ¦ ¦
C98 | ¦ A04AS193-00001 ¦ ¦

## 산출기준
[플랜트건축팀 - Q'ty Parameter] |  |  | qos | [8 empty] | * Rev.4 : 적색
Category | 구간판별 | Q'ty Cal Type Tag |  | 항목 | 산출수식 약자 | 수동 입력값 |  | 엑셀 적용여부 | Parameter Type | Parameter | 단위 | 비고 | Note
0.Room | # | RM-Q1 | [ 룸 일반 산출 ] | ▶ 모델 Parameter
|  | = A | 바닥마감, Ceiling마감 | 면적 | A |  |  |  | BP | Area | m2 | Revit자동산출
|  | = A * CR | 벽체 마감 | 둘레 | P |  |  |  | BP | Perimeter | mm | Revit자동산출
|  | = P/1000 | Skirt | Ceiling Height | CH |  |  |  | SP | H_Room H or CH | mm | *적용규칙A, 3.7 참조
|  |  | *벽마감 상세산출시 하기 적용 | ▶ 수동 입력 값 (엑셀 상에서 입력)
|  | = (P/1000)*(CH/1000) | 벽체마감(일반) | 주 마감재 높이 | MH | 2.1 | m | O |  |  |  | ex) 1.5m Tile + Above Paint => MH=1.5
|  | = (P/1000)*MH | 벽체마감(높이 구간 별 다를때 주 마감) | Raised Floor 높이 | RH | 1 | m | O
|  | = ( P/1000 )* (CH/1000-MH ) | 벽체마감(높이 구간 별 다를때 부 마감) | 천장Paint 보측면에 대한 할증률 | CR | 1.3 |  | O |  |  |  | * 페인트 아닌 경우 순수 면적 CR=1.0
|  | = (P/1000) * RH | Raised Floor 내측벽 마감
1.Floors | # | FL-Q1 | [ 플로어 일반 산출 ] | ▶ 모델 Parameter
|  | =A | 바닥 면적, Slab Form 면적 | 체적 | V |  |  |  | BP | Volume | m3 | *적용규칙A, 4.1 참조
|  | =V | Slab Concrete 물량 | 면적 | A |  |  |  | BP | Area | m2 | Revit자동산출
|  | =V*RE | 철근 물량 | 둘레 | P |  |  |  | BP | Perimeter | mm | Revit자동산출
▶ 수동 입력 값 (엑셀 상에서 입력)
|  |  |  | 철근비 | RE | 0.1 |  | O |  |  |  | *적용규칙B 철근비 참조
2.Roofs | # | RF-Q1 | [ 루프 일반 산출 ] | ▶ 모델 Parameter
|  | =A | Roof 면적 | 면적 | A |  |  |  | BP | Area | m2 | Revit자동산출
|  | =A*Ts | 부피 (Slope가 있을 경우) | 길이 | L |  |  |  | BP | Length | mm | Revit자동산출 (Gutter 객체 Only)
|  | =A*Tp | 부피 (Slope가 있을 경우)
|  | = L/1000 | Gutter 길이 | ▶ 수동 입력 값 (엑셀 상에서 입력)
|  |  |  | Slope Motar 평균두께 | Ts | 0.06 | m | O |  |  |  | *적용규칙A, 5.4 참조
|  |  |  | Protection Motar 평균 두께 | Tp | 0.06 | m | O |  |  |  | *적용규칙A, 5.4 참조
|  |  |  | Roof 방수마감 중 Parapet 측 추가물량 | Wf | [6 empty] | *Parapet Wall에서 산출
3.Walls | # | WA-Q1 | [ 벽체 일반 산출 ] | ▶ 모델 Parameter
|  | =A | Wall One Side 면적 | 체적 | V |  |  |  | BP | Volume | m3 | Revit자동산출
|  | =V | Conc. Wall 일 경우 Conc. 물량 | 면적 | A |  |  |  | BP | Area | m2 | Revit자동산출
|  | =V*RE | Conc. Wall 일 경우 철근 물량
|  | =A*2 | Wall Both Side 면적 | ▶ 수동 입력 값 (엑셀 상에서 입력)
|  |  |  | 철근비 | RE | 0.12 |  | O |  |  |  | *적용규칙B 철근비 참조
|  |  |  | 외측Paint 프레임부분에 대한 할증 | PR | 1.2 | [5 empty] | *적용규칙A, 6.6 참조
4.St Fdn | # | SF-Q0 | [ 온통 터파기 산출 전용 ] | ▶ 모델 Parameter | [8 empty] | Geometry derived by algorithm in Dynamo
[ 온통 터파기 ] |  | 토공 공통 입력 항목 |  | GL에서 기초 구조체바닥깊이 | H2 |  |  |  |  | Elevation at Bottom | mm | *GL=0 를 Survey Level Z=0 로 Setting한 경우 | [ 온통 터파기 산출 전용 ]
|  | Lean 두께 (m) | 0.1
|  | Base 두께 (m) | 0.15
|  | SubBase두께 (m) | 0.15
|  | ExtraExcavation 두께(입찰) | 0
|  | VCF 토량환산계수 | 1.15
|  | Lean 돌출길이 (m) | 0.1
|  | 터파기 여유폭 (m) | 0.2
|  | 지하수위 (m) | -1
|  | FL - GL gap(Level Difference) (m) | 0.2
▶ 수동 입력 값 (엑셀 상에서 입력)
|  |  |  | Lean 두께 | C1 | 0.1 | m | O
|  |  |  | Base 두께 | C2 | 0.15 | m | O
|  |  | ※ EarthWork | SubBase두께 | C3 | 0.15 | m | O
|  |  | * Excavation : 가상모델링으로 산출 | ExtraExcavation 두께(입찰) | C4 | 0 | m | O
|  |  | * Backfill : Exca - (Conc+Lean+Base+Subbase) | VCF 토량환산계수 | VCF | 1.15 |  | O
|  |  | * Disposal : (Exca - Back)*VCF | Lean 돌출길이 | D1 | 0.1 | m | O
|  |  |  | 터파기 여유폭 | D2 | 0.2 | m | O
|  |  |  | 지하수위 | GWL | -1 | m | O
|  |  |  | FL - GL gap(Level Difference) | LD | 0.2 | m | O
|  |  |  | G = L / H | G | 1 |  | O |  |  |  | *G = L / H ex) 45도 터파기 : G=1, 90도 터파기 : G=0
|  |  |  | 터파기 깊이 | H | [6 empty] | Dynamo 자동산출 (H2+C1+C2+C3)
4.St Fdn | # | SF-Q1 | [ Mat, Mass ] | ▶ 모델 Parameter | [8 empty] | [ Mat, Mass ]
Foundation Slab |  | =V | 기초 Concrete 물량 | 기초판 체적 | V |  |  |  | BP | Volume | m3 | Revit자동산출
[ Mat, Mass ] |  | =V*RE | 철근 물량 | 면적 | A |  |  |  | BP | Area | m2 | Revit자동산출
|  | = (P/1000) * (T/1000) | 거푸집 물량 | 둘레 | P |  |  |  | BP | Perimeter | mm | Revit자동산출
|  | = (P/1000) * (H2/1000) | UG Protection (바닥 ⇒ Lean에서 산출) | 두께 | T |  |  |  | BP | Thickness | mm | Revit자동산출
|  | =Exca | * Excavation : 가상모델링으로 산출 | GL에서 기초바닥깊이 | H2 |  |  |  | BP | Elevation at Bottom | mm | *GL=0 를 Survey Level Z=0 로 Setting한 경우
|  | =Back | * Backfill : Exca - (Conc+Lean+Base+Subbase) | ▶ 수동 입력 값 (엑셀 상에서 입력)
|  | =Disp | * Disposal : (Exca - Back)*VCF | Lean 두께 | C1 | 0.1 | m | O |  |  |  | *적용규칙B 철근비 참조
|  | =(A+(P/1000)*D1+(4*D1*D1)) | (입찰 Only) 바닥보호층, 기층, 보조기층 | Base 두께 | C2 | 0.15 | m | O
|  | =(A+(P/1000)*D1+(4*D1*D1))*C1 | (입찰 Only) Lean Conc | SubBase두께 | C3 | 0.15 | m | O
|  |  |  | ExtraExcavation 두께(입찰) | C4 | 0 | m | O
|  |  |  | VCF 토량환산계수 | VCF | 1.15 |  | O
|  |  |  | Lean 돌출길이 | D1 | 0.1 | m | O
|  |  |  | 터파기 여유폭 | D2 | 0.2 | m | O
|  |  |  | 지하수위 | GWL | -1 | m | O
|  |  |  | FL - GL gap(Level Difference) | LD | 0.2 | m | O
|  |  |  | Mat, Mass철근비 | RE | 0.12 |  | O
|  |  |  | G = L / H | G | 1 |  | O |  |  |  | *G = L / H ex) 45도 터파기 : G=1, 90도 터파기 : G=0
|  |  |  | 터파기 깊이 | H | [6 empty] | Dynamo 자동산출 (H2+C1+C2+C3)
4.St Fdn | # | SF-Q2 | [ SOG ] | ▶ 모델 Parameter
Foundation Slab |  | =V | 기초 Concrete 물량 | 기초판 체적 | V |  |  |  | BP | Volume | m3 | Revit자동산출
[ SOG ] |  | =V*RE | 철근 물량 | 면적 | A |  |  |  | BP | Area | m2 | Revit자동산출
|  | = P/1000 | 테두리 Isolation 물량 | 둘레 | P |  |  |  | BP | Perimeter | mm | Revit자동산출
|  | = (P/1000) * (T/1000) | 거푸집 물량 | 두께 | T |  |  |  | BP | Thickness | mm | Revit자동산출
|  | = A | -UG Protection (바닥 ) -SOG 옆면 Protection 산출 X | GL에서 기초바닥깊이 | H2 |  |  |  | BP | Elevation at Bottom | mm | *GL=0 를 Survey Level Z=0 로 Setting한 경우
|  | =Exca | * Excavation : 가상모델링으로 산출 | ▶ 수동 입력 값 (엑셀 상에서 입력)
|  | =Back | * Backfill : Exca - (Conc+Lean+Base+Subbase) | Lean 두께 | C1 | 0.1 | m | O |  |  |  | *적용규칙B 철근비 참조
|  | =Disp | * Disposal : (Exca - Back)*VCF | Base 두께 | C2 | 0.15 | m | O
|  | = V + (TCS * P/1000) | (입찰 Only) Thickened 포함 슬라브 Conc | SubBase두께 | C3 | 0.15 | m | O
|  | = (V + (TCS * P/1000) )*RE | (입찰 Only) Thickened 포함 슬라브 철근 | ExtraExcavation 두께(입찰) | C4 | 0 | m | O
|  | = ( A + (P/1000)*D1+(4*D1*D1) ) | (입찰 Only) 바닥보호층, 기층, 보조기층 | VCF 토량환산계수 | VCF | 1.15 |  | O
|  | = ( A + (P/1000)*D1+(4*D1*D1) ) * C1 | (입찰 Only) Lean Conc | Lean 돌출길이 | D1 | 0.1 | m | O
|  | 수동 입력 | Control Joint | 터파기 여유폭 | D2 | 0.2 | m | O
|  |  |  | 지하수위 | GWL | -1 | m | O
|  |  |  | FL - GL gap(Level Difference) | LD | 0.2 | m | O
|  |  |  | G = L / H | G | 1 |  | O |  |  |  | *G = L / H ex) 45도 터파기 : G=1, 90도 터파기 : G=0
|  |  |  | SOG철근비 | RE | 0.09 |  | O
|  |  |  | 테두리 내림부 깊이 | TCH | 0.2 | m
|  |  |  | 테두리 내림부 폭 | TCW | 0.5 | m
|  |  |  | 테두리 내림부 단면적 (Thickened Cross Section) | TCS | 0.1 | m2 | O |  |  |  | *설계자 결정
|  |  |  | 터파기 깊이 | H | 1.6 | m | O |  |  |  | Dynamo 자동산출 (H2+C1+C2+C3)
4.St Fdn | # | SF-Q2A | [ Suspended Slab ] | ▶ 모델 Parameter
Foundation Slab |  | =V | 기초 Concrete 물량 | 기초판 체적 | V |  |  |  | BP | Volume | m3 | Revit자동산출
[ Suspended Slab ] |  | =V*RE | 철근 물량 | 면적 | A |  |  |  | BP | Area | m2 | Revit자동산출
|  | = P/1000 | 테두리 Isolation 물량 | 둘레 | P |  |  |  | BP | Perimeter | mm | Revit자동산출
|  | = (P/1000) * (T/1000) | 거푸집 물량 | 두께 | T |  |  |  | BP | Thickness | mm | Revit자동산출
|  | = A | -UG Protection (바닥 ) -SOG 옆면 Protection 산출 X | GL에서 기초바닥깊이 | H2 |  |  |  | BP | Elevation at Bottom | mm | *GL=0 를 Survey Level Z=0 로 Setting한 경우
|  | =Exca | * Excavation : 가상모델링으로 산출 | ▶ 수동 입력 값 (엑셀 상에서 입력)
|  | =Back | * Backfill : Exca - (Conc+Lean+Base+Subbase) | Lean 두께 | C1 | 0.1 | m | O |  |  |  | *적용규칙B 철근비 참조
|  | =Disp | * Disposal : (Exca - Back)*VCF | Base 두께 | C2 | 0.15 | m | O
|  | = V + (TCS * P/1000) | (입찰 Only) Thickened 포함 슬라브 Conc | SubBase두께 | C3 | 0.15 | m | O
|  | = (V + (TCS * P/1000) )*RE | (입찰 Only) Thickened 포함 슬라브 철근 | ExtraExcavation 두께(입찰) | C4 | 0 | m | O
|  | = ( A + (P/1000)*D1+(4*D1*D1) ) | (입찰 Only) 바닥보호층, 기층, 보조기층 | VCF 토량환산계수 | VCF | 1.15 |  | O
|  | = ( A + (P/1000)*D1+(4*D1*D1) ) * C1 | (입찰 Only) Lean Conc | Lean 돌출길이 | D1 | 0.1 | m | O
|  | 수동 입력 | Control Joint | 터파기 여유폭 | D2 | 0.2 | m | O
|  |  |  | 지하수위 | GWL | -1 | m | O
|  |  |  | FL - GL gap(Level Difference) | LD | 0.2 | m | O
|  |  |  | G = L / H | G | 1 |  | O |  |  |  | *G = L / H ex) 45도 터파기 : G=1, 90도 터파기 : G=0
|  |  |  | SOG철근비 | RE | 0.09 |  | O
|  |  |  | 터파기 깊이 | H | 1.6 | m | O |  |  |  | Dynamo 자동산출 (H2+C1+C2+C3)
4.St Fdn | # | SF-Q2B | [ 장비패드 ] | ▶ 모델 Parameter
Foundation Slab |  | =V | 기초 Concrete 물량 | 기초판 체적 | V |  |  |  | BP | Volume | m3 | Revit자동산출
[ SOG ] |  | =V*RE | 철근 물량 | 면적 | A |  |  |  | BP | Area | m2 | Revit자동산출
|  | = P/1000 | 테두리 Isolation 물량 | 둘레 | P |  |  |  | BP | Perimeter | mm | Revit자동산출
|  | = (P/1000) * (T/1000) | 거푸집 물량 | 두께 | T |  |  |  | BP | Thickness | mm | Revit자동산출
|  | = A | -UG Protection (바닥 ) -SOG 옆면 Protection 산출 X | GL에서 기초바닥깊이 | H2 |  |  |  | BP | Elevation at Bottom | mm | *GL=0 를 Survey Level Z=0 로 Setting한 경우
|  | =Exca | * Excavation : 가상모델링으로 산출 | ▶ 수동 입력 값 (엑셀 상에서 입력)
|  | =Back | * Backfill : Exca - (Conc+Lean+Base+Subbase) | Lean 두께 | C1 | 0.1 | m | O |  |  |  | *적용규칙B 철근비 참조
|  | =Disp | * Disposal : (Exca - Back)*VCF | Base 두께 | C2 | 0.15 | m | O
|  | = V + (TCS * P/1000) | (입찰 Only) Thickened 포함 슬라브 Conc | SubBase두께 | C3 | 0.15 | m | O
|  | = (V + (TCS * P/1000) )*RE | (입찰 Only) Thickened 포함 슬라브 철근 | ExtraExcavation 두께(입찰) | C4 | 0 | m | O
|  | = ( A + (P/1000)*D1+(4*D1*D1) ) | (입찰 Only) 바닥보호층, 기층, 보조기층 | VCF 토량환산계수 | VCF | 1.15 |  | O
|  | = ( A + (P/1000)*D1+(4*D1*D1) ) * C1 | (입찰 Only) Lean Conc | Lean 돌출길이 | D1 | 0.1 | m | O
|  | 수동 입력 | Control Joint | 터파기 여유폭 | D2 | 0.2 | m | O
|  |  |  | 지하수위 | GWL | -1 | m | O
|  |  |  | FL - GL gap(Level Difference) | LD | 0.2 | m | O
|  |  |  | G = L / H | G | 1 |  | O |  |  |  | *G = L / H ex) 45도 터파기 : G=1, 90도 터파기 : G=0
|  |  |  | SOG철근비 | RE | 0.09 |  | O
|  |  |  | 터파기 깊이 | H | 1.6 | m | O |  |  |  | Dynamo 자동산출 (H2+C1+C2+C3)
4.St Fdn | # | SF-Q2A | [ 피트/트렌치 플로어 산출 ] | ▶ 모델 Parameter | [8 empty] | [ Trench ]
|  | =V | 기초 Concrete 물량 | Lean 체적 | V |  |  |  | BP | Volume | m3 | Revit자동산출 | *Trench Wall : Wall 패밀리에서 산출, Trench 바닥 : Floor 패밀리에서 산출
[Trench/Pit 바닥] |  | =V*RE | 철근 물량 | 면적 | A |  |  |  | BP | Area | m2 | Revit자동산출
|  | = P/1000 | 테두리 Isolation 물량 | 둘레 | P |  |  |  | BP | Perimeter | mm | Revit자동산출
|  | Pit/Trench 바닥 옆면 Form 산출 X | *Form물량: Pit,Trench Wall에서 산출
|  | =A | UG Protection (바닥) 'Pit/Trench 바닥 옆면 Protection 산출 X
|  | =A | 피트/트렌치 내측 바닥면 마감 면적 | ▶ 수동 입력 값 (엑셀 상에서 입력)
|  | =Exca | * Excavation : 가상모델링으로 산출 | Lean 두께 | C1 | 0.1 | m | O |  |  |  | * W : Trench/Pit 벽체 두께 포함한 폭
|  | =Back | * Backfill : Exca - (Conc+Lean+Base+Subbase) | Base 두께 | C2 | 0.15 | m | O |  |  |  | * L : Trench/Pit 벽체 두께 포함한 길이
|  | =Disp | * Disposal : (Exca - Back)*VCF | SubBase두께 | C3 | 0.15 | m | O
|  | = ( A + (P/1000)*D1+(4*D1*D1) ) | (입찰 Only) 바닥보호층, 기층, 보조기층 | ExtraExcavation 두께(입찰) | C4 | 0 | m | O
|  | = ( A + (P/1000)*D1+(4*D1*D1) ) * C1 | (입찰 Only) Lean Conc | VCF 토량환산계수 | VCF | 1.15 |  | O
|  |  |  | Lean 돌출길이 | D1 | 0.1 | m | O
|  |  |  | 터파기 여유폭 | D2 | 0.2 | m | O
|  |  |  | 지하수위 | GWL | -1 | m | O
|  |  |  | FL - GL gap(Level Difference) | LD | 0.2 | m | O
|  |  |  | G = L / H | G | 1 |  | O |  |  |  | *G = L / H ex) 45도 터파기 : G=1, 90도 터파기 : G=0
|  |  |  | 터파기 깊이 | H | [6 empty] | Dynamo 자동산출 (H2+C1+C2+C3)
|  |  |  | Trench/Pit 깊이 (GL이하) | H2 | 1 | m | O
|  |  |  | Trench/Pit 바닥슬라브 철근비 | RE | 0.12 |  | O |  |  |  | *적용규칙B 철근비 참조
4.St Fdn | # | SF-Q3 | [ Lean ] | ▶ 모델 Parameter | [8 empty] | [ Lean, Base, SubBase ]
Foundation Slab |  | =V | Lean Concrete 물량 | Lean 체적 | V |  |  |  | BP | Volume | m3 | Revit자동산출 | *적용규칙A, 7.1 참조
[ Lean ] |  | =A | Base 물량, Sub Base 물량 | 면적 | A |  |  |  | BP | Area | m2 | Revit자동산출
|  | =A | PE Sheet, Bitumen Paint
* Earth Work 물량은 해당 기초에서 산출
▶ 수동 입력 값 (엑셀 상에서 입력)
4.St Fdn | # | SF-Q4 | [Wall Foundation] | ▶ 모델 Parameter | [8 empty] | [ Wall Foundation ]
[Wall Foundation] |  | =V | 기초 Concrete 물량 | 체적 | V |  |  |  | BP | Volume | m3 | Revit자동산출
|  | =V*RE | 철근 물량 | 면적 | A |  |  |  | BP | Area | m2 | Revit자동산출
|  | =A*2 | 거푸집 물량, 측면보호층 (Wall Part) | 폭 | W |  |  |  | BP | Width | mm | Revit자동산출
|  | =2*(W/1000+L/1000) * (T/1000) + 2*(W/1000*L/1000) | UG Protection (바닥 + 상부 + 측면) | 두께 | T |  |  |  | BP | Foundation Thickness | mm | Revit자동산출
|  | =Exca | * Excavation : 가상모델링으로 산출 | 길이 | L |  |  |  | BP | Length | mm | Revit자동산출
|  | =Back | * Backfill : Exca - (Conc+Lean+Base+Subbase) | ▶ 수동 입력 값 (엑셀 상에서 입력)
|  | =Disp | * Disposal : (Exca - Back)*VCF | Lean 두께 | C1 | 0.1 | m | O |  |  |  | *적용규칙B 철근비 참조
|  | = (L/1000) * (T/1000) * 2 | 거푸집 물량, 측면보호층 (FDN Part) | Base 두께 | C2 | 0.15 | m | O
|  | =(W/1000+2*D1)*(L/1000+2*D1) | (입찰 Only) 바닥보호층, 기층, 보조기층 | SubBase두께 | C3 | 0.15 | m | O
|  | =(W/1000+2*D1)*(L/1000+2*D1) * C1 | (입찰 Only) Lean Conc | ExtraExcavation 두께(입찰) | C4 | 0 | m | O
|  | =(W/1000+2*D1)*(L/1000+2*D1) * C1 | (입찰 Only) Lean Conc | VCF 토량환산계수 | VCF | 1.15 |  | O
|  |  |  | Lean 돌출길이 | D1 | 0.1 | m | O
|  |  |  | 터파기 여유폭 | D2 | 0.2 | m | O
|  |  |  | 지하수위 | GWL | -1 | m | O
|  |  |  | FL - GL gap(Level Difference) | LD | 0.2 | m | O
|  |  |  | 기초철근비 | RE | 0.12 |  | O |  |  |  | *적용규칙B 철근비 참조
|  |  |  | G = L / H | G | 1 |  | O |  |  |  | *G = L / H ex) 45도 터파기 : G=1, 90도 터파기 : G=0
4.St Fdn | # | SF-Q5 | [독립기초] | ▶ 모델 Parameter | [8 empty] | Load Family
Load Family |  | =V | 기초 Concrete 물량 | 기초판 체적 | V |  |  |  | BP | Volume | m3 | Revit자동산출 | [ 독립기초 ]
[독립기초] |  | =V*RE | 철근 물량 | 기초 폭 | W |  |  |  | BP | Width | mm | Revit자동산출
|  | =2*(W/1000 + D/1000) * (T/1000) | 거푸집 물량 | 기초 길이 | D |  |  |  | BP | Length | mm | Revit자동산출
|  | =2*(W/1000 + D/1000) * (T/1000) + 2*(W/1000*D/1000) | Protection : 옆면 + 윗면 + 밑면 | 기초 두께 | T |  |  |  | BP | Foundation Thickness | mm | Revit자동산출
|  |  |  | GL에서 기초바닥깊이 | H2 |  |  |  | BP | Elevation at Bottom Survey | mm | *GL=0 를 Survey Level Z=0 로 Setting한 경우
|  | =Exca | * Excavation : 가상모델링으로 산출 | ▶ 수동 입력 값 (엑셀 상에서 입력)
|  | =Back | * Backfill : Exca - (Conc+Lean+Base+Subbase) | Lean 두께 | C1 | 0.1 | m | O
|  | =Disp | * Disposal : (Exca - Back)*VCF | Base 두께 | C2 | 0.15 | m | O
|  | =(W/1000+2*D1)*(D/1000+2*D1) | (입찰 Only) 바닥보호층, 기층, 보조기층 | SubBase두께 | C3 | 0.15 | m | O
|  | =(W/1000+2*D1)*(D/1000+2*D1) * C1 | (입찰 Only) Lean Conc | ExtraExcavation 두께(입찰) | C4 | 0 | m | O
|  |  |  | VCF 토량환산계수 | VCF | 1.15 |  | O
|  |  |  | Lean 돌출길이 | D1 | 0.1 | m | O
|  |  |  | 터파기 여유폭 | D2 | 0.2 | m | O
|  |  |  | 지하수위 | GWL | -1 | m | O
|  |  |  | FL - GL gap(Level Difference) | LD | 0.2 | m | O
|  |  |  | 기초철근비 | RE | 0.12 |  | O |  |  |  | *적용규칙B 철근비 참조
|  |  |  | Pedestal폭1 | PC | 0.45 | m | O
|  |  |  | Pedestal폭2 | PD | 0.45 | m | O
|  |  |  | 터파기 깊이 | H | [6 empty] | Dynamo 자동산출 (H2+C1+C2+C3)
|  |  |  | G = L / H | G | 1 |  | O |  |  |  | *G = L / H ex) 45도 터파기 : G=1, 90도 터파기 : G=0
4.St Fdn | # | SF-Q6 | [Pile] | ▶ 모델 Parameter | [8 empty] | Load Family
[Pile] |  | =L | Pile 길이 | 파일 길이 | L |  |  |  | SP-F | Depth | mm | Revit자동산출 | [ Pile ]
▶ 수동 입력 값 (엑셀 상에서 입력)
|  | =Q | Pile 개수 | Q'ty | Q | 1
5.St Col | # | SC-Q1 | [Concrete Column]-AG | ▶ 모델 Parameter | [8 empty] | [ Concrete Column ]
[Concret Column] |  | =V | 기둥 Concrete 물량 | 체적 | V |  |  |  | BP | Volume | m3 | *적용규칙B - 형상결합 우선순위 참조 | ※ Revit 자동산출 V : 슬라브두께 포함 체적 (적용규칙B - 형상결합 우선순위)
|  | =V*RE | 철근 물량 | 기둥단면 가로 (X) | W |  |  |  | SP-F | Width | mm | *적용규칙A, 8.5 참조 | ※ Revit 자동산출 H : 슬라브두께 포함 높이
|  | = 2*( (W/1000)+(D/1000) ) * (H/1000) | 거푸집 물량, Paint | 기둥단면 세로 (Y) | D |  |  |  | SP-F | Depth | mm | *적용규칙A, 8.5 참조
|  |  |  | 높이 | H |  |  |  | BP | Length | mm | *슬라브 두께를 포함한 기둥높이
▶ 수동 입력 값 (엑셀 상에서 입력)
|  |  |  | 철근비 | RE | 0.3 |  | O |  |  |  | *적용규칙B 철근비 참조
|  |  |  | GroutThk | GT | 0.05 | m | O
5.St Col | # | SC-Q1A | [Concrete Column]-UG | ▶ 모델 Parameter | [8 empty] | [ Concrete Column ]
[Concret Column] |  | =V | 기둥 Concrete 물량 | 체적 | V |  |  |  | BP | Volume | m3 | *적용규칙B - 형상결합 우선순위 참조 | ※ Revit 자동산출 V : 슬라브두께 포함 체적 (적용규칙B - 형상결합 우선순위)
|  | =V*RE | 철근 물량 | 기둥단면 가로 (X) | W |  |  |  | SP-F | Width | mm | *적용규칙A, 8.5 참조 | ※ Revit 자동산출 H : 슬라브두께 포함 높이
|  | = 2*( (W/1000)+(D/1000) ) * (H/1000) | 거푸집 물량, UG Protection | 기둥단면 세로 (Y) | D |  |  |  | SP-F | Depth | mm | *적용규칙A, 8.5 참조
|  | = (W/1000) * (D/1000) * GT | Pedestal Grout 물량 (별도 모델링시는 제외) | 높이 | H |  |  |  | BP | Length | mm | *슬라브 두께를 포함한 기둥높이
|  | = 2*( (W/1000)+(D/1000) ) | Separation Joint | ▶ 수동 입력 값 (엑셀 상에서 입력)
|  |  |  | 지하수위 | GWL | -1 | m | O
|  |  |  | FL - GL gap(Level Difference) | LD | 0.2 | m | O
|  |  |  | 철근비 | RE | 0.3 |  | O |  |  |  | *적용규칙B 철근비 참조
|  |  |  | GroutThk | GT | 0.05 | m | O
5.St Col | # | SC-Q2 | [Steel Column] | ▶ 모델 Parameter | [8 empty] | [ Steel Column ]
[Steel Column] |  | = (H/1000) * W | 철골 물량 | 철골단위중량 | W |  |  |  | BP | Nominal Weight | kgf/m | 철골Family에 Shape에 따라 수동입력된 값
|  | = P * (H/1000) | 철골 도장 물량 | 철골둘레 | P |  |  |  | BP | Perimeter | m2/m | 철골Family에 Shape에 따라 수동입력된 값
|  |  |  | 높이 | H |  |  |  | BP | Length | mm | Revit자동산출 Cut Length (X), Length 적용
▶ 수동 입력 값 (엑셀 상에서 입력)
|  |  |  | 철골제작할증 | SE | 0.2 |  | O
|  |  |  | 철골페인트할증 | PE | 0.2
6.St Framing | # | SB-Q1 | [Concrete Beam] - AG | ▶ 모델 Parameter | [8 empty] | [ Concrete Beam ] - AG
[Concret Beam] - AG |  | = V | 보 Concrete 물량 | 체적 | V |  |  |  | BP | Volume | m3 | *적용규칙B - 형상결합 우선순위 참조 | ※ Revit 자동산출 V : 슬라브두께 포함 체적 (적용규칙B - 형상결합 우선순위)
|  | = V*RE | 철근 물량 | 보 폭 | W |  |  |  | SP-P | Width | mm | Revit자동산출 | ※ 거푸집 = 슬라브두께 포함한 D로 적용 (여유반영)
|  | = 2*(L/1000)*(D/1000) + (W/1000)*(L/1000) | 거푸집 물량, Paint | 보 높이 | D |  |  |  | SP-F | Height | mm | Revit자동산출 (슬라브두께 포함 보높이)
|  |  |  | 길이 | L |  |  |  | BP | Length | mm | Revit자동산출 Cut Length (X), Length 적용
▶ 수동 입력 값 (엑셀 상에서 입력)
|  |  |  | 철근비 | RE | 0.14 |  | O |  |  |  | *적용규칙B 철근비 참조
6.St Framing | # | SB-Q1A | [Concrete Beam] - UG | ▶ 모델 Parameter | [8 empty] | [ Concrete Beam ] - UG
[Concret Beam] -UG |  | = V | 보 Concrete 물량 | 체적 | V |  |  |  | BP | Volume | m3 | *적용규칙B - 형상결합 우선순위 참조 | ※ Revit 자동산출 V : 슬라브두께 포함 체적 (적용규칙B - 형상결합 우선순위)
|  | = V*RE | 철근 물량 | 보 폭 | W |  |  |  | SP-P | Width | mm | Revit자동산출
|  | = 2 * (L/1000) * (D/1000) | 거푸집 물량, Paint | 보 높이 | D |  |  |  | SP-F | Height | mm | Revit자동산출 (슬라브두께 포함 보높이)
|  | = 2 * (L/1000) * (H2/1000) + (W/1000) * (L/1000) | GL하부 보 양측 측면 면적 + 바닥 | 길이 | L |  |  |  | BP | Length | mm | Revit자동산출 Cut Length (X), Length 적용
|  | =Exca | * Excavation : 가상모델링으로 산출 | ▶ 수동 입력 값 (엑셀 상에서 입력)
|  | =Back | * Backfill : Exca - (Conc+Lean+Base+Subbase) | Lean 두께 | C1 | 0.1 | m | O
|  | =Disp | * Disposal : (Exca - Back)*VCF | Base 두께 | C2 | 0.15 | m | O
|  | = ( (W/1000) + 2*D1 ) * (L/1000) | (입찰 Only) 바닥보호층, 기층, 보조기층 | SubBase두께 | C3 | 0.15 | m | O
|  | = ( (W/1000) + 2*D1 ) * (L/1000) * C1 | (입찰 Only) Lean Conc | ExtraExcavation 두께(입찰) | C4 | 0 | m | O
|  |  |  | VCF 토량환산계수 | VCF | 1.15 |  | O
|  |  |  | Lean 돌출길이 | D1 | 0.1 | m | O
|  |  |  | 터파기 여유폭 | D2 | 0.2 | m | O
|  |  |  | 지하수위 | GWL | -1 | m | O
|  |  |  | FL - GL gap(Level Difference) | LD | 0.2 | m | O
|  |  |  | 철근비 | RE | 0.14 |  | O |  |  |  | *적용규칙B 철근비 참조
|  |  |  | G = L / H | G | 1 |  | O |  |  |  | *G = L / H ex) 45도 터파기 : G=1, 90도 터파기 : G=0
|  |  |  | GL에서 TG바닥깊이 | H2 | 0.3 | m | O
|  |  |  | 터파기 깊이 | H | [6 empty] | Dynamo 자동산출 (H2+C1+C2+C3)
6.St Framing | # | SB-Q2 | [Steel Beam] | ▶ 모델 Parameter | [8 empty] | Load Family - Steel
[Steel Beam] |  | = (L/1000) * W | 철골 물량 | 철골단위중량 | W |  |  |  | BP | Nominal Weight | kgf/m | 철골Family에 Shape에 따라 수동입력된 값 | [ Steel Beam ]
|  | = P * (L/1000) | 철골 도장 물량 | 철골둘레 | P |  |  |  | BP | Perimeter | m2/m | 철골Family에 Shape에 따라 수동입력된 값
|  |  |  | 보 길이 | L |  |  |  | BP | Length | mm | Revit자동산출 Cut Length (X), Length 적용
▶ 수동 입력 값 (엑셀 상에서 입력)
|  |  |  | 철골제작할증 | SE | 0.2 |  | O
|  |  |  | 페인트할증 | PE | 0.2
7.Ceilings | # | CE-Q1 | [ 천장 일반 산출 ] | ▶ 모델 Parameter | [8 empty] | System Family
|  |  | * Ceiling 마감 면적은 Room 패밀리에서 산출 | 면적 | A |  |  |  | BP | Area | m2 | Revit자동산출
8.Doors | # | DR-Q1 | [ 도어 일반 산출 ] | ▶ 수동 입력 값 (엑셀 상에서 입력) | [8 empty] | Load Family
|  | =Q | Door 개수 | Q'ty | Q | 1
9.Windows | # | WD-Q1 | [ 윈도우 일반 산출 ] | ▶ 수동 입력 값 (엑셀 상에서 입력) | [8 empty] | Load Family
|  | =Q | Window 개수 | Q'ty | Q | 1
| # | WD-Q2 | [ 스카이라이트 일반 산출 ] | ▶ 모델 Parameter | [8 empty] | Load Family
|  | = (H/1000) * (W/1000) | Skylight 면적 | Window 높이 | H |  |  |  | BP | Height |  | Revit자동산출 | Skylight
|  |  |  | Window 폭 | W |  |  |  | BP | Width |  | Revit자동산출
10.Stairs | # | SR-Q1 | [Concrete Stair] | ▶ 모델 Parameter | [8 empty] | Cast-In-Place Stair / Concrete Stair
[Concrete Stair] |  | =[(R*T*QR)*W+(A+S+C)*T1*W]*Q | Concrete 물량 | Riser 개수 | QR |  |  |  | BP | Actual Number of Risers | EA
|  | =[(R*T*QR)*W+(A+S+C)*T1*W]*RE*Q | 철근 물량 | Riser 높이 | R |  |  |  | BP | Actual Riser Height | mm
|  | =[(A+S+C)*W+R*W*QR]*Q | 거푸집 물량 | Tread 깊이 | T |  |  |  | BP | Actual Tread Depth | mm
|  | =[(A+C)*W+(T+R)*QR*W]*Q | 마감 물량
수식 출처 확인 ↑
▶ 수동 입력 값 (엑셀 상에서 입력)
|  |  |  | 철근비 | RE | 0.12 |  | O |  |  |  | *적용규칙B 철근비 참조 | * 참고 : ABOQ
|  |  |  | Landing Slab 길이 | A | 1.5 | m | [5 empty] | ※ Concrete = [(A+C)*THK + S*(THK+0.17)] * W
[5 empty] | B | 3 | m | [5 empty] | * S=√(B^2+H^2)
|  |  |  | Landing Slab 길이 | C | 2 | m | [5 empty] | ※ Form = (A + C + S + H) * W
|  |  |  | 계단높이 | H | 1.5 | m
|  |  |  | 계단폭 | W | 2 | m
|  |  |  | Landing Slab두께 | T1 | 0.15 | m
|  |  |  | 경사길이 | S | 3.3541 | m |  |  |  |  | 엑셀상에서 자동계산
|  |  |  | Form | [7 empty] | (A+S+C+H)*W
|  |  |  | Q'ty | Q | 1
10.Stairs | # | SR-Q2 | [Steel Stair] | ▶ 모델 Parameter
[Steel Stair] |  | 수동 산출 |  | Riser 개수 | QR |  |  |  | BP | Actual Number of Risers | EA
|  | = S |  | Riser 높이 | R |  |  |  | BP | Actual Riser Height | mm
|  |  |  | Tread 깊이 | T |  |  |  | BP | Actual Tread Depth | mm
▶ 수동 입력 값 (엑셀 상에서 입력)
|  |  |  | Landing Slab 길이 | A | 1.5 | m
[5 empty] | B | 3 | m
|  |  |  | Landing Slab 길이 | C | 2 | m
|  |  |  | 계단높이 | H | 1.5 | m
|  |  |  | 계단폭 | W | 2 | m
|  |  |  | Landing Slab두께 | T1 | 0.15 | m
|  |  |  | 경사길이 | S | 3.3541 | m |  |  |  |  | 엑셀상에서 자동계산
|  |  |  | Q'ty | Q | 1
11.Railings | # | RL-Q1 | [Handrail] | ▶ 모델 Parameter | [8 empty] | System Family
|  | = L/1000 | Handrail 길이 | 길이 | L |  |  |  | BP | Length | mm | Revit자동산출 | Railing
12.Generic | # | GM-Q1A | [Caged Ladder] | ▶ 모델 Parameter | [8 empty] | Load Family - Ladder
|  | = L/1000 | Ladder 길이 | 길이 | L |  |  |  | FP | Ladder_Length | mm | Revit자동산출
▶ 수동 입력 값 (엑셀 상에서 입력)
|  |  |  | pad 가로 | PW | 1.2 | m
|  |  |  | pad 세로 | PL | 0.9 | m
|  |  |  | pad 두께 | PT | 0.2 | m
| # | GM-Q1B | [Non-Caged Ladder] | ▶ 모델 Parameter | [8 empty] | Load Family - Ladder
|  | = L/1000 | Ladder 길이 | 길이 | L |  |  |  | FP | Id_total height | mm | Revit자동산출
| # | GM-Q2 | [Downspout & Splash Block] | ▶ 모델 Parameter | [8 empty] | Load Family - Downspout
|  | =L/1000 | Downspout 길이 | 길이 | L |  |  |  | BP | Length_System | mm | Revit자동산출
▶ 수동 입력 값 (엑셀 상에서 입력)
|  | = Q | Splash Block | Q'ty | Q | 1
| # | GM-Q3 | [Grouting] | ▶ 모델 Parameter | [8 empty] | Load Family - Grouting
|  | =V | Grout 물량 | Volume | V |  |  |  | BP | Volume | m3 | Revit자동산출
| # | GM-Q4 | [MISC : EA base] | ▶ 수동 입력 값 (엑셀 상에서 입력) | [8 empty] | Load Family - Grouting
|  | = Q | Grout 물량 | Q'ty | Q | 1
W
D'
D
C1
C2
C3
H
W
D
C2
T
R
W
L
T
H2
W
D
L
G
C1
C2
C3
D
H2
줄기초 재정리 ?
W
항목 추가
C1
C2
C3
Mat FDN Top level 이 GL 보다 높을때 - 값으로 산출됨 (합계에 반영될 수 있음) - 값은 0으로 산출되야함
C1
C2
C3
C1
C2
C3
C3
TCS
C1
C2
C3
Note on E8: Pak : Note 추가 Rev.4
Note on L40: HEC: Elevation at Bottom Survey 에서 Elevation at Bottom 으로 수정( GL에서 기초바닥 깊이는 하기에 입력한 FL-GL gap 으로 보정)
Note on D94: Pak : -4*D1*D1 추가
Note on D95: Pak : -4*D1*D1 추가
Note on E96: Pak : 항목 추가
Note on N105: Pak : Note 추가 Rev.4
Note on E150: Pak : - Floor 카테고리에서 이동 - 물량수식 수정
Note on E154: Pak : 항목 추가
Note on E155: Pak : 항목 추가
Note on E156: Pak : 항목 추가
Note on E187: Pak : 항목 추가 *Wall에 대한 Protection 미고려
Note on D192: Pak : 수식 수정 R4(05.02)
Note on D193: Pak : 수식 수정 R4(05.02)
Note on D194: Pak : 수식 수정 R4(05.02)
Note on D207: Pak : 수식 수정 R4(05.02)
Note on E208: Pak : 항목 추가
Note on D212: Pak : 수식 수정 R4(05.02)
Note on D213: Pak : 수식 수정 R4(05.02)
Note on E214: Pak : 항목 추가
Note on E235: Pak : 슬라브두께를 포함한 H로 변경
Note on L235: R4: Length => Depth
Note on E246: Pak : 슬라브두께를 포함한 H로 변경
Note on L246: R4: Length => Depth
Note on E270: Pak : 슬라브 두께 포함한 B로 변경 R4(05.02)
Note on E280: Pak : 슬라브 두께 포함한 B로 변경 R4(05.02)

## 0.Room
[Family List] - Room |  |  |  |  | 표준구성도로 가기
NO | Family Category | Building Tag | Q'ty Cal Type Tag | Standard Type | Family Type Name | 추천 WorkMaster | Work Master Code /w Description | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Description | 입찰_ 물량산출식 | 실행_ 물량산출식 | Quantity |  | Remark (물량관련)
0 | Room
0.1 | Basic Room
| □ Room - normal |  |  | ▶ Rooms
- | System Family |  | RM-Q1 | H_F91 / B35 / W02C / C95A | F91 / B35 / W02C / C95A | [31 empty] | 산출기준 >> [ 룸 일반 산출 ]
|  |  |  | 101 | CENTRAL CONTROL ROOM
|  |  |  | 102 | MEETING ROOM
|  |  |  | 103 | ENGINEERING ROOM
|  |  |  | 152 | CCR SIDE
|  |  | F91 | Floor | A04AS174-00002 ¦ ¦ A04AM080-00005 ¦
[5 empty] | Raised Floor ¦ Top Finish: Anti-Static Vinyl Tile ¦ ¦ | A04AS174-00002 | A04AS174-00002 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Anti-Static Vinyl Tile 600mm x 600mm / 600mm<H≤1000mm | A04AS174-00002 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Raised Floor | Top Finish: Anti-Static Vinyl Tile | 0 | 0 | 0 | 0 |  | 0 | 600mm x 600mm / 600mm<H≤1000mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A | 149.2 | M2
[5 empty] | Steel Trowel Finish ¦ ¦ ¦ | A04AM080-00005 | A04AS173-00001 Finishing Work Exterior/Interior Finish Work Steel Trowel Finish | A04AS173-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Steel Trowel Finish | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A | 149.2 | M2
[5 empty] | Floor Painting ¦ Epoxy Paint ¦ ¦ |  | A04AM080-00006 Finishing Work Painting Work Floor Painting Epoxy Paint | A04AM080-00006 |  | M2 | Finishing Work | Painting Work | Floor Painting | Epoxy Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | = A |  | M2 |  | slab 부재 구분되어 있지 않으면 부재에 eposy & steel trowerl 추가 힘듬
|  |  | B35 | Base | ¦ A04AN084-00013 ¦ ¦
[5 empty] | Skirt Tile ¦ Vinyl Tile ¦ ¦ | A04AN084-00013 | A04AN084-00013 Finishing Work Tile Work Skirt Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084-00013 |  | M | Finishing Work | Tile Work | Skirt Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = P/1000 | = P/1000 | 73.2 | M
|  |  | W02C | Wall | ¦ A04AM078-00002 ¦ ¦
[5 empty] | Internal Wall Painting ¦ Water Emulsion Paint ¦ ¦ | A04AM078-00002 | A04AM078-00002 Finishing Work Painting Work Internal Wall Painting Water Emulsion Paint | A04AM078-00002 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Water Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000) | 0 | M2
[32 empty] | = (P/1000)*(CH/1000) | _by "H_WA_AR_B07_Int Wall_Plaster"
[5 empty] | Internal Wall Painting ¦ Epoxy Paint ¦ ¦ |  | A04AM078-00005 Finishing Work Painting Work Internal Wall Painting Epoxy Paint | A04AM078-00005 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Epoxy Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * RH | = (P/1000) * 0.73 |  | M2
|  |  | C95A | Ceiling | ¦ A04AS190-00001 ¦ ¦
[5 empty] | Acoustic Tiled Ceiling System ¦ M-Bar System ¦ ¦ | A04AS190-00001 | A04AS190-00001 Finishing Work Exterior/Interior Finish Work Acoustic Tiled Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS190-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Acoustic Tiled Ceiling System | M-Bar System | 0 | 0 | 0 | 0 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | 0 | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * CR | = A |  | M2 | * 페인트의 경우 보측면 할증계수 적용 * 비 페인트의 경우 순수 면적
- | System Family |  | RM-Q1 | H_F34B / B35 / W02A / C92 | F34B / B35 / W02A / C92 | [31 empty] | 산출기준 >> [ 룸 일반 산출 ]
|  |  |  | 104 | CANTEEN
|  |  |  | 108 | LOCKER ROOM
|  |  |  | 113 | REST ROOM
|  |  |  | 151 | LOCKER ENTRANCE
|  |  | F34B | Floor | ¦ A04AN083-00004 ¦ ¦ A04AS168-00003
[5 empty] | Floor Tile ¦ Vinyl Tile ¦ ¦ | A04AN083-00004 | A04AN083-00004 Finishing Work Tile Work Floor Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive | A04AN083-00004 | B | M2 | Finishing Work | Tile Work | Floor Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
[5 empty] | Screed ¦ ¦ ¦ | A04AS168-00003 | A04AS168-00003 Finishing Work Exterior/Interior Finish Work Screed w/o Welded Wire Fabric 75mm≤THK | A04AS168-00003 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Screed | 0 | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | 75mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  | B35 | Base | ¦ A04AN084-00013 ¦ ¦
[5 empty] | Skirt Tile ¦ Vinyl Tile ¦ ¦ | A04AN084-00013 | A04AN084-00013 Finishing Work Tile Work Skirt Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084-00013 |  | M | Finishing Work | Tile Work | Skirt Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = P/1000 | = P/1000 |  | M
|  |  | W02A | Wall | ¦ A04AM078-00002 ¦ ¦
[5 empty] | Internal Wall Painting ¦ Water Emulsion Paint ¦ ¦ | A04AM078-00002 | A04AM078-00002 Finishing Work Painting Work Internal Wall Painting Water Emulsion Paint | A04AM078-00002 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Water Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000) |  | M2
[32 empty] | = (P/1000)*(CH/1000) | _by "H_WA_AR_B07_Int Wall_Plaster"
[32 empty] | = (P/1000) * RH | = (P/1000) * RH
|  |  | C92 | Ceiling | ¦ A04AS187-00001 ¦ ¦
[5 empty] | Gypsum Plaster Board Ceiling System ¦ M-Bar System ¦ ¦ | A04AS187-00001 | A04AS187-00001 Finishing Work Exterior/Interior Finish Work Gypsum Plaster Board Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) 1-Layer Gypsumboard THK=12.5mm | A04AS187-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Gypsum Plaster Board Ceiling System | M-Bar System | 0 | 0 | 0 | 0 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2 | * 페인트의 경우 보측면 할증계수 적용 * 비 페인트의 경우 순수 면적 | 12.5t 1 layer
- | System Family |  | RM-Q1 | H_F34B / B35 / W02A / C95A | F34B / B35 / W02A / C95A | [31 empty] | 산출기준 >> [ 룸 일반 산출 ]
|  |  |  | 116 | MAMA'S REST ROOM
|  |  | F34B | Floor | ¦ A04AN083-00004 ¦ ¦ A04AS168-00003
[5 empty] | Floor Tile ¦ Vinyl Tile ¦ ¦ | A04AN083-00004 | A04AN083-00004 Finishing Work Tile Work Floor Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive | A04AN083-00004 | B | M2 | Finishing Work | Tile Work | Floor Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
[5 empty] | Screed ¦ ¦ ¦ | A04AS168-00003 | A04AS168-00003 Finishing Work Exterior/Interior Finish Work Screed w/o Welded Wire Fabric 75mm≤THK | A04AS168-00003 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Screed | 0 | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | 75mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  | B35 | Base | ¦ A04AN084-00013 ¦ ¦
[5 empty] | Skirt Tile ¦ Vinyl Tile ¦ ¦ | A04AN084-00013 | A04AN084-00013 Finishing Work Tile Work Skirt Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084-00013 |  | M | Finishing Work | Tile Work | Skirt Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = P/1000 | = P/1000 |  | M
|  |  | W02A | Wall | ¦ A04AM078-00002 ¦ ¦
[5 empty] | Internal Wall Painting ¦ Water Emulsion Paint ¦ ¦ | A04AM078-00002 | A04AM078-00002 Finishing Work Painting Work Internal Wall Painting Water Emulsion Paint | A04AM078-00002 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Water Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000) |  | M2
[32 empty] | = (P/1000)*(CH/1000) | _by "H_WA_AR_B07_Int Wall_Plaster"
[32 empty] | = (P/1000) * RH | = (P/1000) * RH
|  |  | C95A | Ceiling | ¦ A04AS190-00001 ¦ ¦
[5 empty] | Acoustic Tiled Ceiling System ¦ M-Bar System ¦ ¦ | A04AS190-00001 | A04AS190-00001 Finishing Work Exterior/Interior Finish Work Acoustic Tiled Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS190-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Acoustic Tiled Ceiling System | M-Bar System | 0 | 0 | 0 | 0 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | 0 | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2 | * 페인트의 경우 보측면 할증계수 적용 * 비 페인트의 경우 순수 면적 | 12.5t 1 layer
- | System Family |  | RM-Q1 | H_F41 / B35 / W02A / C92 | F41 / B35 / W02A / C92 | [31 empty] | 산출기준 >> [ 룸 일반 산출 ]
|  |  |  | 105 | AIR LOCK
|  |  | F41 | Floor | ¦ A04AN083-00011 ¦ ¦
[5 empty] | Floor Tile ¦ Porcelain Tile ¦ ¦ | A04AN083-00011 | A04AN083-00011 Finishing Work Tile Work Floor Tile Porcelain Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083-00011 |  | M2 | Finishing Work | Tile Work | Floor Tile | Porcelain Tile | 0 | 0 | 0 | 0 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  | B35 | Base | ¦ A04AN084-00013 ¦ ¦
[5 empty] | Skirt Tile ¦ Vinyl Tile ¦ ¦ | A04AN084-00013 | A04AN084-00013 Finishing Work Tile Work Skirt Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084-00013 |  | M | Finishing Work | Tile Work | Skirt Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = P/1000 | = P/1000 |  | M
|  |  | W02A | Wall | ¦ A04AM078-00002 ¦ ¦
[5 empty] | Internal Wall Painting ¦ Water Emulsion Paint ¦ ¦ | A04AM078-00002 | A04AM078-00002 Finishing Work Painting Work Internal Wall Painting Water Emulsion Paint | A04AM078-00002 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Water Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000) |  | M2
[32 empty] | = (P/1000)*(CH/1000) | _by "H_WA_AR_B07_Int Wall_Plaster"
|  |  | C92 | Ceiling | ¦ A04AS187-00001 ¦ ¦ | [30 empty] | update 필요
[5 empty] | Aluminum Spandrel Ceiling System ¦ M-Bar System ¦ ¦ | A04AS187-00001 | A04AS192-00001 Finishing Work Exterior/Interior Finish Work Aluminum Spandrel Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS192-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Aluminum Spandrel Ceiling System | M-Bar System | 0 | 0 | 0 | 0 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2 | * 페인트의 경우 보측면 할증계수 적용 * 비 페인트의 경우 순수 면적
- | System Family |  | RM-Q1 | H_F34A / B35 / W02A / C95A | F34A / B35 / W02A / C95A | [31 empty] | 산출기준 >> [ 룸 일반 산출 ]
|  |  |  | 107 | OFFICE ROOM
|  |  |  | 111 | CORRIDOR
|  |  | F34A | Floor | ¦ A04AN083-00004 ¦ ¦
[5 empty] | Floor Tile ¦ Vinyl Tile ¦ ¦ | A04AN083-00004 | A04AN083-00004 Finishing Work Tile Work Floor Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive | A04AN083-00004 |  | M2 | Finishing Work | Tile Work | Floor Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  | B35 | Base | ¦ A04AN084-00013 ¦ ¦
[5 empty] | Skirt Tile ¦ Vinyl Tile ¦ ¦ | A04AN084-00013 | A04AN084-00013 Finishing Work Tile Work Skirt Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084-00013 |  | M | Finishing Work | Tile Work | Skirt Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = P/1000 | = P/1000 |  | M
|  |  | W02A | Wall | ¦ A04AM078-00002 ¦ ¦
[5 empty] | Internal Wall Painting ¦ Water Emulsion Paint ¦ ¦ | A04AM078-00002 | A04AM078-00002 Finishing Work Painting Work Internal Wall Painting Water Emulsion Paint | A04AM078-00002 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Water Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000) |  | M2
[32 empty] | = (P/1000)*(CH/1000) | _by "H_WA_AR_B07_Int Wall_Plaster"
|  |  | C95A | Ceiling | ¦ A04AS190-00001 ¦ ¦
[5 empty] | Ceiling Painting ¦ Water Emulsion Paint ¦ ¦ | A04AS190-00001 | A04AM079-00002 Finishing Work Painting Work Ceiling Painting Water Emulsion Paint | A04AM079-00002 |  | M2 | Finishing Work | Painting Work | Ceiling Painting | Water Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2 | * 페인트의 경우 보측면 할증계수 적용 * 비 페인트의 경우 순수 면적
- | System Family |  | RM-Q1 | H_F31C / B35 / W32F / C95A | F31C / B35 / W32F / C95A | [31 empty] | 산출기준 >> [ 룸 일반 산출 ]
|  |  |  | 109 | SHOWER ROOM
|  |  | F31C | Floor | ¦ A04AN083-00001 ¦ A04AP310-00001 ¦ A04AS168-00003
[5 empty] | Floor Tile ¦ Ceramic Tile ¦ ¦ | A04AN083-00001 | A04AN083-00001 Finishing Work Tile Work Floor Tile Ceramic Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083-00001 |  | M2 | Finishing Work | Tile Work | Floor Tile | Ceramic Tile | 0 | 0 | 0 | 0 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
[5 empty] | Waterproofing Membrane ¦ ¦ ¦ | A04AP310-00001 | A04AP310-00001 Finishing Work Waterproofing Work Waterproofing Membrane for Internal Area | A04AP310-00001 |  | M2 | Finishing Work | Waterproofing Work | Waterproofing Membrane | 0 | 0 | 0 | 0 | for Internal Area |  | 0 |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
[5 empty] | Screed ¦ ¦ ¦ | A04AS168-00003 | A04AS168-00003 Finishing Work Exterior/Interior Finish Work Screed w/o Welded Wire Fabric 75mm≤THK | A04AS168-00003 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Screed | 0 | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | 75mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  | B35 | Base | ¦ A04AN084-00013 ¦ ¦
[5 empty] | Skirt Tile ¦ Vinyl Tile ¦ ¦ | A04AN084-00013 | A04AN084-00013 Finishing Work Tile Work Skirt Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084-00013 |  | M | Finishing Work | Tile Work | Skirt Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = P/1000 |  |  | M
|  |  | W32F | Wall | ¦ A04AN082-00002 ¦ A04AP310-00001 ¦
[5 empty] | Wall Tile ¦ Glazed Ceramic Tile ¦ ¦ | A04AN082-00002 | A04AN082-00002 Finishing Work Tile Work Wall Tile Glazed Ceramic Tile w/ Mortar Bond Coat or Adhesive | A04AN082-00002 |  | M2 | Finishing Work | Tile Work | Wall Tile | Glazed Ceramic Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*MH | = (P/1000)*(CH/1000) |  | M2
[5 empty] | Waterproofing Membrane ¦ ¦ ¦ | A04AP310-00001 | A04AP310-00001 Finishing Work Waterproofing Work Waterproofing Membrane for Internal Area | A04AP310-00001 |  | M2 | Finishing Work | Waterproofing Work | Waterproofing Membrane | 0 | 0 | 0 | 0 | for Internal Area |  | 0 |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*MH | = (P/1000)*2.1 |  | M2
[32 empty] | = ( P/1000 )*( (CH/1000)-MH ) | = ( P/1000 )*( (CH/1000)-MH )
|  |  | C95A | Ceiling | ¦ A04AS190-00001 ¦ ¦
[5 empty] | Moisture Resistant Tiled Ceiling System ¦ M-Bar System ¦ ¦ | A04AS190-00001 | A04AS191-00001 Finishing Work Exterior/Interior Finish Work Moisture Resistant Tiled Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS191-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Moisture Resistant Tiled Ceiling System | M-Bar System | 0 | 0 | 0 | 0 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | 0 | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2 | * 페인트의 경우 보측면 할증계수 적용 * 비 페인트의 경우 순수 면적
- | System Family |  | RM-Q1 | H_F34A / B35 / W01A / C01 | F34A / B35 / W01A / C01 | [31 empty] | 산출기준 >> [ 룸 일반 산출 ]
|  |  |  | 110 | STAIRCASE
|  |  |  | 202 | STAIRCASE
|  |  |  | 302 | STAIRCASE
|  |  |  | R01 | STAIRCASE
|  | F43-1 | F34A | Floor | ¦ A04AN083-00004 ¦ ¦
[5 empty] | Floor Tile ¦ Vinyl Tile ¦ ¦ | A04AN083-00004 | A04AN083-00004 Finishing Work Tile Work Floor Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive | A04AN083-00004 |  | M2 | Finishing Work | Tile Work | Floor Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
[32 empty] | = A | = A
|  |  | B35 | Base | ¦ A04AN084-00013 ¦ ¦
[5 empty] | Skirt Tile ¦ Vinyl Tile ¦ ¦ | A04AN084-00013 | A04AN084-00013 Finishing Work Tile Work Skirt Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084-00013 |  | M | Finishing Work | Tile Work | Skirt Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = P/1000 | = P/1000 |  | M
|  |  | W01A | Wall | ¦ A04AM078-00001 ¦ ¦
[5 empty] | Internal Wall Painting ¦ Water Emulsion Paint ¦ ¦ | A04AM078-00001 | A04AM078-00002 Finishing Work Painting Work Internal Wall Painting Water Emulsion Paint | A04AM078-00002 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Water Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000) |  | M2
[32 empty] | = (P/1000)*(CH/1000) | _by "H_WA_AR_B07_Int Wall_Plaster"
|  |  | C01 | Ceiling | ¦ A04AM079-00001 ¦ ¦
[5 empty] | Ceiling Painting ¦ Water Emulsion Paint ¦ ¦ | A04AM079-00001 | A04AM079-00002 Finishing Work Painting Work Ceiling Painting Water Emulsion Paint | A04AM079-00002 |  | M2 | Finishing Work | Painting Work | Ceiling Painting | Water Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2 | * 페인트의 경우 보측면 할증계수 적용 * 비 페인트의 경우 순수 면적
- | System Family |  | RM-Q1 | H_F43 / B35 / W02A / C95A | F43 / B35 / W02A / C95A | [31 empty] | 산출기준 >> [ 룸 일반 산출 ]
|  |  |  | 112 | CONFERENCE ROOM
|  |  |  | 115 | PRESIDENT ROOM
|  |  | F43 | Floor | ¦ A04AS170-00001 ¦ ¦
[5 empty] | Carpet Tile ¦ ¦ ¦ | A04AS170-00001 | A04AS170-00001 Finishing Work Exterior/Interior Finish Work Carpet Tile | A04AS170-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Carpet Tile | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
[32 empty] | = A | = A
|  |  | B35 | Base | ¦ A04AN084-00013 ¦ ¦
[5 empty] | Skirt Tile ¦ Vinyl Tile ¦ ¦ | A04AN084-00013 | A04AN084-00013 Finishing Work Tile Work Skirt Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084-00013 |  | M | Finishing Work | Tile Work | Skirt Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = P/1000 | = P/1000 |  | M
|  |  | W02A | Wall | ¦ A04AM078-00002 ¦ ¦
[5 empty] | Internal Wall Painting ¦ Water Emulsion Paint ¦ ¦ | A04AM078-00002 | A04AM078-00002 Finishing Work Painting Work Internal Wall Painting Water Emulsion Paint | A04AM078-00002 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Water Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000) |  | M2
[32 empty] | = (P/1000)*(CH/1000) | _by "H_WA_AR_B07_Int Wall_Plaster"
|  |  | C95A | Ceiling | ¦ A04AS190-00001 ¦ ¦
[5 empty] | Gypsum Plaster Board Ceiling System ¦ M-Bar System ¦ ¦ | A04AS190-00001 | A04AS187-00001 Finishing Work Exterior/Interior Finish Work Gypsum Plaster Board Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) 1-Layer Gypsumboard THK=12.5mm | A04AS187-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Gypsum Plaster Board Ceiling System | M-Bar System | 0 | 0 | 0 | 0 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2 | * 페인트의 경우 보측면 할증계수 적용 * 비 페인트의 경우 순수 면적
- | System Family |  | RM-Q1 | H_F34A / B35 / W02A / C95A | F34A / B35 / W02A / C95A | [31 empty] | 산출기준 >> [ 룸 일반 산출 ]
|  |  |  | 114 | PARTNER'S OFFICE
|  |  |  | 117 | STORAGE
|  |  | F34A | Floor | ¦ A04AN083-00004 ¦ ¦
[5 empty] | Floor Tile ¦ Vinyl Tile ¦ ¦ | A04AN083-00004 | A04AN083-00004 Finishing Work Tile Work Floor Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive | A04AN083-00004 |  | M2 | Finishing Work | Tile Work | Floor Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
[32 empty] | = A | = A
|  |  | B35 | Base | ¦ A04AN084-00013 ¦ ¦
[5 empty] | Skirt Tile ¦ Vinyl Tile ¦ ¦ | A04AN084-00013 | A04AN084-00013 Finishing Work Tile Work Skirt Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084-00013 |  | M | Finishing Work | Tile Work | Skirt Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = P/1000 | = P/1000 |  | M
|  |  | W02A | Wall | ¦ A04AM078-00002 ¦ ¦
[5 empty] | Internal Wall Painting ¦ Water Emulsion Paint ¦ ¦ | A04AM078-00002 | A04AM078-00002 Finishing Work Painting Work Internal Wall Painting Water Emulsion Paint | A04AM078-00002 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Water Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000) |  | M2
[32 empty] | = (P/1000)*(CH/1000) | _by "H_WA_AR_B07_Int Wall_Plaster"
|  |  | C95A | Ceiling | ¦ A04AS190-00001 ¦ ¦
[5 empty] | Acoustic Tiled Ceiling System ¦ M-Bar System ¦ ¦ | A04AS190-00001 | A04AS190-00001 Finishing Work Exterior/Interior Finish Work Acoustic Tiled Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS190-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Acoustic Tiled Ceiling System | M-Bar System | 0 | 0 | 0 | 0 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | 0 | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2 | * 페인트의 경우 보측면 할증계수 적용 * 비 페인트의 경우 순수 면적
- | System Family |  | RM-Q1 | H_F31B / B35 / W34B / C96A | F31B / B35 / W34B / C96A | [31 empty] | 산출기준 >> [ 룸 일반 산출 ]
|  |  |  | 118 | DISABLED TOILET(W)
|  |  |  | 119 | DISABLED TOILET(M)
|  |  |  | 120 | TOILET(W)
|  |  |  | 121 | TOILET(M)
|  |  | F31B | Floor | ¦ A04AN083-00001 ¦ A04AP085-00001 ¦ A04AS168-00003
[5 empty] | Floor Tile ¦ Ceramic Tile ¦ ¦ | A04AN083-00001 | A04AN083-00001 Finishing Work Tile Work Floor Tile Ceramic Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083-00001 |  | M2 | Finishing Work | Tile Work | Floor Tile | Ceramic Tile | 0 | 0 | 0 | 0 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
[5 empty] | Liquid Waterproofing ¦ ¦ ¦ | A04AP085-00001 | A04AP085-00001 Finishing Work Waterproofing Work Liquid Waterproofing for Internal Floor Area Min. 2 Coats | A04AP085-00001 |  | M2 | Finishing Work | Waterproofing Work | Liquid Waterproofing | 0 | 0 | 0 | 0 | for Internal Floor Area | Min. 2 Coats | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
[5 empty] | Screed ¦ ¦ ¦ | A04AS168-00003 | A04AS168-00003 Finishing Work Exterior/Interior Finish Work Screed w/o Welded Wire Fabric 75mm≤THK | A04AS168-00003 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Screed | 0 | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | 75mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  | B35 | Base | ¦ A04AN084-00013 ¦ ¦
[6 empty] | A04AN084-00013 | [25 empty] | = P/1000 | = P/1000
|  |  | W34B | Wall | ¦ A04AN082-00002 ¦ A04AP085-00002 ¦
[5 empty] | Wall Tile ¦ Glazed Ceramic Tile ¦ ¦ | A04AN082-00002 | A04AN082-00002 Finishing Work Tile Work Wall Tile Glazed Ceramic Tile w/ Mortar Bond Coat or Adhesive | A04AN082-00002 |  | M2 | Finishing Work | Tile Work | Wall Tile | Glazed Ceramic Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000) |  | M2
[5 empty] | Liquid Waterproofing ¦ ¦ ¦ | A04AP085-00002 | A04AP085-00002 Finishing Work Waterproofing Work Liquid Waterproofing for Internal Wall Area Min. 2 Coats | A04AP085-00002 |  | M2 | Finishing Work | Waterproofing Work | Liquid Waterproofing | 0 | 0 | 0 | 0 | for Internal Wall Area | Min. 2 Coats | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*(CH/1000) | _by "H_WA_AR_B07_Int Wall_Plaster" |  | M2
|  |  | C96A | Ceiling | ¦ A04AS191-00001 ¦ ¦
[5 empty] | Moisture Resistant Tiled Ceiling System ¦ M-Bar System ¦ ¦ | A04AS191-00001 | A04AS191-00001 Finishing Work Exterior/Interior Finish Work Moisture Resistant Tiled Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS191-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Moisture Resistant Tiled Ceiling System | M-Bar System | 0 | 0 | 0 | 0 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | 0 | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2 | * 페인트의 경우 보측면 할증계수 적용 * 비 페인트의 경우 순수 면적
- | System Family |  | RM-Q1 | H_F06A / B03 / W01A / C01 | F06A / B03 / W01A / C01 | [31 empty] | 산출기준 >> [ 룸 일반 산출 ]
|  |  |  | 122 | CYLINDER ROOM (HFC-23)
|  |  |  | 124 | F.O TANK ROOM
|  |  |  | 201 | CABLE ROOM
|  |  |  | 301 | ELECTRICAL ROOM
|  |  | F06A | Floor | ¦ A04AM080-00006 ¦ ¦
[5 empty] | Floor Painting ¦ Epoxy Paint ¦ ¦ | A04AM080-00006 | A04AM080-00006 Finishing Work Painting Work Floor Painting Epoxy Paint | A04AM080-00006 |  | M2 | Finishing Work | Painting Work | Floor Painting | Epoxy Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  | B03 | Base | ¦ A04AM081-00007 ¦ ¦
[5 empty] | Skirt Painting ¦ Epoxy Paint ¦ ¦ | A04AM081-00007 | A04AM081-00007 Finishing Work Painting Work Skirt Painting Epoxy Paint H<150mm | A04AM081-00007 |  | M | Finishing Work | Painting Work | Skirt Painting | Epoxy Paint | 0 | 0 | 0 | 0 |  | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = P/1000 | = P/1000 |  | M
|  |  | W01A | Wall | ¦ A04AM078-00001 ¦ ¦
[5 empty] | Internal Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM078-00001 | A04AM078-00001 Finishing Work Painting Work Internal Wall Painting Acrylic Emulsion Paint | A04AM078-00001 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000) |  | M2
[32 empty] | = (P/1000)*(CH/1000) | _by "H_WA_AR_B07_Int Wall_Plaster"
|  |  | C01 | Ceiling | ¦ A04AM079-00001 ¦ ¦
[5 empty] | Ceiling Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM079-00001 | A04AM079-00001 Finishing Work Painting Work Ceiling Painting Acrylic Emulsion Paint | A04AM079-00001 |  | M2 | Finishing Work | Painting Work | Ceiling Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * CR | = A * CR |  | M2 | * 페인트의 경우 보측면 할증계수 적용 * 비 페인트의 경우 순수 면적
- | System Family |  | RM-Q1 | H_F03 / B35 / W04A / C01 | F03 / B35 / W04A / C01 | [31 empty] | 산출기준 >> [ 룸 일반 산출 ]
|  |  |  | 203 | BATTERY ROOM
|  |  | F03 | Floor | ¦ A04AM080-00003 ¦ ¦
[5 empty] | Floor Painting ¦ Acid/Alkaline Resistant Paint ¦ ¦ | A04AM080-00003 | A04AM080-00003 Finishing Work Painting Work Floor Painting Acid/Alkaline Resistant Paint | A04AM080-00003 |  | M2 | Finishing Work | Painting Work | Floor Painting | Acid/Alkaline Resistant Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  | B35 | Base | ¦ A04AN084-00013 ¦ ¦
[6 empty] | A04AN084-00013 | [25 empty] | = P/1000 | = P/1000
|  |  | W04A | Wall | ¦ A04AM078-00004 ¦ ¦
[5 empty] | Internal Wall Painting ¦ Acid/Alkaline Resistant Paint ¦ ¦ | A04AM078-00004 | A04AM078-00004 Finishing Work Painting Work Internal Wall Painting Acid/Alkaline Resistant Paint | A04AM078-00004 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Acid/Alkaline Resistant Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*MH | = (P/1000)*1.5 |  | M2
[32 empty] | = (P/1000)*MH | = (P/1000)*MH
[5 empty] | Internal Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ |  | A04AM078-00001 Finishing Work Painting Work Internal Wall Painting Acrylic Emulsion Paint | A04AM078-00001 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = ( P/1000 )*( (CH/1000)-1.5 ) | = ( P/1000 )*( (CH/1000)-1.5 ) |  | M2
|  |  | C01 | Ceiling | ¦ A04AM079-00001 ¦ ¦
[5 empty] | Ceiling Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM079-00001 | A04AM079-00001 Finishing Work Painting Work Ceiling Painting Acrylic Emulsion Paint | A04AM079-00001 |  | M2 | Finishing Work | Painting Work | Ceiling Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2 | * 페인트의 경우 보측면 할증계수 적용 * 비 페인트의 경우 순수 면적
- | System Family |  | RM-Q1 | H_F06A / B03 / W01A / C95A | F06A / B03 / W01A / C95A | [31 empty] | 산출기준 >> [ 룸 일반 산출 ]
|  |  |  | 125 | HVAC ROOM
|  |  | F06A | Floor | ¦ A04AM080-00006 ¦ ¦
[5 empty] | Floor Painting ¦ Epoxy Paint ¦ ¦ | A04AM080-00006 | A04AM080-00006 Finishing Work Painting Work Floor Painting Epoxy Paint | A04AM080-00006 |  | M2 | Finishing Work | Painting Work | Floor Painting | Epoxy Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
[32 empty] | = A | = A
[32 empty] | = A | = A
|  |  | B03 | Base | ¦ A04AM081-00007 ¦ ¦
[5 empty] | Skirt Painting ¦ Epoxy Paint ¦ ¦ | A04AM081-00007 | A04AM081-00007 Finishing Work Painting Work Skirt Painting Epoxy Paint H<150mm | A04AM081-00007 |  | M | Finishing Work | Painting Work | Skirt Painting | Epoxy Paint | 0 | 0 | 0 | 0 |  | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = P/1000 | = P/1000 |  | M
|  |  | W01A | Wall | ¦ A04AM078-00001 ¦ ¦
[5 empty] | Internal Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM078-00001 | A04AM078-00001 Finishing Work Painting Work Internal Wall Painting Acrylic Emulsion Paint | A04AM078-00001 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*MH | = (P/1000)*(CH/1000) |  | M2
[5 empty] | Acoustic Panel ¦ ¦ ¦ |  | A04AS181-00001 Finishing Work Exterior/Interior Finish Work Acoustic Panel for Wall w/ Accessories (Supporting Frame, Acoustic Insulation, Etc.) | A04AS181-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Acoustic Panel | 0 | 0 | 0 | 0 | for Wall | w/ Accessories (Supporting Frame, Acoustic Insulation, Etc.) | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000) |  | M2
|  |  | C95A | Ceiling | ¦ A04AS190-00001 ¦ ¦
[5 empty] | Rigid Insulation ¦ ¦ ¦ | A04AS190-00001 | A04AS194-00003 Finishing Work Exterior/Interior Finish Work Rigid Insulation for Exposed Ceiling Structure of Cable Room w/ Accessories 75mm≤THK | A04AS194-00003 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Rigid Insulation | 0 | 0 | 0 | 0 | for Exposed Ceiling Structure of Cable Room | w/ Accessories | 0 | 75mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * CR | = A * CR |  | M2 | * 페인트의 경우 보측면 할증계수 적용 * 비 페인트의 경우 순수 면적
- | System Family |  | RM-Q1 | H_F91 / B35 / W02A / C01 | F91 / B35 / W02A / C01 | [31 empty] | 산출기준 >> [ 룸 일반 산출 ]
|  |  |  | 303 | ELECTONIC ROOM
|  |  |  | 304 | CHARGER & UPS ROOM
|  |  |  | 305 | COMMUNICATION ROOM
|  |  | F91 | Floor | A04AS174-00002 ¦ ¦ A04AM080-00005 ¦
[5 empty] | Raised Floor ¦ Top Finish: Anti-Static Vinyl Tile ¦ ¦ | A04AS174-00002 | A04AS174-00002 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Anti-Static Vinyl Tile 600mm x 600mm / 600mm<H≤1000mm | A04AS174-00002 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Raised Floor | Top Finish: Anti-Static Vinyl Tile | 0 | 0 | 0 | 0 |  | 0 | 600mm x 600mm / 600mm<H≤1000mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
[5 empty] | Floor Painting ¦ Anti-Dust Paint ¦ ¦ | A04AM080-00005 | A04AM080-00005 Finishing Work Painting Work Floor Painting Anti-Dust Paint | A04AM080-00005 |  | M2 | Finishing Work | Painting Work | Floor Painting | Anti-Dust Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  | B35 | Base | ¦ A04AN084-00013 ¦ ¦
[5 empty] | Skirt Tile ¦ Vinyl Tile ¦ ¦ | A04AN084-00013 | A04AN084-00013 Finishing Work Tile Work Skirt Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084-00013 |  | M | Finishing Work | Tile Work | Skirt Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = P/1000 | = P/1000 |  | M
|  |  | W02A | Wall | ¦ A04AM078-00002 ¦ ¦
[5 empty] | Internal Wall Painting ¦ Water Emulsion Paint ¦ ¦ | A04AM078-00002 | A04AM078-00002 Finishing Work Painting Work Internal Wall Painting Water Emulsion Paint | A04AM078-00002 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Water Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000) |  | M2
[32 empty] | = (P/1000)*(CH/1000) | _by "H_WA_AR_B07_Int Wall_Plaster"
[5 empty] | Internal Wall Painting ¦ Anti-Dust Paint ¦ ¦ |  | A04AM078-00007 Finishing Work Painting Work Internal Wall Painting Anti-Dust Paint | A04AM078-00007 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Anti-Dust Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*0.7 | = ( P/1000 )*0.7 |  | M2
|  |  | C01 | Ceiling | ¦ A04AM079-00001 ¦ ¦
[5 empty] | Ceiling Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM079-00001 | A04AM079-00001 Finishing Work Painting Work Ceiling Painting Acrylic Emulsion Paint | A04AM079-00001 |  | M2 | Finishing Work | Painting Work | Ceiling Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2 | * 페인트의 경우 보측면 할증계수 적용 * 비 페인트의 경우 순수 면적
- | System Family |  | RM-Q1 | H_F34A / B35 / W02A / C95A | F34A / B35 / W02A / C95A | [31 empty] | 산출기준 >> [ 룸 일반 산출 ]
|  |  |  | 306 | TOOL ROOM
|  |  | F34A | Floor | ¦ A04AN083-00004 ¦ ¦
[5 empty] | Floor Tile ¦ Vinyl Tile ¦ ¦ | A04AN083-00004 | A04AN083-00004 Finishing Work Tile Work Floor Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive | A04AN083-00004 |  | M2 | Finishing Work | Tile Work | Floor Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
[5 empty] | Screed ¦ ¦ ¦ |  | A04AS168-00001 Finishing Work Exterior/Interior Finish Work Screed w/o Welded Wire Fabric THK<50mm | A04AS168-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Screed | 0 | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  | B35 | Base | ¦ A04AN084-00013 ¦ ¦
[5 empty] | Skirt Tile ¦ Vinyl Tile ¦ ¦ | A04AN084-00013 | A04AN084-00013 Finishing Work Tile Work Skirt Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084-00013 |  | M | Finishing Work | Tile Work | Skirt Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = P/1000 | = P/1000 |  | M
|  |  | W02A | Wall | ¦ A04AM078-00002 ¦ ¦
[5 empty] | Internal Wall Painting ¦ Water Emulsion Paint ¦ ¦ | A04AM078-00002 | A04AM078-00002 Finishing Work Painting Work Internal Wall Painting Water Emulsion Paint | A04AM078-00002 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Water Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000) |  | M2
[32 empty] | = (P/1000)*(CH/1000) | _by "H_WA_AR_B07_Int Wall_Plaster"
[32 empty] | = (P/1000)*0.7 | = ( P/1000 )*( (CH/1000)-MH )
|  |  | C95A | Ceiling | ¦ A04AS190-00001 ¦ ¦
[5 empty] | Acoustic Tiled Ceiling System ¦ M-Bar System ¦ ¦ | A04AS190-00001 | A04AS190-00001 Finishing Work Exterior/Interior Finish Work Acoustic Tiled Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS190-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Acoustic Tiled Ceiling System | M-Bar System | 0 | 0 | 0 | 0 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | 0 | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2 | * 페인트의 경우 보측면 할증계수 적용 * 비 페인트의 경우 순수 면적
- | System Family |  | RM-Q1 | H_F01 / B01 / W01A / C01 | F01 / B01 / W01A / C01 | [31 empty] | 산출기준 >> [ 룸 일반 산출 ]
|  | Building Tag |  | Room No | Room Name
|  |  | F01 | Floor | ¦ A04AM080-00001 ¦ ¦
[5 empty] | Floor Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM080-00001 | A04AM080-00001 Finishing Work Painting Work Floor Painting Acrylic Emulsion Paint | A04AM080-00001 |  | M2 | Finishing Work | Painting Work | Floor Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
[32 empty] | = A | = A
[32 empty] | = A | = A
[32 empty] | = A | = A
|  |  | B01 | Base | ¦ A04AM081-00001 ¦ ¦
[5 empty] | Skirt Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM081-00001 | A04AM081-00001 Finishing Work Painting Work Skirt Painting Acrylic Emulsion Paint H<150mm | A04AM081-00001 |  | M | Finishing Work | Painting Work | Skirt Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = P/1000 | = P/1000 |  | M
[32 empty] | = P/1000 | = P/1000
[32 empty] | = P/1000 | = P/1000
[32 empty] | = P/1000 | = P/1000
|  |  | W01A | Wall | ¦ A04AM078-00001 ¦ ¦
[5 empty] | Internal Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM078-00001 | A04AM078-00001 Finishing Work Painting Work Internal Wall Painting Acrylic Emulsion Paint | A04AM078-00001 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000) |  | M2
[32 empty] | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000)
[32 empty] | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000)
[32 empty] | = (P/1000)*(CH/1000) | = (P/1000)*(CH/1000)
|  |  | C01 | Ceiling | ¦ A04AM079-00001 ¦ ¦
[5 empty] | Ceiling Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM079-00001 | A04AM079-00001 Finishing Work Painting Work Ceiling Painting Acrylic Emulsion Paint | A04AM079-00001 |  | M2 | Finishing Work | Painting Work | Ceiling Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2 | * 페인트의 경우 보측면 할증계수 적용 * 비 페인트의 경우 순수 면적
[32 empty] | = A | = A
[32 empty] | = A | = A
[32 empty] | = A | = A

## 1.Floors
[Family List] - Floors |  |  |  |  | 표준구성도로 가기
NO | Family Category | Building Tag | Q'ty Cal Type Tag | Standard Type | Family Type Name | Work Master Code /w Description | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Description | 입찰_ 물량산출식 | 실행_ 물량산출식 | Quantity |  | Remark (물량관련)
1 | Floors ( FL )
1.1 | Floor (System Family)
| □ Concrete Slab |  |  | ▶ Concrete Slab
1.1.1.1.1 | System Family |  | FL-Q1 | H_FL_AR_S17_RC Slab | [31 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM C150 Type I or Type IA F'c (Cylinder Strength) = 28MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AF037-00003 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AF037-00003 |  | TON | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | KS D3504 SD400 (Fy=400MPa) | = V*RE | = V*RE |  | TON | RE=0.10
|  |  |  | 거푸집 | Form Work (1 time in use) ¦ Flat Form ¦ ¦ | A03AF036-00001 Concrete Work Superstructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF036-00001 |  | M2 | Concrete Work | Superstructure Work | Form Work (1 time in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
[5 empty] | H_FL_AR_S17_RC Slab T150_B1S1 | [25 empty] | = A | = A
H_FL_AR_S17_RC Slab T150_1S1
H_FL_AR_S17_RC Slab T150_2S1
H_FL_AR_S17_RC Slab T180_3S1
H_FL_AR_S17_RC Slab T200_SS1
H_FL_AR_S17_RC Slab T150_2S2
H_FL_AR_S17_RC Slab T150_GS1
[31 empty] | = A | = A
[31 empty] | = A | = A
1.1.1.1.2 | System Family |  | FL-Q1 | H_FL_AR_S17_RC Slab_S Trowel | [31 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM C150 Type I or Type IA F'c (Cylinder Strength) = 28MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AF037-00003 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AF037-00003 |  | TON | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | KS D3504 SD400 (Fy=400MPa) | = V*RE | = V*RE |  | TON | RE=0.10
|  |  |  | 거푸집 | Form Work (1 time in use) ¦ Flat Form ¦ ¦ | A03AF036-00001 Concrete Work Superstructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF036-00001 |  | M2 | Concrete Work | Superstructure Work | Form Work (1 time in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
| □ Concrete Slab |  |  | ▶ Roof Concrete Slab
1.1.1.2.1 | System Family |  | FL-Q1 | H_FL_AR_S17_Roof RC Slab | [31 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V | = V |  | M3 | *적용규칙A, 5.4
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AF037-00003 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AF037-00003 |  | TON | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V*RE | = V*RE |  | TON | RE=0.10
|  |  |  | 거푸집 | Form Work (1 time in use) ¦ Flat Form ¦ ¦ | A03AF036-00001 Concrete Work Superstructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF036-00001 |  | M2 | Concrete Work | Superstructure Work | Form Work (1 time in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
H_FL_AR_S17_RC Slab T150_RS1
H_FL_AR_S17_RC Slab T150_PHRS1
H_FL_AR_S17_RC Slab T150_2CS1
| □ Concrete Slab |  |  | ▶ Turbine Top Deck Slab
1.1.1.3.1 | System Family |  | FL-Q1 | H_FL_AR_S17_STG Top Slab | [25 empty] | Steam Turbine 기초 Top Desk Slab | [5 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 30MPa ≤ F'c (Cylinder Strength) < 35MPa ¦ | A03AE032-00019 Concrete Work Mass Concrete Work Structural Concrete Cement Type-1 30MPa ≤ F'c (Cylinder Strength) < 35MPa Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032-00019 |  | M3 | Concrete Work | Mass Concrete Work | Structural Concrete | 0 | Cement Type-1 | 30MPa ≤ F'c (Cylinder Strength) < 35MPa | 0 | 0 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AF037-00003 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AF037-00003 |  | TON | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V*RE | = V*RE |  | TON | RE=0.10
|  |  |  | 거푸집 | Form Work (1 time in use) ¦ Flat Form ¦ ¦ | A03AF036-00001 Concrete Work Superstructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF036-00001 |  | M2 | Concrete Work | Superstructure Work | Form Work (1 time in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
| □ Concrete Deck Slab |  |  | ▶ Concrete Deck Slab
1.1.1.4.1 | System Family |  | FL-Q1 | H_FL_AR_S17_RC Deck Slab | [25 empty] | Steel Deck Slab | [5 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM C150 Type I or Type IA F'c (Cylinder Strength) = 28MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AF037-00003 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AF037-00003 |  | TON | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | KS D3504 SD400 (Fy=400MPa) | = V*RE | = V*RE |  | TON | RE=0.10
|  |  |  | 데크_제작 | Galvanized Steel Deck Plate ¦ ¦ ¦ | S02AA024-00001 Miscellaneous Steel Fabrication Work Shelter/Building Galvanized Steel Deck Plate | S02AA024-00001 |  | M2 | Miscellaneous Steel Fabrication Work | Shelter/Building | Galvanized Steel Deck Plate | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | THK=(1.6) mm 600x200x75 | = A | = A |  | M2
|  |  |  | 데크_시공 | Galvanized Steel Deck Plate ¦ ¦ ¦ | S04AA024-00001 Miscellaneous Steel Erection Work Shelter/Building Galvanized Steel Deck Plate | S04AA024-00001 |  | M2 | Miscellaneous Steel Erection Work | Shelter/Building | Galvanized Steel Deck Plate | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | THK=(1.6) mm 600x200x75 | = A | = A |  | M2
1.1.1.4.2 | System Family |  | FL-Q1 | H_FL_AR_S17_RC Deck Slab_S Trowel | [25 empty] | Steel Deck Slab | [5 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM C150 Type I or Type IA F'c (Cylinder Strength) = 28MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AF037-00003 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AF037-00003 |  | TON | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | KS D3504 SD400 (Fy=400MPa) | = V*RE | = V*RE |  | TON | RE=0.10
|  |  |  | 데크_제작 | Galvanized Steel Deck Plate ¦ ¦ ¦ | S02AA024-00001 Miscellaneous Steel Fabrication Work Shelter/Building Galvanized Steel Deck Plate | S02AA024-00001 |  | M2 | Miscellaneous Steel Fabrication Work | Shelter/Building | Galvanized Steel Deck Plate | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | THK=(1.6) mm 600x200x75 | = A | = A |  | M2
|  |  |  | 데크_시공 | Galvanized Steel Deck Plate ¦ ¦ ¦ | S04AA024-00001 Miscellaneous Steel Erection Work Shelter/Building Galvanized Steel Deck Plate | S04AA024-00001 |  | M2 | Miscellaneous Steel Erection Work | Shelter/Building | Galvanized Steel Deck Plate | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | THK=(1.6) mm 600x200x75 | = A | = A |  | M2
|  |  |  | Steel Trowel | Steel Trowel Finish ¦ ¦ ¦ | A04AS173-00001 Finishing Work Exterior/Interior Finish Work Steel Trowel Finish | A04AS173-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Steel Trowel Finish | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
| □ Concrete Deck Slab |  |  | ▶ Roof Concrete Deck Slab
1.1.1.5.1 | System Family |  | FL-Q1 | H_RF_AR_S17_Roof RC Deck Slab | [31 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AF037-00003 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AF037-00003 |  | TON | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V*RE | = V*RE |  | TON | RE=0.10
|  |  |  | 데크_제작 | Galvanized Steel Deck Plate ¦ ¦ ¦ | S02AA024-00001 Miscellaneous Steel Fabrication Work Shelter/Building Galvanized Steel Deck Plate | S02AA024-00001 |  | M2 | Miscellaneous Steel Fabrication Work | Shelter/Building | Galvanized Steel Deck Plate | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | THK=(1.6) mm 600x200x75 | = A | = A |  | M2
|  |  |  | 데크_시공 | Galvanized Steel Deck Plate ¦ ¦ ¦ | S04AA024-00001 Miscellaneous Steel Erection Work Shelter/Building Galvanized Steel Deck Plate | S04AA024-00001 |  | M2 | Miscellaneous Steel Erection Work | Shelter/Building | Galvanized Steel Deck Plate | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | THK=(1.6) mm 600x200x75 | = A | = A |  | M2
| □ Checkered / Grating |  |  | ▶ Grating Floor
1.1.2.1.1 | System Family |  | FL-Q1 | H_FL_AR_S05_Grating | [25 empty] | Grating | [5 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  |  | 그레이팅_제작 | Grating ¦ Hot-Dip Galvanized Steel, (I=32) ¦ ¦ | S02AA018-00003 Miscellaneous Steel Fabrication Work Shelter/Building Grating Hot-Dip Galvanized Steel, (I=32) | S02AA018-00003 |  | M2 | Miscellaneous Steel Fabrication Work | Shelter/Building | Grating | Hot-Dip Galvanized Steel, (I=32) | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ASTM A 1011M ) THK=( 32 )mm | = A | = A |  | M2
|  |  |  | 그레이팅_시공 | Grating ¦ Hot-Dip Galvanized Steel, (I=32) ¦ ¦ | S04AA018-00003 Miscellaneous Steel Erection Work Shelter/Building Grating Hot-Dip Galvanized Steel, (I=32) | S04AA018-00003 |  | M2 | Miscellaneous Steel Erection Work | Shelter/Building | Grating | Hot-Dip Galvanized Steel, (I=32) | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ASTM A 1011M ) THK=( 32 )mm | = A | = A |  | M2
H_FL_AR_S05_Grating_T32
Template
Template
Template
| □ Checkered / Grating |  |  | ▶ Removable Grating Floor
1.1.2.2.1 | System Family |  | FL-Q1 | H_FL_AR_S06_Removable Grating | [25 empty] | *WM : Removable Grating 구분 없음 | [5 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  |  | 그레이팅_제작 | Grating ¦ Hot-Dip Galvanized Steel, (I=32) ¦ ¦ | S02AA018-00003 Miscellaneous Steel Fabrication Work Shelter/Building Grating Hot-Dip Galvanized Steel, (I=32) | S02AA018-00003 | (a) | M2 | Miscellaneous Steel Fabrication Work | Shelter/Building | Grating | Hot-Dip Galvanized Steel, (I=32) | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ASTM A 1011M ) THK=( 32 )mm, Removable Type | = A | = A |  | M2
|  |  |  | 그레이팅_시공 | Grating ¦ Hot-Dip Galvanized Steel, (I=32) ¦ ¦ | S04AA018-00003 Miscellaneous Steel Erection Work Shelter/Building Grating Hot-Dip Galvanized Steel, (I=32) | S04AA018-00003 | (a) | M2 | Miscellaneous Steel Erection Work | Shelter/Building | Grating | Hot-Dip Galvanized Steel, (I=32) | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ASTM A 1011M ) THK=( 32 )mm, Removable Type | = A | = A |  | M2
| □ Checkered / Grating |  |  | ▶ Checkered Plate Floor
1.1.2.3.1 | System Family |  | FL-Q1 | H_FL_AR_S07_CHK PL | [25 empty] | Checkered Plate | [5 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  |  | 체커드_제작 | Checkered/Flooring Plate ¦ Galvanized Steel ¦ ¦ | S02AA017-00003 Miscellaneous Steel Fabrication Work Shelter/Building Checkered/Flooring Plate Galvanized Steel THK ≤ 6mm | S02AA017-00003 |  | M2 | Miscellaneous Steel Fabrication Work | Shelter/Building | Checkered/Flooring Plate | Galvanized Steel | THK ≤ 6mm | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ASTM A36 ) THK=( 6 )mm | = A | = A |  | M2
|  |  |  | 체커드_시공 | Checkered/Flooring Plate ¦ ¦ ¦ | S04AA017-00001 Miscellaneous Steel Erection Work Shelter/Building Checkered/Flooring Plate | S04AA017-00001 |  | M2 | Miscellaneous Steel Erection Work | Shelter/Building | Checkered/Flooring Plate | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | THK=( )mm | 0 | 0 | Material: ( ASTM A36 ) THK=( 6 )mm | = A | = A |  | M2
H_FL_AR_S07_CHK PL_T6
Template
| □ Finish |  |  | ▶ Tile
[Ceramic Tile]
1.1.3.1.1 | System Family |  | FL-Q1 | H_FL_AR_B07_Ceramic Tile |  | F31A | [6 empty] | F31A | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
[5 empty] | Floor Tile ¦ Ceramic Tile ¦ ¦ | A04AN083-00001 Finishing Work Tile Work Floor Tile Ceramic Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083-00001 |  | M2 | Finishing Work | Tile Work | Floor Tile | Ceramic Tile | 0 | 0 | 0 | 0 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | _by Rooms | _by Rooms |  | M2
1.1.3.1.2 | System Family |  | FL-Q1 | H_FL_AR_B07_Ceramic Tile_L Waterproof |  | F31B | [6 empty] | F31B | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  |  | 스크리드 | Screed ¦ ¦ ¦ | A04AS168-00001 Finishing Work Exterior/Interior Finish Work Screed w/o Welded Wire Fabric THK<50mm | A04AS168-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Screed | 0 | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Drain Slope | _by Rooms | = A |  | M2
|  |  |  | 방수 | Liquid Waterproofing ¦ ¦ ¦ | A04AP085-00001 Finishing Work Waterproofing Work Liquid Waterproofing for Internal Floor Area Min. 2 Coats | A04AP085-00001 |  | M2 | Finishing Work | Waterproofing Work | Liquid Waterproofing | 0 | 0 | 0 | 0 | for Internal Floor Area | Min. 2 Coats | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | _by Rooms | = A |  | M2
|  |  |  | 타일 | Floor Tile ¦ Ceramic Tile ¦ ¦ | A04AN083-00001 Finishing Work Tile Work Floor Tile Ceramic Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083-00001 |  | M2 | Finishing Work | Tile Work | Floor Tile | Ceramic Tile | 0 | 0 | 0 | 0 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( 300 )mm x L( 300 )mm x THK( 7 )mm | _by Rooms | _by Rooms |  | M2
1.1.3.1.3 | System Family |  | FL-Q1 | H_FL_AR_B07_Ceramic Tile_Memb |  | F31C | [6 empty] | F31C | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  |  | 스크리드 | Screed ¦ ¦ ¦ | A04AS168-00001 Finishing Work Exterior/Interior Finish Work Screed w/o Welded Wire Fabric THK<50mm | A04AS168-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Screed | 0 | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Drain Slope | _by Rooms | = A |  | M2
|  |  |  | 방수 | Waterproofing Membrane ¦ ¦ ¦ | A04AP310-00001 Finishing Work Waterproofing Work Waterproofing Membrane for Internal Area | A04AP310-00001 |  | M2 | Finishing Work | Waterproofing Work | Waterproofing Membrane | 0 | 0 | 0 | 0 | for Internal Area |  | 0 |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | _by Rooms | = A |  | M2
|  |  | No BM | 타일 | Floor Tile ¦ Ceramic Tile ¦ ¦ | A04AN083-00001 Finishing Work Tile Work Floor Tile Ceramic Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083-00001 |  | M2 | Finishing Work | Tile Work | Floor Tile | Ceramic Tile | 0 | 0 | 0 | 0 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( 7 )mm | _by Rooms | _by Rooms |  | M2
| □ Finish |  |  | ▶ Tile
[Acid Resistant Tile]
1.1.3.1.4 | System Family |  | FL-Q1 | H_FL_AR_B07_Acid R Tile |  | F32A | [6 empty] | F32A | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  | No BM |  | Floor Tile ¦ Acid/Alkaline Resistant Tile ¦ ¦ | A04AN083-00002 Finishing Work Tile Work Floor Tile Acid/Alkaline Resistant Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083-00002 |  | M2 | Finishing Work | Tile Work | Floor Tile | Acid/Alkaline Resistant Tile | 0 | 0 | 0 | 0 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | _by Rooms | _by Rooms |  | M2
1.1.3.1.5 | System Family |  | FL-Q1 | H_FL_AR_B07_Acid R Tile_L Waterproof |  | F32B | [6 empty] | F32B | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  |  | 스크리드 | Screed ¦ ¦ ¦ | A04AS168-00001 Finishing Work Exterior/Interior Finish Work Screed w/o Welded Wire Fabric THK<50mm | A04AS168-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Screed | 0 | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Drain Slope | _by Rooms | = A |  | M2
|  |  |  | 방수 | Liquid Waterproofing ¦ ¦ ¦ | A04AP085-00001 Finishing Work Waterproofing Work Liquid Waterproofing for Internal Floor Area Min. 2 Coats | A04AP085-00001 |  | M2 | Finishing Work | Waterproofing Work | Liquid Waterproofing | 0 | 0 | 0 | 0 | for Internal Floor Area | Min. 2 Coats | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | _by Rooms | = A |  | M2
|  |  | No BM | 타일 | Floor Tile ¦ Acid/Alkaline Resistant Tile ¦ ¦ | A04AN083-00002 Finishing Work Tile Work Floor Tile Acid/Alkaline Resistant Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083-00002 |  | M2 | Finishing Work | Tile Work | Floor Tile | Acid/Alkaline Resistant Tile | 0 | 0 | 0 | 0 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( 7 )mm | _by Rooms | _by Rooms |  | M2
| □ Finish |  |  | ▶ Tile
[Vinyl Tile]
1.1.3.1.6 | System Family |  | FL-Q1 | H_FL_AR_B07_Vinyl Tile |  | F34A | [6 empty] | F34A | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  | No BM |  | Floor Tile ¦ Vinyl Tile ¦ ¦ | A04AN083-00004 Finishing Work Tile Work Floor Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive | A04AN083-00004 |  | M2 | Finishing Work | Tile Work | Floor Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | _by Rooms | _by Rooms |  | M2
1.1.3.1.7 | System Family |  | FL-Q1 | H_FL_AR_B07_Vinyl Tile_Screed |  | F34B | [6 empty] | F34B | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  |  | 스크리드 | Screed ¦ ¦ ¦ | A04AS168-00001 Finishing Work Exterior/Interior Finish Work Screed w/o Welded Wire Fabric THK<50mm | A04AS168-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Screed | 0 | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Drain Slope | _by Rooms | = A |  | M2
|  |  | No BM | 타일 | Floor Tile ¦ Vinyl Tile ¦ ¦ | A04AN083-00004 Finishing Work Tile Work Floor Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive | A04AN083-00004 |  | M2 | Finishing Work | Tile Work | Floor Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( 7 )mm | _by Rooms | _by Rooms |  | M2
1.1.3.1.8 | System Family |  | FL-Q1 | H_FL_AR_B07_Anti Static Vinyl Tile |  | F35 | [6 empty] | F35 | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  | No BM |  | Floor Tile ¦ Anti-Static Vinyl Tile ¦ ¦ | A04AN083-00005 Finishing Work Tile Work Floor Tile Anti-Static Vinyl Tile w/ Mortar Bond Coat or Adhesive | A04AN083-00005 |  | M2 | Finishing Work | Tile Work | Floor Tile | Anti-Static Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | _by Rooms | _by Rooms |  | M2
| □ Finish |  |  | ▶ Tile
[Etc. Tile]
| System Family |  | FL-Q1 | H_FL_AR_B07_Terrazzo Tile |  | F33 | [6 empty] | F36 | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  | No BM |  | Floor Tile ¦ Granite Tile ¦ ¦ | A04AN083-00006 Finishing Work Tile Work Floor Tile Granite Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083-00006 |  | M2 | Finishing Work | Tile Work | Floor Tile | Granite Tile | 0 | 0 | 0 | 0 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | _by Rooms | _by Rooms |  | M2
1.1.3.1.9 | System Family |  | FL-Q1 | H_FL_AR_B07_Granite Tile |  | F36 | [6 empty] | F36 | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  | No BM |  | Floor Tile ¦ Granite Tile ¦ ¦ | A04AN083-00006 Finishing Work Tile Work Floor Tile Granite Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083-00006 |  | M2 | Finishing Work | Tile Work | Floor Tile | Granite Tile | 0 | 0 | 0 | 0 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | _by Rooms | _by Rooms |  | M2
1.1.3.1.10 | System Family |  | FL-Q1 | H_FL_AR_B07_Marble Tile |  | F37 | [6 empty] | F37 | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  | No BM |  | Floor Tile ¦ Marble Tile ¦ ¦ | A04AN083-00007 Finishing Work Tile Work Floor Tile Marble Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083-00007 |  | M2 | Finishing Work | Tile Work | Floor Tile | Marble Tile | 0 | 0 | 0 | 0 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | _by Rooms | _by Rooms |  | M2
1.1.3.1.11 | System Family |  | FL-Q1 | H_FL_AR_B07_Stone Tile |  | F38 | [6 empty] | F38 | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  | No BM |  | Floor Tile ¦ Stone Tile ¦ ¦ | A04AN083-00008 Finishing Work Tile Work Floor Tile Stone Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083-00008 |  | M2 | Finishing Work | Tile Work | Floor Tile | Stone Tile | 0 | 0 | 0 | 0 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | _by Rooms | _by Rooms |  | M2
1.1.3.1.12 | System Family |  | FL-Q1 | H_FL_AR_B07_Porcelain Tile |  | F39 | [6 empty] | F41 | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  | No BM |  | Floor Tile ¦ Porcelain Tile ¦ ¦ | A04AN083-00011 Finishing Work Tile Work Floor Tile Porcelain Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083-00011 |  | M2 | Finishing Work | Tile Work | Floor Tile | Porcelain Tile | 0 | 0 | 0 | 0 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( 9 )mm | _by Rooms | _by Rooms |  | M2
1.1.3.1.13 | System Family |  | FL-Q1 | H_FL_AR_B07_Carpet Tile |  | F43 | [6 empty] | F43 | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  | No BM |  | Carpet Tile ¦ ¦ ¦ | A04AS170-00001 Finishing Work Exterior/Interior Finish Work Carpet Tile | A04AS170-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Carpet Tile | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( 9 )mm | _by Rooms | _by Rooms |  | M2
| □ Finish |  |  | ▶ Mat
1.1.3.2.1 | System Family |  | FL-Q1 | H_FL_AR_B07_Carpet |  | F71 | [6 empty] | F71 | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
[5 empty] | Carpet ¦ ¦ ¦ | A04AS169-00001 Finishing Work Exterior/Interior Finish Work Carpet | A04AS169-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Carpet | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
1.1.3.2.2 | System Family |  | FL-Q1 | H_FL_AR_B07_Matwell |  | F72 | [6 empty] | F72 | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
[5 empty] | Recess Floor Mat ¦ ¦ ¦ | A04AS171-00001 Finishing Work Exterior/Interior Finish Work Recess Floor Mat | A04AS171-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Recess Floor Mat | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
1.1.3.2.3 | System Family |  | FL-Q1 | H_FL_AR_B07_Entrance Floor Mats and Frame |  | F73 | [6 empty] | F73 | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
[5 empty] | Entrance Floor Mats and Frame ¦ Embedded Type ¦ ¦ | A04AS172-00002 Finishing Work Exterior/Interior Finish Work Entrance Floor Mats and Frame Embedded Type | A04AS172-00002 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Entrance Floor Mats and Frame | Embedded Type | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
| □ Finish |  |  | ▶ Raised Floor
1.1.3.3.1 | System Family |  | FL-Q1 | H_FL_AR_B10_Raised Floor_600x600 |  | F91, F92, F93 | [6 empty] | F91 | [22 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  |  | 바닥 페인트 | Floor Painting ¦ Anti-Dust Paint ¦ ¦ | A04AM080-00005 Finishing Work Painting Work Floor Painting Anti-Dust Paint | A04AM080-00005 |  | M2 | Finishing Work | Painting Work | Floor Painting | Anti-Dust Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | _by Rooms | = A |  | M2
|  |  |  | Raised Floor | Raised Floor ¦ Top Finish: Anti-Static Vinyl Tile ¦ ¦ | A04AS174-00002 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Anti-Static Vinyl Tile 600mm x 600mm / 600mm<H≤1000mm | A04AS174-00002 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Raised Floor | Top Finish: Anti-Static Vinyl Tile | 0 | 0 | 0 | 0 |  | 0 | 600mm x 600mm / 600mm<H≤1000mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | 600x600x H=( 1000 )mm Top Finish: Anti-Static Vinyl Tile | _by Rooms | _by Rooms |  | M2
| □ Finish |  |  | ▶ UG Insulation
1.1.3.4.1 | System Family |  | FL-Q1 | H_FL_AR_B07_Ground Insulation | [31 empty] | 산출기준 >> [ 플로어 일반 산출 ]
[5 empty] | Insulation under Ground Floor ¦ Extruded Polystyrene Insulation Board ¦ ¦ | A03AD047-00003 Concrete Work Substructure Work Insulation under Ground Floor Extruded Polystyrene Insulation Board 75mm≤THK<100mm | A03AD047-00003 |  | M2 | Concrete Work | Substructure Work | Insulation under Ground Floor | Extruded Polystyrene Insulation Board | 0 | 0 | 0 | 0 |  | 0 | 75mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 50 )mm | _by "▶ SOG Slab" | = A |  | M2
H_FL_AR_B07_Ground Insulation_T110
1.2 | Slab Edge (System Family)
| □ Edge - normal |  |  | ▶ Edge
1.2.1.1.1 | System Family |  | FL-Q1 | H_FL_AR_S17_Thickened | [31 empty] | 산출기준 >> [ 플로어 일반 산출 ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM C150 Type I or Type IA F'c (Cylinder Strength) = 28MPa | _by "▶ SOG Slab" | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AF037-00003 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AF037-00003 |  | TON | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | KS D3504 SD400 (Fy=400MPa) | _by "▶ SOG Slab" | = V*RE |  | TON | RE=0.10
H_SF_AR_S17_Thickened_SOG Edge_600x300
삭제
Str. FDN 카테고리에서 입력 요망

## 2.Roofs
[Family List] - Roofs |  |  |  |  | 표준구성도로 가기
NO | Family Category | Building Tag | Q'ty Cal Type Tag | Standard Type | Family Type Name | Work Master Code /w Description | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Description | 입찰_ 물량산출식 | 실행_ 물량산출식 | Quantity |  | Remark (물량관련)
2 | Roofs [RF]
2.1 | Basic Roof (System Family)
| □ For Concrete Roof |  |  | ▶ Slope < Insulation < Waterproofing
2.1.1.1.1 | System Family |  | RF-Q1 | H_RF_AR_B06_LW Conc(Slope)_XPS_Memb |  | RF11 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
|  |  |  | 보호/보조층 | Roof Screed ¦ Light-Weight Concrete Screed ¦ ¦ | A04AQ086-00001 Finishing Work Roof Work Roof Screed Light-Weight Concrete Screed w/o Welded Wire Fabric 30mm≤Min. THK<50mm | A04AQ086-00001 |  | M3 | Finishing Work | Roof Work | Roof Screed | Light-Weight Concrete Screed | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | 30mm≤Min. THK<50mm | 0 | Min. THK=( )mm, Slope=( ) | 0 | 0 | 0 | 0 | 0 | 0 |  | Min. THK=( 30 )mm, Slope=( 1% ) | = A*Ts | = A*Ts |  | M3 | *적용규칙A, 5.4
|  |  |  | 와이어메쉬 | Welded Wire Fabric ¦ ¦ ¦ | A04AQ038-00001 Finishing Work Roof Work Welded Wire Fabric DIA≤6mm | A04AQ038-00001 |  | M2 | Finishing Work | Roof Work | Welded Wire Fabric | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIA≤6mm | 0 | Mesh Size=DIA( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Mesh Size=DIA( #8 )mm x ( 150 )mm x (150 )mm | = A | = A |  | M2
|  |  |  | 단열층 | Roof Insulation ¦ Rigid Extruded Polystyrene Foam Insulation ¦ ¦ | A04AQ088-00004 Finishing Work Roof Work Roof Insulation Rigid Extruded Polystyrene Foam Insulation 100mm≤THK | A04AQ088-00004 |  | M2 | Finishing Work | Roof Work | Roof Insulation | Rigid Extruded Polystyrene Foam Insulation | 0 | 0 | 0 | 0 |  | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | XPS THK=( 120 )mm | = A | = A |  | M2
|  |  |  | 방수층 | Waterproofing Membrane ¦ EPDM(or Equivalent) ¦ ¦ | A04AQ310-00001 Finishing Work Roof Work Waterproofing Membrane EPDM(or Equivalent) w/ Accessories | A04AQ310-00001 |  | M2 | Finishing Work | Roof Work | Waterproofing Membrane | EPDM(or Equivalent) | 0 | 0 | 0 | 0 | w/ Accessories | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2 | *적용규칙A, 5.3
H_RF_AR_B06_LW Conc(Slope)_XPS_Memb_T150
2.1.1.1.2 | System Family |  | RF-Q1 | H_RF_AR_B06_Mortar(Slope)_XPS_Memb |  | RF12 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
|  |  |  | 보호/보조층 | Roof Screed ¦ Bed Mortar Screed ¦ ¦ | A04AQ086-00004 Finishing Work Roof Work Roof Screed Bed Mortar Screed w/o Welded Wire Fabric 30mm≤Min. THK<50mm | A04AQ086-00004 |  | M3 | Finishing Work | Roof Work | Roof Screed | Bed Mortar Screed | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | 30mm≤Min. THK<50mm | 0 | Min. THK=( )mm, Slope=( ) | 0 | 0 | 0 | 0 | 0 | 0 |  | Min. THK=( 30 )mm, Slope=( 1% ) | = A*Ts | = A*Ts |  | M3 | *적용규칙A, 5.4
|  |  |  | 와이어메쉬 | Welded Wire Fabric ¦ ¦ ¦ | A04AQ038-00001 Finishing Work Roof Work Welded Wire Fabric DIA≤6mm | A04AQ038-00001 |  | M2 | Finishing Work | Roof Work | Welded Wire Fabric | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIA≤6mm | 0 | Mesh Size=DIA( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Mesh Size=DIA( #8 )mm x ( 150 )mm x (150 )mm | = A | = A |  | M2
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A04AQ012-00001 Finishing Work Roof Work PE Sheet (Vapor Barrier) | A04AQ012-00001 |  | M2 | Finishing Work | Roof Work | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm, 2ply | = A | = A |  | M2
|  |  |  | 단열층 | Roof Insulation ¦ Rigid Extruded Polystyrene Foam Insulation ¦ ¦ | A04AQ088-00004 Finishing Work Roof Work Roof Insulation Rigid Extruded Polystyrene Foam Insulation 100mm≤THK | A04AQ088-00004 |  | M2 | Finishing Work | Roof Work | Roof Insulation | Rigid Extruded Polystyrene Foam Insulation | 0 | 0 | 0 | 0 |  | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 120 )mm | = A | = A |  | M2
|  |  |  | 방수층 | Waterproofing Membrane ¦ EPDM(or Equivalent) ¦ ¦ | A04AQ310-00001 Finishing Work Roof Work Waterproofing Membrane EPDM(or Equivalent) w/ Accessories | A04AQ310-00001 |  | M2 | Finishing Work | Roof Work | Waterproofing Membrane | EPDM(or Equivalent) | 0 | 0 | 0 | 0 | w/ Accessories | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2 | *적용규칙A, 5.3
H_RF_AR_B06_Mortar(Slope)_XPS_Memb_T150
2.1.1.1.3 | System Family |  | RF-Q1 | H_RF_AR_B06_LW Conc(Slope)_XPS_Memb_Gravel |  | RF13 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
|  |  |  | 보호/보조층 | Roof Screed ¦ Light-Weight Concrete Screed ¦ ¦ | A04AQ086-00001 Finishing Work Roof Work Roof Screed Light-Weight Concrete Screed w/o Welded Wire Fabric 30mm≤Min. THK<50mm | A04AQ086-00001 |  | M3 | Finishing Work | Roof Work | Roof Screed | Light-Weight Concrete Screed | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | 30mm≤Min. THK<50mm | 0 | Min. THK=( )mm, Slope=( ) | 0 | 0 | 0 | 0 | 0 | 0 |  | Min. THK=( 30 )mm, Slope=( 1% ) | = A*Ts | = A*Ts |  | M3 | *적용규칙A, 5.4
|  |  |  | 와이어메쉬 | Welded Wire Fabric ¦ ¦ ¦ | A04AQ038-00001 Finishing Work Roof Work Welded Wire Fabric DIA≤6mm | A04AQ038-00001 |  | M2 | Finishing Work | Roof Work | Welded Wire Fabric | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIA≤6mm | 0 | Mesh Size=DIA( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Mesh Size=DIA( #8 )mm x ( 150 )mm x (150 )mm | = A | = A |  | M2
|  |  |  | 단열층 | Roof Insulation ¦ Rigid Extruded Polystyrene Foam Insulation ¦ ¦ | A04AQ088-00004 Finishing Work Roof Work Roof Insulation Rigid Extruded Polystyrene Foam Insulation 100mm≤THK | A04AQ088-00004 |  | M2 | Finishing Work | Roof Work | Roof Insulation | Rigid Extruded Polystyrene Foam Insulation | 0 | 0 | 0 | 0 |  | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 120 )mm | = A | = A |  | M2
|  |  |  | 방수층 | Waterproofing Membrane ¦ EPDM(or Equivalent) ¦ ¦ | A04AQ310-00001 Finishing Work Roof Work Waterproofing Membrane EPDM(or Equivalent) w/ Accessories | A04AQ310-00001 |  | M2 | Finishing Work | Roof Work | Waterproofing Membrane | EPDM(or Equivalent) | 0 | 0 | 0 | 0 | w/ Accessories | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( )mm | = A | = A |  | M2 | *적용규칙A, 5.3
|  |  |  | 보호/보조층 | Gravel for Roof ¦ ¦ ¦ | A04AQ091-00001 Finishing Work Roof Work Gravel for Roof | A04AQ091-00001 |  | M2 | Finishing Work | Roof Work | Gravel for Roof | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mmDIA=( )mm~( )mm or Max DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( )mmDIA=( )mm~( )mm or Max DIA=( )mm | = A | = A |  | M2
H_RF_AR_B06_LW Conc(Slope)_XPS_Memb_Gravel_T150
| □ For Concrete Roof |  |  | ▶ Slope < Waterproofing < Insulation < Protection
2.1.1.2.1 | System Family |  | RF-Q1 | H_RF_AR_B06_Memb_XPS_PE_Protective Conc |  | RF21 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
|  |  |  | 방수층 | Waterproofing Membrane ¦ EPDM(or Equivalent) ¦ ¦ | A04AQ310-00001 Finishing Work Roof Work Waterproofing Membrane EPDM(or Equivalent) w/ Accessories | A04AQ310-00001 |  | M2 | Finishing Work | Roof Work | Waterproofing Membrane | EPDM(or Equivalent) | 0 | 0 | 0 | 0 | w/ Accessories | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( )mm | = A | = A |  | M2 | *적용규칙A, 5.3
|  |  |  | 단열층 | Roof Insulation ¦ Rigid Extruded Polystyrene Foam Insulation ¦ ¦ | A04AQ088-00004 Finishing Work Roof Work Roof Insulation Rigid Extruded Polystyrene Foam Insulation 100mm≤THK | A04AQ088-00004 |  | M2 | Finishing Work | Roof Work | Roof Insulation | Rigid Extruded Polystyrene Foam Insulation | 0 | 0 | 0 | 0 |  | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 120 )mm | = A | = A |  | M2
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A04AQ012-00001 Finishing Work Roof Work PE Sheet (Vapor Barrier) | A04AQ012-00001 |  | M2 | Finishing Work | Roof Work | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm, 2ply | = A | = A |  | M2
|  |  |  | 보호/보조층 | Protective Concrete w/ Steel Trowel Finish ¦ ¦ ¦ | A04AQ089-00001 Finishing Work Roof Work Protective Concrete w/ Steel Trowel Finish | A04AQ089-00001 |  | M3 | Finishing Work | Roof Work | Protective Concrete w/ Steel Trowel Finish | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A*Tp | = A*Tp |  | M3 | *적용규칙A, 5.4
H_RF_AR_B06_Memb_XPS_PE_Protective Conc_SkyPanel Roof_T390
H_RF_AR_B06_Memb_XPS_PE_Protective Conc_SkyPanel Roof_T160
2.1.1.2.2 | System Family |  | RF-Q1 | H_RF_AR_B06_Memb_XPS_PE_Roof Tile |  | RF22 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
|  |  |  | 방수층 | Waterproofing Membrane ¦ EPDM(or Equivalent) ¦ ¦ | A04AQ310-00001 Finishing Work Roof Work Waterproofing Membrane EPDM(or Equivalent) w/ Accessories | A04AQ310-00001 |  | M2 | Finishing Work | Roof Work | Waterproofing Membrane | EPDM(or Equivalent) | 0 | 0 | 0 | 0 | w/ Accessories | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( )mm | = A | = A |  | M2 | *적용규칙A, 5.3
|  |  |  | 단열층 | Roof Insulation ¦ Rigid Extruded Polystyrene Foam Insulation ¦ ¦ | A04AQ088-00002 Finishing Work Roof Work Roof Insulation Rigid Extruded Polystyrene Foam Insulation 50mm≤THK<75mm | A04AQ088-00002 |  | M2 | Finishing Work | Roof Work | Roof Insulation | Rigid Extruded Polystyrene Foam Insulation | 0 | 0 | 0 | 0 |  | 0 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 120 )mm | = A | = A |  | M2
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A04AQ012-00001 Finishing Work Roof Work PE Sheet (Vapor Barrier) | A04AQ012-00001 |  | M2 | Finishing Work | Roof Work | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm, 2ply | = A | = A |  | M2
|  |  |  | 보호/보조층 | Concrete Tile ¦ ¦ ¦ | A04AQ090-00001 Finishing Work Roof Work Concrete Tile w/ Plastic Spacer THK≤50mm | A04AQ090-00001 |  | M2 | Finishing Work | Roof Work | Concrete Tile | 0 | 0 | 0 | 0 | 0 | w/ Plastic Spacer | 0 | THK≤50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( )mm | = A*Tp | = A*Tp |  | M2 | *적용규칙A, 5.4
H_RF_AR_B06_Memb_XPS_PE_Roof Tile_T120
2.1.1.2.3 | System Family |  | RF-Q1 | H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_Geot_Gravel |  | RF23 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
|  |  |  | 보호/보조층 | Roof Screed ¦ Light-Weight Concrete Screed ¦ ¦ | A04AQ086-00001 Finishing Work Roof Work Roof Screed Light-Weight Concrete Screed w/o Welded Wire Fabric 30mm≤Min. THK<50mm | A04AQ086-00001 |  | M3 | Finishing Work | Roof Work | Roof Screed | Light-Weight Concrete Screed | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | 30mm≤Min. THK<50mm | 0 | Min. THK=( )mm, Slope=( ) | 0 | 0 | 0 | 0 | 0 | 0 |  | Min. THK=( 30 )mm, Slope=( 1% ) | = A*Ts | = A*Ts |  | M3 | *적용규칙A, 5.4
|  |  |  | 방수층 | Waterproofing Membrane ¦ EPDM(or Equivalent) ¦ ¦ | A04AQ310-00001 Finishing Work Roof Work Waterproofing Membrane EPDM(or Equivalent) w/ Accessories | A04AQ310-00001 |  | M2 | Finishing Work | Roof Work | Waterproofing Membrane | EPDM(or Equivalent) | 0 | 0 | 0 | 0 | w/ Accessories | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( )mm | = A | = A |  | M2 | *적용규칙A, 5.3
|  |  |  | 단열층 | Roof Insulation ¦ Rigid Extruded Polystyrene Foam Insulation ¦ ¦ | A04AQ088-00002 Finishing Work Roof Work Roof Insulation Rigid Extruded Polystyrene Foam Insulation 50mm≤THK<75mm | A04AQ088-00002 |  | M2 | Finishing Work | Roof Work | Roof Insulation | Rigid Extruded Polystyrene Foam Insulation | 0 | 0 | 0 | 0 |  | 0 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 120 )mm | = A | = A |  | M2
|  |  |  | 보호/보조층 | Geotextile ¦ ¦ ¦ | A04AQ095-00001 Finishing Work Roof Work Geotextile w/ Fixing Accessories | A04AQ095-00001 |  | M2 | Finishing Work | Roof Work | Geotextile | 0 | 0 | 0 | 0 | 0 | w/ Fixing Accessories | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm, 2ply | = A | = A |  | M2
|  |  |  | 보호/보조층 | Gravel for Roof ¦ ¦ ¦ | A04AQ091-00001 Finishing Work Roof Work Gravel for Roof | A04AQ091-00001 |  | M2 | Finishing Work | Roof Work | Gravel for Roof | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mmDIA=( )mm~( )mm or Max DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( )mm | = A*Tp | = A*Tp |  | M2
H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_Geot_Gravel_T120
2.1.1.2.4 | System Family |  | RF-Q1 | H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_Geot_Roof Tile |  | RF24 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
|  |  |  | 보호/보조층 | Roof Screed ¦ Light-Weight Concrete Screed ¦ ¦ | A04AQ086-00001 Finishing Work Roof Work Roof Screed Light-Weight Concrete Screed w/o Welded Wire Fabric 30mm≤Min. THK<50mm | A04AQ086-00001 |  | M3 | Finishing Work | Roof Work | Roof Screed | Light-Weight Concrete Screed | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | 30mm≤Min. THK<50mm | 0 | Min. THK=( )mm, Slope=( ) | 0 | 0 | 0 | 0 | 0 | 0 |  | Min. THK=( 30 )mm, Slope=( 1% ) | = A*Ts | = A*Ts |  | M3 | *적용규칙A, 5.4
|  |  |  | 방수층 | Waterproofing Membrane ¦ EPDM(or Equivalent) ¦ ¦ | A04AQ310-00001 Finishing Work Roof Work Waterproofing Membrane EPDM(or Equivalent) w/ Accessories | A04AQ310-00001 |  | M2 | Finishing Work | Roof Work | Waterproofing Membrane | EPDM(or Equivalent) | 0 | 0 | 0 | 0 | w/ Accessories | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( )mm | = A | = A |  | M2 | *적용규칙A, 5.3
|  |  |  | 단열층 | Roof Insulation ¦ Rigid Extruded Polystyrene Foam Insulation ¦ ¦ | A04AQ088-00002 Finishing Work Roof Work Roof Insulation Rigid Extruded Polystyrene Foam Insulation 50mm≤THK<75mm | A04AQ088-00002 |  | M2 | Finishing Work | Roof Work | Roof Insulation | Rigid Extruded Polystyrene Foam Insulation | 0 | 0 | 0 | 0 |  | 0 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 120 )mm | = A | = A |  | M2
|  |  |  | 보호/보조층 | Geotextile ¦ ¦ ¦ | A04AQ095-00001 Finishing Work Roof Work Geotextile w/ Fixing Accessories | A04AQ095-00001 |  | M2 | Finishing Work | Roof Work | Geotextile | 0 | 0 | 0 | 0 | 0 | w/ Fixing Accessories | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm, 2ply | = A | = A |  | M2
|  |  |  | 보호/보조층 | Concrete Tile ¦ ¦ ¦ | A04AQ090-00001 Finishing Work Roof Work Concrete Tile w/ Plastic Spacer THK≤50mm | A04AQ090-00001 |  | M2 | Finishing Work | Roof Work | Concrete Tile | 0 | 0 | 0 | 0 | 0 | w/ Plastic Spacer | 0 | THK≤50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( )mm | = A*Tp | = A*Tp |  | M2
H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_Geot_Roof Tile_T120
2.1.1.2.5 | System Family |  | RF-Q1 | H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_PE_Roof Tile |  | RF25 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
|  |  |  | 보호/보조층 | Roof Screed ¦ Light-Weight Concrete Screed ¦ ¦ | A04AQ086-00001 Finishing Work Roof Work Roof Screed Light-Weight Concrete Screed w/o Welded Wire Fabric 30mm≤Min. THK<50mm | A04AQ086-00001 |  | M3 | Finishing Work | Roof Work | Roof Screed | Light-Weight Concrete Screed | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | 30mm≤Min. THK<50mm | 0 | Min. THK=( )mm, Slope=( ) | 0 | 0 | 0 | 0 | 0 | 0 |  | Min. THK=( 30 )mm, Slope=( 1% ) | = A*Ts | = A*Ts |  | M3 | *적용규칙A, 5.4
|  |  |  | 방수층 | Waterproofing Membrane ¦ EPDM(or Equivalent) ¦ ¦ | A04AQ310-00001 Finishing Work Roof Work Waterproofing Membrane EPDM(or Equivalent) w/ Accessories | A04AQ310-00001 |  | M2 | Finishing Work | Roof Work | Waterproofing Membrane | EPDM(or Equivalent) | 0 | 0 | 0 | 0 | w/ Accessories | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( )mm | = A | = A |  | M2 | *적용규칙A, 5.3
|  |  |  | 단열층 | Roof Insulation ¦ Rigid Extruded Polystyrene Foam Insulation ¦ ¦ | A04AQ088-00002 Finishing Work Roof Work Roof Insulation Rigid Extruded Polystyrene Foam Insulation 50mm≤THK<75mm | A04AQ088-00002 |  | M2 | Finishing Work | Roof Work | Roof Insulation | Rigid Extruded Polystyrene Foam Insulation | 0 | 0 | 0 | 0 |  | 0 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 120 )mm | = A | = A |  | M2
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A04AQ012-00001 Finishing Work Roof Work PE Sheet (Vapor Barrier) | A04AQ012-00001 |  | M2 | Finishing Work | Roof Work | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm, 2ply | = A | = A |  | M2
|  |  |  | 보호/보조층 | Concrete Tile ¦ ¦ ¦ | A04AQ090-00001 Finishing Work Roof Work Concrete Tile w/ Plastic Spacer THK≤50mm | A04AQ090-00001 |  | M2 | Finishing Work | Roof Work | Concrete Tile | 0 | 0 | 0 | 0 | 0 | w/ Plastic Spacer | 0 | THK≤50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( )mm | = A*Tp | = A*Tp |  | M2
H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_PE_Roof Tile_T120
2.1.1.2.6 | System Family |  | RF-Q1 | H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_PE_Protective Conc |  | RF26 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
|  |  |  | 보호/보조층 | Roof Screed ¦ Light-Weight Concrete Screed ¦ ¦ | A04AQ086-00001 Finishing Work Roof Work Roof Screed Light-Weight Concrete Screed w/o Welded Wire Fabric 30mm≤Min. THK<50mm | A04AQ086-00001 |  | M3 | Finishing Work | Roof Work | Roof Screed | Light-Weight Concrete Screed | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | 30mm≤Min. THK<50mm | 0 | Min. THK=( )mm, Slope=( ) | 0 | 0 | 0 | 0 | 0 | 0 |  | Min. THK=( 30 )mm, Slope=( 1% ) | = A*Ts | = A*Ts |  | M3 | *적용규칙A, 5.4
|  |  |  | 방수층 | Waterproofing Membrane ¦ EPDM(or Equivalent) ¦ ¦ | A04AQ310-00001 Finishing Work Roof Work Waterproofing Membrane EPDM(or Equivalent) w/ Accessories | A04AQ310-00001 |  | M2 | Finishing Work | Roof Work | Waterproofing Membrane | EPDM(or Equivalent) | 0 | 0 | 0 | 0 | w/ Accessories | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( )mm | = A | = A |  | M2 | *적용규칙A, 5.3
|  |  |  | 단열층 | Roof Insulation ¦ Rigid Extruded Polystyrene Foam Insulation ¦ ¦ | A04AQ088-00002 Finishing Work Roof Work Roof Insulation Rigid Extruded Polystyrene Foam Insulation 50mm≤THK<75mm | A04AQ088-00002 |  | M2 | Finishing Work | Roof Work | Roof Insulation | Rigid Extruded Polystyrene Foam Insulation | 0 | 0 | 0 | 0 |  | 0 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 120 )mm | = A | = A |  | M2
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A04AQ012-00001 Finishing Work Roof Work PE Sheet (Vapor Barrier) | A04AQ012-00001 |  | M2 | Finishing Work | Roof Work | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm, 2ply | = A | = A |  | M2
|  |  |  | 보호/보조층 | Protective Concrete w/ Steel Trowel Finish ¦ ¦ ¦ | A04AQ089-00001 Finishing Work Roof Work Protective Concrete w/ Steel Trowel Finish | A04AQ089-00001 |  | M3 | Finishing Work | Roof Work | Protective Concrete w/ Steel Trowel Finish | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( )mm | = A*Tp | = A*Tp |  | M3 | *적용규칙A, 5.4
H_RF_AR_B06_LW Conc(Slope)_Memb_XPS_PE_Protective Conc_T120
| □ For Concrete Roof |  |  | ▶ Waterproofing < Insulation < Protection & Slope
2.1.1.3.1 | System Family |  | RF-Q1 | H_RF_AR_B06_Memb_XPS_PE_Protective Conc(Slope) |  | RF31 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
|  |  |  | 방수층 | Waterproofing Membrane ¦ EPDM(or Equivalent) ¦ ¦ | A04AQ310-00001 Finishing Work Roof Work Waterproofing Membrane EPDM(or Equivalent) w/ Accessories | A04AQ310-00001 |  | M2 | Finishing Work | Roof Work | Waterproofing Membrane | EPDM(or Equivalent) | 0 | 0 | 0 | 0 | w/ Accessories | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EPDM(or Equivalent) THK=( 4 )mm | = A | = A |  | M2 | *적용규칙A, 5.3
|  |  |  | 단열층 | Roof Insulation ¦ Rigid Extruded Polystyrene Foam Insulation ¦ ¦ | A04AQ088-00002 Finishing Work Roof Work Roof Insulation Rigid Extruded Polystyrene Foam Insulation 50mm≤THK<75mm | A04AQ088-00002 |  | M2 | Finishing Work | Roof Work | Roof Insulation | Rigid Extruded Polystyrene Foam Insulation | 0 | 0 | 0 | 0 |  | 0 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | XPS THK=( 120 )mm | = A | = A |  | M2
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A04AQ012-00001 Finishing Work Roof Work PE Sheet (Vapor Barrier) | A04AQ012-00001 |  | M2 | Finishing Work | Roof Work | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Mesh Size=DIA( #8 )mm x ( 150 )mm x (150 )mm | = A | = A |  | M2
|  |  |  | 보호/보조층 | Protective Concrete w/ Steel Trowel Finish ¦ ¦ ¦ | A04AQ089-00001 Finishing Work Roof Work Protective Concrete w/ Steel Trowel Finish | A04AQ089-00001 |  | M3 | Finishing Work | Roof Work | Protective Concrete w/ Steel Trowel Finish | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Protective Concrete w/ Steel Trowel Finish (Slope 1%) | = A*Ts | = A*Ts |  | M3 | *적용규칙A, 5.4
H_RF_AR_B06_Roof Finish
2.1.1.3.2 | System Family |  | RF-Q1 | H_RF_AR_B06_Memb_XPS_PE_LW Conc(Slope) |  | RF32 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
|  |  |  | 방수층 | Waterproofing Membrane ¦ EPDM(or Equivalent) ¦ ¦ | A04AQ310-00001 Finishing Work Roof Work Waterproofing Membrane EPDM(or Equivalent) w/ Accessories | A04AQ310-00001 |  | M2 | Finishing Work | Roof Work | Waterproofing Membrane | EPDM(or Equivalent) | 0 | 0 | 0 | 0 | w/ Accessories | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EPDM(or Equivalent) THK=( 4 )mm | = A | = A |  | M2 | *적용규칙A, 5.3
|  |  |  | 단열층 | Roof Insulation ¦ Rigid Extruded Polystyrene Foam Insulation ¦ ¦ | A04AQ088-00002 Finishing Work Roof Work Roof Insulation Rigid Extruded Polystyrene Foam Insulation 50mm≤THK<75mm | A04AQ088-00002 |  | M2 | Finishing Work | Roof Work | Roof Insulation | Rigid Extruded Polystyrene Foam Insulation | 0 | 0 | 0 | 0 |  | 0 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | XPS THK=( 120 )mm | = A | = A |  | M2
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A04AQ012-00001 Finishing Work Roof Work PE Sheet (Vapor Barrier) | A04AQ012-00001 |  | M2 | Finishing Work | Roof Work | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Mesh Size=DIA( #8 )mm x ( 150 )mm x (150 )mm | = A | = A |  | M2
|  |  |  | 보호/보조층 | Roof Screed ¦ Light-Weight Concrete Screed ¦ ¦ | A04AQ086-00001 Finishing Work Roof Work Roof Screed Light-Weight Concrete Screed w/o Welded Wire Fabric 30mm≤Min. THK<50mm | A04AQ086-00001 |  | M3 | Finishing Work | Roof Work | Roof Screed | Light-Weight Concrete Screed | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | 30mm≤Min. THK<50mm | 0 | Min. THK=( )mm, Slope=( ) | 0 | 0 | 0 | 0 | 0 | 0 |  | Min. THK=( 30 )mm, Slope=( 1% ) | = A*Ts | = A*Ts |  | M3 | *적용규칙A, 5.4
H_RF_AR_B06_Memb_XPS_PE_LW Conc(Slope)_T120
| □ Cladding Roof |  |  | ▶ Sandwitch Panel Roof
2.1.2.1.1 | System Family |  | RF-Q1 | H_RF_AR_B05_Roof Panel Steel Mineral Wool |  | RF61 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
[5 empty] | Sandwich Panel ¦ Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A ¦ ¦ Mineral Wool (Rock Wool) | A05ZZ200-00008 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200-00008 |  | M2 | Cladding Work | - | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A | 0 | 0 | Mineral Wool (Rock Wool) | for Roof | w/ Accessories, Flashing | 0 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 200 )mm | = A | = A |  | M2
H_RF_AR_B05_Roof Panel Steel Mineral Wool_T200
2.1.2.1.2 | System Family |  | RF-Q1 | H_RF_AR_B05_Roof Panel Steel Glass Wool |  | RF62 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
[5 empty] | Sandwich Panel ¦ Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A ¦ ¦ Glass Wool (Fiberglass) | A05ZZ200-00032 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200-00032 |  | M2 | Cladding Work | - | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A | 0 | 0 | Glass Wool (Fiberglass) | for Roof | w/ Accessories, Flashing | 0 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 220 )mm | = A | = A |  | M2
H_RF_AR_B05_Roof Panel Steel Glass Wool_T220
2.1.2.1.3 | System Family |  | RF-Q1 | H_RF_AR_B05_Roof Panel AL Mineral Wool |  | RF63 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
[5 empty] | Sandwich Panel ¦ Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A ¦ ¦ Mineral Wool (Rock Wool) | A05ZZ200-00054 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200-00054 |  | M2 | Cladding Work | - | Sandwich Panel | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A | 0 | 0 | Mineral Wool (Rock Wool) | for Roof | w/ Accessories, Flashing | 0 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( )mm | = A | = A |  | M2
H_RF_AR_B05_Roof Panel AL Mineral Wool_T200
2.1.2.1.4 | System Family |  | RF-Q1 | H_RF_AR_B05_Roof Panel AL Glass Wool |  | RF64 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
[5 empty] | Sandwich Panel ¦ Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A ¦ ¦ Glass Wool (Fiberglass) | A05ZZ200-00078 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200-00078 |  | M2 | Cladding Work | - | Sandwich Panel | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A | 0 | 0 | Glass Wool (Fiberglass) | for Roof | w/ Accessories, Flashing | 0 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( )mm | = A | = A |  | M2
H_RF_AR_B05_Roof Panel AL Glass Wool_T200
| □ Cladding Roof |  |  | ▶ Single Metal Sheet Roof
2.1.2.2.1 | System Family |  | RF-Q1 | H_RF_AR_B05_Roof Single Sheet Steel |  | RF71 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
[5 empty] | Single Metal Sheet ¦ Corrugated Galvanized Steel Sheet ¦ ¦ | A05ZZ199-00006 Cladding Work - Single Metal Sheet Corrugated Galvanized Steel Sheet for Roof w/ Accessories, Flashing | A05ZZ199-00006 |  | M2 | Cladding Work | - | Single Metal Sheet | Corrugated Galvanized Steel Sheet | 0 | 0 | 0 | for Roof | w/ Accessories, Flashing | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.7 )mm | = A | = A | 208.04 | M2
H_RF_AR_B05_Roof Single Sheet Steel_T0.6
2.1.2.2.2 | System Family |  | RF-Q1 | H_RF_AR_B05_Roof Single Sheet AL |  | RF72 | [29 empty] | 산출기준 >> [ 루프 일반 산출 ]
[5 empty] | Single Metal Sheet ¦ Corrugated Aluminum Sheet ¦ ¦ | A05ZZ199-00004 Cladding Work - Single Metal Sheet Corrugated Aluminum Sheet for Roof w/ Accessories, Flashing | A05ZZ199-00004 |  | M2 | Cladding Work | - | Single Metal Sheet | Corrugated Aluminum Sheet | 0 | 0 | 0 | for Roof | w/ Accessories, Flashing | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.7 )mm | = A | = A |  | M2
H_RF_AR_B05_Roof Single Sheet AL_T0.7
2.2 | Gutter (System Family)
| □ Gutter - general |  |  | ▶ Gutter
2.2.1.1.1 | System Family |  | RF-Q1 | H_RF_AR_B07_Gutter_Steel_Eave | [31 empty] | 산출기준 >> [ 루프 일반 산출 ]
[5 empty] | Gutter ¦ Galvanized Steel Eave Gutter w/ Coating ¦ ¦ | A05ZZ204-00001 Cladding Work - Gutter Galvanized Steel Eave Gutter w/ Coating w/ Accessories | A05ZZ204-00001 |  | M | Cladding Work | - | Gutter | Galvanized Steel Eave Gutter w/ Coating | 0 | 0 | 0 | 0 | w/ Accessories | 0 |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.7 )mm | = L/1000 | = L/1000 | 34 | M
H_RF_AR_B07_Gutter_Steel_Eave_W200xH200_T0.7
2.2.1.1.2 | System Family |  | RF-Q1 | H_RF_AR_B07_Gutter_Steel_Valley | [31 empty] | 산출기준 >> [ 루프 일반 산출 ]
[5 empty] | Gutter ¦ Galvanized Steel Valley Gutter w/ Coating ¦ ¦ | A05ZZ204-00002 Cladding Work - Gutter Galvanized Steel Valley Gutter w/ Coating w/ Accessories | A05ZZ204-00002 |  | M | Cladding Work | - | Gutter | Galvanized Steel Valley Gutter w/ Coating | 0 | 0 | 0 | 0 | w/ Accessories | 0 |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.7 )mm | = L/1000 | = L/1000 |  | M
H_RF_AR_B07_Gutter_Steel_Valley_W250xH300xT0.7
2.2.1.1.3 | System Family |  | RF-Q1 | H_RF_AR_B07_Gutter_AL_Eave | [31 empty] | 산출기준 >> [ 루프 일반 산출 ]
[5 empty] | Gutter ¦ Aluminum Eave Gutter w/ Coating ¦ ¦ | A05ZZ204-00003 Cladding Work - Gutter Aluminum Eave Gutter w/ Coating w/ Accessories | A05ZZ204-00003 |  | M | Cladding Work | - | Gutter | Aluminum Eave Gutter w/ Coating | 0 | 0 | 0 | 0 | w/ Accessories | 0 |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.7 )mm | = L/1000 | = L/1000 |  | M
H_RF_AR_B07_Gutter_AL_Eave_W200xH200xT0.7
2.2.1.1.4 | System Family |  | RF-Q1 | H_RF_AR_B07_Gutter_AL_Valley | [31 empty] | 산출기준 >> [ 루프 일반 산출 ]
[5 empty] | Gutter ¦ Aluminum Valley Gutter w/ Coating ¦ ¦ | A05ZZ204-00004 Cladding Work - Gutter Aluminum Valley Gutter w/ Coating w/ Accessories | A05ZZ204-00004 |  | M | Cladding Work | - | Gutter | Aluminum Valley Gutter w/ Coating | 0 | 0 | 0 | 0 | w/ Accessories | 0 |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.7 )mm | = L/1000 | = L/1000 |  | M
H_RF_AR_B07_Gutter_AL_Valley_W200xH200xT0.7
2.3 | Fascia (System Family)
| □ Fascia - general |  |  | ▶ Fascia
2.3.1.1.1 | System Family |  | RF-Q1 | H_RF_AR_B07_Fascia-Flat | [31 empty] | 산출기준 >> [ 루프 일반 산출 ]
[5 empty] | Flashing along Roof Corner ¦ Galvanized Steel Flashing ¦ ¦ | A04AQ097-00001 Finishing Work Roof Work Flashing along Roof Corner Galvanized Steel Flashing w/ Fixing Accessories, Sealant | A04AQ097-00001 |  | M2 | Finishing Work | Roof Work | Flashing along Roof Corner | Galvanized Steel Flashing | 0 | 0 | 0 | 0 | w/ Fixing Accessories, Sealant | 0 |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = L/1000 | = L/1000 |  | M2
H_RF_AR_B07_Fascia-Flashing
2.4 | Roof Soffit (System Family)
| □ Soffit - general |  |  | ▶ Soffit
2.4.1.1.1 | System Family |  | RF-Q1 | H_RF_AR_B07_Soffit | [31 empty] | 산출기준 >> [ 루프 일반 산출 ]
H_RF_AR_B07_Soffit
2.5 | Sloped Glazing (System Family)
| □ Sloped Glazing - general |  |  | ▶ Sloped Glazing
2.5.1.1.1 | System Family |  | RF-Q1 | H_RF_AR_B07_Sloped Glazing | [31 empty] | 산출기준 >> [ 루프 일반 산출 ]
H_RF_AR_B07_Sloped Glazing

## 3.Walls_Ext
[Family List] - Walls_Exterior |  |  |  |  | 표준구성도로 가기
NO | Family Category | Building Tag | Q'ty Cal Type Tag | Standard Type | Family Type Name | Work Master Code /w Description | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Description | 입찰_ 물량산출식 | 실행_ 물량산출식 | Quantity |  | Remark (물량관련)
3 | Walls (WA)
3.1 | Basic Wall - Ext (System Family)
| □ Exterior Wall |  |  | ▶ Gypsum + Concrete (*Concrete Wall은 별도 Family로 분리)
3.1.1.1.1 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_1L Gypsum_Mineral Wool |  | EW11 | [23 empty] | *Concrete+Gypsum 외벽의 내부Gypsum | [5 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드+단열층 | Plasterboard Dry Liner System ¦ ¦ ¦ Mineral Wool (Rock Wool) | A04AS176-00002 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Mineral Wool (Rock Wool) for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS176-00002 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Plasterboard Dry Liner System | 0 | 0 | 0 | Mineral Wool (Rock Wool) | for Wall To External Side | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Mineral Wool (Rock Wool) / THK=(135)mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T10
3.1.1.1.2 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_1L Gypsum_Glass Wool |  | EW12 | [23 empty] | *Concrete+Gypsum 외벽의 내부Gypsum | [5 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드+단열층 | Plasterboard Dry Liner System ¦ ¦ ¦ Glass Wool (Fiberglass) | A04AS176-00005 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Glass Wool (Fiberglass) for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS176-00005 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Plasterboard Dry Liner System | 0 | 0 | 0 | Glass Wool (Fiberglass) | for Wall To External Side | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Glass Wool (Fiberglass) / THK=(135)mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T10
3.1.1.1.3 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_2L Gypsum_Glass Wool |  | EW12A | [23 empty] | *Concrete+Gypsum 외벽의 내부Gypsum | [5 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드층 | Gypsumboard Partition Wall (Fixed Type) ¦ Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side ¦ ¦ w/o Insulation | A04AS177-00004 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177-00004 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Fixed Type) | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side | 0 | 0 | w/o Insulation | 0 | Including Supporting Frame(Stud) & Accessories | 0 | 1-Layer Gypsumboard THK=9.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Thk9.5 2 Ply Gypsum-Interior Side | = A | = A |  | M2
|  |  |  | 단열층 | Insulation ¦ Glass Wool (Fiberglass) ¦ ¦ | A04AL076-00008 Finishing Work Masonry Work Insulation Glass Wool (Fiberglass) Minimum Density of 50 kg/m3 100mm≤THK | A04AL076-00008 |  | M2 | Finishing Work | Masonry Work | Insulation | Glass Wool (Fiberglass) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Glass Wool (Fiberglass) / THK=(135)mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T10
3.1.1.1.4 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_1L Gypsum_Rigid Ins |  | EW13 | [23 empty] | *Concrete+Gypsum 외벽의 내부Gypsum | [5 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드+단열층 | Plasterboard Dry Liner System ¦ ¦ ¦ Rigid Insulation | A04AS176-00008 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Rigid Insulation for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS176-00008 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Plasterboard Dry Liner System | 0 | 0 | 0 | Rigid Insulation | for Wall To External Side | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Rigid Insulation / THK=(135)mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T10
| □ Exterior Wall |  |  | ▶ Gypsum + Masonry
[Gyp + Block]
3.1.1.2.1 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_1L Gypsum_T200 Block_Mineral Wool |  | EW21 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드+단열층 | Plasterboard Dry Liner System ¦ ¦ ¦ Mineral Wool (Rock Wool) | A04AS176-00002 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Mineral Wool (Rock Wool) for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS176-00002 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Plasterboard Dry Liner System | 0 | 0 | 0 | Mineral Wool (Rock Wool) | for Wall To External Side | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material Mineral Wool (Rock Wool) / THK=(135)mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 조적층 | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00002 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 100mm<THK≤200mm | A04AL069-00002 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 100mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 200 )mm | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Wall Exterior Finish THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Wall Exterior Finish | = A * PR | = A * PR |  | M2
3.1.1.2.2 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_1L Gypsum_T200 Block_Glass Wool |  | EW22 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드+단열층 | Plasterboard Dry Liner System ¦ ¦ ¦ Glass Wool (Fiberglass) | A04AS176-00005 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Glass Wool (Fiberglass) for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS176-00005 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Plasterboard Dry Liner System | 0 | 0 | 0 | Glass Wool (Fiberglass) | for Wall To External Side | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material Glass Wool (Fiberglass) / THK=(135)mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 조적층 | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00002 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 100mm<THK≤200mm | A04AL069-00002 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 100mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 200 )mm | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Wall Exterior Finish THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Wall Exterior Finish | = A * PR | = A * PR |  | M2
3.1.1.2.3 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_1L Gypsum_T200 Block_Rigid Ins |  | EW23 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드+단열층 | Plasterboard Dry Liner System ¦ ¦ ¦ Rigid Insulation | A04AS176-00008 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Rigid Insulation for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS176-00008 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Plasterboard Dry Liner System | 0 | 0 | 0 | Rigid Insulation | for Wall To External Side | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material Rigid Insulation / THK=(135)mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 조적층 | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00002 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 100mm<THK≤200mm | A04AL069-00002 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 100mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 200 )mm | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * PR | = A * PR |  | M2
| □ Exterior Wall |  |  | ▶ Gypsum + Masonry
[Gyp + Brick]
3.1.1.2.4 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Brick_Mineral Wool |  | EW24 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드+단열층 | Plasterboard Dry Liner System ¦ ¦ ¦ Mineral Wool (Rock Wool) | A04AS176-00002 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Mineral Wool (Rock Wool) for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS176-00002 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Plasterboard Dry Liner System | 0 | 0 | 0 | Mineral Wool (Rock Wool) | for Wall To External Side | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material Mineral Wool (Rock Wool) / THK=(135)mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00002 Finishing Work Masonry Work Concrete Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL073-00002 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material 1.0B, THK=( 190 )mm | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * PR | = A * PR |  | M2
3.1.1.2.5 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Brick_Glass Wool |  | EW25 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드+단열층 | Plasterboard Dry Liner System ¦ ¦ ¦ Glass Wool (Fiberglass) | A04AS176-00005 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Glass Wool (Fiberglass) for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS176-00005 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Plasterboard Dry Liner System | 0 | 0 | 0 | Glass Wool (Fiberglass) | for Wall To External Side | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material Glass Wool (Fiberglass) / THK=(135)mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00002 Finishing Work Masonry Work Concrete Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL073-00002 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material 1.0B, THK=( 190 )mm | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * PR | = A * PR |  | M2
3.1.1.2.6 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Brick_Rigid Ins |  | EW26 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드+단열층 | Plasterboard Dry Liner System ¦ ¦ ¦ Rigid Insulation | A04AS176-00008 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Rigid Insulation for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS176-00008 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Plasterboard Dry Liner System | 0 | 0 | 0 | Rigid Insulation | for Wall To External Side | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material Rigid Insulation / THK=(135)mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00002 Finishing Work Masonry Work Concrete Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL073-00002 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material 1.0B, THK=( 190 )mm | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * PR | = A * PR |  | M2
| □ Exterior Wall |  |  | ▶ Gypsum + Masonry
[Gyp + Clay Brick]
3.1.1.2.7 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Clay Brick_Mineral Wool |  | EW27 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드+단열층 | Plasterboard Dry Liner System ¦ ¦ ¦ Mineral Wool (Rock Wool) | A04AS176-00002 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Mineral Wool (Rock Wool) for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS176-00002 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Plasterboard Dry Liner System | 0 | 0 | 0 | Mineral Wool (Rock Wool) | for Wall To External Side | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material Mineral Wool (Rock Wool) / THK=(135)mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 조적층 | Burnt Clay Brick ¦ ¦ ¦ | A04AL074-00002 Finishing Work Masonry Work Burnt Clay Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL074-00002 |  | M2 | Finishing Work | Masonry Work | Burnt Clay Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material 1.0B, THK=( 190 )mm | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * PR | = A * PR |  | M2
3.1.1.2.8 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Clay Brick_Glass Wool |  | EW28 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드+단열층 | Plasterboard Dry Liner System ¦ ¦ ¦ Glass Wool (Fiberglass) | A04AS176-00005 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Glass Wool (Fiberglass) for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS176-00005 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Plasterboard Dry Liner System | 0 | 0 | 0 | Glass Wool (Fiberglass) | for Wall To External Side | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material Glass Wool (Fiberglass) / THK=(135)mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 조적층 | Burnt Clay Brick ¦ ¦ ¦ | A04AL074-00002 Finishing Work Masonry Work Burnt Clay Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL074-00002 |  | M2 | Finishing Work | Masonry Work | Burnt Clay Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material 1.0B, THK=( 190 )mm | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * PR | = A * PR |  | M2
3.1.1.2.9 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_1L Gypsum_1B Clay Brick_Rigid Ins |  | EW29 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드+단열층 | Plasterboard Dry Liner System ¦ ¦ ¦ Rigid Insulation | A04AS176-00008 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Rigid Insulation for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS176-00008 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Plasterboard Dry Liner System | 0 | 0 | 0 | Rigid Insulation | for Wall To External Side | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material Rigid Insulation / THK=(135)mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 조적층 | Burnt Clay Brick ¦ ¦ ¦ | A04AL074-00002 Finishing Work Masonry Work Burnt Clay Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL074-00002 |  | M2 | Finishing Work | Masonry Work | Burnt Clay Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material 1.0B, THK=( 190 )mm | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * PR | = A * PR |  | M2
| □ Exterior Wall |  |  | ▶ Masonry + Masonry
[Block + Block]
3.1.1.3.1 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_T100 Block_T200 Block_Mineral Wool |  | EW31 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00001 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 50mm<THK≤100mm | A04AL069-00001 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 50mm<THK≤100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 단열층 | Insulation ¦ Mineral Wool (Rock Wool) ¦ ¦ | A04AL076-00004 Finishing Work Masonry Work Insulation Mineral Wool (Rock Wool) Minimum Density of 50 kg/m3 100mm≤THK | A04AL076-00004 |  | M2 | Finishing Work | Masonry Work | Insulation | Mineral Wool (Rock Wool) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
|  |  |  | 조적층 | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00002 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 100mm<THK≤200mm | A04AL069-00002 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 100mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 200 )mm | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * PR | = A * PR |  | M2
3.1.1.3.2 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_T100 Block_T200 Block_Galss Wool |  | EW32 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00001 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 50mm<THK≤100mm | A04AL069-00001 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 50mm<THK≤100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 단열층 | Insulation ¦ Glass Wool (Fiberglass) ¦ ¦ | A04AL076-00008 Finishing Work Masonry Work Insulation Glass Wool (Fiberglass) Minimum Density of 50 kg/m3 100mm≤THK | A04AL076-00008 |  | M2 | Finishing Work | Masonry Work | Insulation | Glass Wool (Fiberglass) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
|  |  |  | 조적층 | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00002 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 100mm<THK≤200mm | A04AL069-00002 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 100mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 200 )mm | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * PR | = A * PR |  | M2
3.1.1.3.3 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_T100 Block_T200 Block_EPS or XPS |  | EW33 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00001 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 50mm<THK≤100mm | A04AL069-00001 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 50mm<THK≤100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 단열층 | Insulation ¦ Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) ¦ ¦ | A04AL076-00012 Finishing Work Masonry Work Insulation Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) Minimum Density of 25 kg/m3 100mm≤THK | A04AL076-00012 |  | M2 | Finishing Work | Masonry Work | Insulation | Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) | 0 | 0 | 0 | 0 | Minimum Density of 25 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
|  |  |  | 조적층 | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00002 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 100mm<THK≤200mm | A04AL069-00002 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 100mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 200 )mm | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * PR | = A * PR |  | M2
| □ Exterior Wall |  |  | ▶ Masonry + Masonry
[Brick + Brick]
3.1.1.3.4 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Brick_Mineral Wool |  | EW34 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00001 Finishing Work Masonry Work Concrete Brick [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. THK≤90mm | A04AL073-00001 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | THK≤90mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 단열층 | Insulation ¦ Mineral Wool (Rock Wool) ¦ ¦ | A04AL076-00004 Finishing Work Masonry Work Insulation Mineral Wool (Rock Wool) Minimum Density of 50 kg/m3 100mm≤THK | A04AL076-00004 |  | M2 | Finishing Work | Masonry Work | Insulation | Mineral Wool (Rock Wool) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00002 Finishing Work Masonry Work Concrete Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL073-00002 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * PR | = A * PR |  | M2
3.1.1.3.5 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Brick_Glass Wool |  | EW35 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00001 Finishing Work Masonry Work Concrete Brick [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. THK≤90mm | A04AL073-00001 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | THK≤90mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 단열층 | Insulation ¦ Glass Wool (Fiberglass) ¦ ¦ | A04AL076-00008 Finishing Work Masonry Work Insulation Glass Wool (Fiberglass) Minimum Density of 50 kg/m3 100mm≤THK | A04AL076-00008 |  | M2 | Finishing Work | Masonry Work | Insulation | Glass Wool (Fiberglass) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00002 Finishing Work Masonry Work Concrete Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL073-00002 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * PR | = A * PR |  | M2
3.1.1.3.6 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Brick_EPS or XPS |  | EW36 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00001 Finishing Work Masonry Work Concrete Brick [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. THK≤90mm | A04AL073-00001 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | THK≤90mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 단열층 | Insulation ¦ Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) ¦ ¦ | A04AL076-00012 Finishing Work Masonry Work Insulation Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) Minimum Density of 25 kg/m3 100mm≤THK | A04AL076-00012 |  | M2 | Finishing Work | Masonry Work | Insulation | Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) | 0 | 0 | 0 | 0 | Minimum Density of 25 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00002 Finishing Work Masonry Work Concrete Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL073-00002 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * PR | = A * PR |  | M2
| □ Exterior Wall |  |  | ▶ Masonry + Masonry
[Clay Brick + Clay Brick]
3.1.1.3.7 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Clay Brick_Mineral Wool |  | EW37 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00001 Finishing Work Masonry Work Concrete Brick [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. THK≤90mm | A04AL073-00001 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | THK≤90mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 단열층 | Insulation ¦ Mineral Wool (Rock Wool) ¦ ¦ | A04AL076-00004 Finishing Work Masonry Work Insulation Mineral Wool (Rock Wool) Minimum Density of 50 kg/m3 100mm≤THK | A04AL076-00004 |  | M2 | Finishing Work | Masonry Work | Insulation | Mineral Wool (Rock Wool) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
|  |  |  | 조적층 | Burnt Clay Brick ¦ ¦ ¦ | A04AL074-00002 Finishing Work Masonry Work Burnt Clay Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL074-00002 |  | M2 | Finishing Work | Masonry Work | Burnt Clay Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Wall Exterior Finish THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Wall Exterior Finish | = A * PR | = A * PR |  | M2
3.1.1.3.8 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Clay Brick_Glass Wool |  | EW38 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00001 Finishing Work Masonry Work Concrete Brick [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. THK≤90mm | A04AL073-00001 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | THK≤90mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 단열층 | Insulation ¦ Glass Wool (Fiberglass) ¦ ¦ | A04AL076-00008 Finishing Work Masonry Work Insulation Glass Wool (Fiberglass) Minimum Density of 50 kg/m3 100mm≤THK | A04AL076-00008 |  | M2 | Finishing Work | Masonry Work | Insulation | Glass Wool (Fiberglass) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
|  |  |  | 조적층 | Burnt Clay Brick ¦ ¦ ¦ | A04AL074-00002 Finishing Work Masonry Work Burnt Clay Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL074-00002 |  | M2 | Finishing Work | Masonry Work | Burnt Clay Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Wall Exterior Finish THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Wall Exterior Finish | = A * PR | = A * PR |  | M2
3.1.1.3.9 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_0.5B Brick_1B Clay Brick_EPS or XPS |  | EW39 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00001 Finishing Work Masonry Work Concrete Brick [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. THK≤90mm | A04AL073-00001 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | THK≤90mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 단열층 | Insulation ¦ Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) ¦ ¦ | A04AL076-00012 Finishing Work Masonry Work Insulation Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) Minimum Density of 25 kg/m3 100mm≤THK | A04AL076-00012 |  | M2 | Finishing Work | Masonry Work | Insulation | Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) | 0 | 0 | 0 | 0 | Minimum Density of 25 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
|  |  |  | 조적층 | Burnt Clay Brick ¦ ¦ ¦ | A04AL074-00002 Finishing Work Masonry Work Burnt Clay Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL074-00002 |  | M2 | Finishing Work | Masonry Work | Burnt Clay Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Wall Exterior Finish THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Wall Exterior Finish | = A * PR | = A * PR |  | M2
| □ Exterior Wall |  |  | ▶ Masonry + Concrete (*Concrete Wall은 별도 Family로 분리)
[Block]
3.1.1.4.1 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_T100 Block_Mineral Wool |  | EW41 | [23 empty] | *Concrete+Masonry 외벽의 내부Masonry | [5 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00001 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 50mm<THK≤100mm | A04AL069-00001 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 50mm<THK≤100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 단열층 | Insulation ¦ Mineral Wool (Rock Wool) ¦ ¦ | A04AL076-00004 Finishing Work Masonry Work Insulation Mineral Wool (Rock Wool) Minimum Density of 50 kg/m3 100mm≤THK | A04AL076-00004 |  | M2 | Finishing Work | Masonry Work | Insulation | Mineral Wool (Rock Wool) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
3.1.1.4.2 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_T100 Block_Galss Wool |  | EW42 | [23 empty] | *Concrete+Masonry 외벽의 내부Masonry | [5 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00001 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 50mm<THK≤100mm | A04AL069-00001 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 50mm<THK≤100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 단열층 | Insulation ¦ Glass Wool (Fiberglass) ¦ ¦ | A04AL076-00008 Finishing Work Masonry Work Insulation Glass Wool (Fiberglass) Minimum Density of 50 kg/m3 100mm≤THK | A04AL076-00008 |  | M2 | Finishing Work | Masonry Work | Insulation | Glass Wool (Fiberglass) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
3.1.1.4.3 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_T100 Block_EPS or XPS |  | EW43 | [23 empty] | *Concrete+Masonry 외벽의 내부Masonry | [5 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00001 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 50mm<THK≤100mm | A04AL069-00001 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 50mm<THK≤100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 단열층 | Insulation ¦ Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) ¦ ¦ | A04AL076-00012 Finishing Work Masonry Work Insulation Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) Minimum Density of 25 kg/m3 100mm≤THK | A04AL076-00012 |  | M2 | Finishing Work | Masonry Work | Insulation | Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) | 0 | 0 | 0 | 0 | Minimum Density of 25 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
| □ Exterior Wall |  |  | ▶ Masonry + Concrete (*Concrete Wall은 별도 Family로 분리)
[Brick]
3.1.1.4.4 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_0.5B Brick_Mineral Wool |  | EW44 | [23 empty] | *Concrete+Masonry 외벽의 내부Masonry | [5 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00001 Finishing Work Masonry Work Concrete Brick [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. THK≤90mm | A04AL073-00001 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | THK≤90mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 90 )mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 단열층 | Insulation ¦ Mineral Wool (Rock Wool) ¦ ¦ | A04AL076-00004 Finishing Work Masonry Work Insulation Mineral Wool (Rock Wool) Minimum Density of 50 kg/m3 100mm≤THK | A04AL076-00004 |  | M2 | Finishing Work | Masonry Work | Insulation | Mineral Wool (Rock Wool) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
3.1.1.4.5 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_0.5B Brick_Galss Wool |  | EW45 | [23 empty] | *Concrete+Masonry 외벽의 내부Masonry | [5 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00001 Finishing Work Masonry Work Concrete Brick [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. THK≤90mm | A04AL073-00001 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | THK≤90mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 90 )mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 단열층 | Insulation ¦ Glass Wool (Fiberglass) ¦ ¦ | A04AL076-00008 Finishing Work Masonry Work Insulation Glass Wool (Fiberglass) Minimum Density of 50 kg/m3 100mm≤THK | A04AL076-00008 |  | M2 | Finishing Work | Masonry Work | Insulation | Glass Wool (Fiberglass) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
3.1.1.4.6 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_0.5B Brick_EPS or XPS |  | EW46 | [23 empty] | *Concrete+Masonry 외벽의 내부Masonry | [5 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00001 Finishing Work Masonry Work Concrete Brick [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. THK≤90mm | A04AL073-00001 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | THK≤90mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 90 )mm | = A | = A |  | M2
|  |  |  | 공기층 | Air Space T20
|  |  |  | 단열층 | Insulation ¦ Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) ¦ ¦ | A04AL076-00012 Finishing Work Masonry Work Insulation Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) Minimum Density of 25 kg/m3 100mm≤THK | A04AL076-00012 |  | M2 | Finishing Work | Masonry Work | Insulation | Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) | 0 | 0 | 0 | 0 | Minimum Density of 25 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 100 )mm | = A | = A |  | M2
| □ Exterior Wall |  |  | ▶ Single Wall
[Only RC]
3.1.1.5.1 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_RC |  | EW51 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 구조층 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM C150 Type I or Type IA F'c (Cylinder Strength) = 28MPa | = V | = V |  | M3
|  |  |  | 공기층 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 400MPa<Fy≤470MPa ¦ | A03AD037-00002 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 400MPa<Fy≤470MPa | A03AD037-00002 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 400MPa<Fy≤470MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V*RE | = V*RE |  | TON
|  |  |  | 단열층 | Form Work (1 time in use) ¦ Flat Form ¦ ¦ | A03AD036-00001 Concrete Work Substructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD036-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (1 time in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A*2 | = A*2 |  | M2
3.1.1.5.2 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_RC_Exposed |  | EW51 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 구조층 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM C150 Type I or Type IA F'c (Cylinder Strength) = 28MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 400MPa<Fy≤470MPa ¦ | A03AD037-00002 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 400MPa<Fy≤470MPa | A03AD037-00002 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 400MPa<Fy≤470MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V*RE | = V*RE |  | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (1 time in use) ¦ Flat Form ¦ ¦ | A03AD036-00001 Concrete Work Substructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD036-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (1 time in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | *HGEN : 노출콘크리트용 Form 단가 적용 필요 (해당 자재 W/M 에 없음) | = A*2 | = A*2 |  | M2
3.1.1.5.3 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_RC_Parapet_Exposed |  | EW51 | [23 empty] | Parapet | [5 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 구조층 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM C150 Type I or Type IA F'c (Cylinder Strength) = 24MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 400MPa<Fy≤470MPa ¦ | A03AD037-00002 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 400MPa<Fy≤470MPa | A03AD037-00002 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 400MPa<Fy≤470MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V*RE | = V*RE |  | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (1 time in use) ¦ Flat Form ¦ ¦ | A03AF036-00001 Concrete Work Superstructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF036-00001 | (a) | M2 | Concrete Work | Superstructure Work | Form Work (1 time in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | *HGEN : 노출콘크리트용 Form 단가 적용 필요 (해당 자재 W/M 에 없음) | = A*2 | = A*2 |  | M2
| □ Exterior Wall |  |  | ▶ Single Wall
[Combined RC]
3.1.1.5.1 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_RC |  | EW51A | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 구조층 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = V | = V | 25.994 | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AF037-00003 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AF037-00003 |  | TON | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = V*RE | = V*RE | 3.12 | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (1 time in use) ¦ Flat Form ¦ ¦ | A03AF036-00001 Concrete Work Superstructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF036-00001 |  | M2 | Concrete Work | Superstructure Work | Form Work (1 time in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A*2 | = A*2 | 259.936 | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * PR | Manual 물량으로 산출 | 0 | M2
H_WA_AR_B02_Ext Wall_RC_T250_W1
3.1.1.5.4 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_RC_Emulsion Paint |  | EW51A | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 구조층 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = V | = V | 25.994 | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AF037-00003 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AF037-00003 |  | TON | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = V*RE | = V*RE | 3.12 | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (1 time in use) ¦ Flat Form ¦ ¦ | A03AF036-00001 Concrete Work Superstructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF036-00001 |  | M2 | Concrete Work | Superstructure Work | Form Work (1 time in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A*2 | = A*2 | 259.936 | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * PR | = A*2 | 0 | M2
H_WA_AR_B02_Ext Wall_RC_T150
H_WA_AR_B02_Ext Wall_RC_T180
| System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_RC_Insulation_Gypsum |  | EW51A | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 구조층 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = V*RE | = V*RE |  | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (1 time in use) ¦ Flat Form ¦ ¦ | A03AD036-00001 Concrete Work Substructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD036-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (1 time in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A*2 | = A*2 |  | M2
|  |  |  | insulation | Insulation ¦ Glass Wool (Fiberglass) ¦ ¦ | A04AL076-00008 Finishing Work Masonry Work Insulation Glass Wool (Fiberglass) Minimum Density of 50 kg/m3 100mm≤THK | A04AL076-00008 |  | M2 | Finishing Work | Masonry Work | Insulation | Glass Wool (Fiberglass) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  |  | 마감층 | Gypsumboard Partition Wall (Fixed Type) ¦ Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side ¦ ¦ w/o Insulation | A04AS177-00004 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177-00004 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Fixed Type) | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side | 0 | 0 | w/o Insulation | 0 | Including Supporting Frame(Stud) & Accessories | 0 | 1-Layer Gypsumboard THK=9.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
H_WA_AR_B02_Ext Wall_RC T250_W1
H_WA_AR_B02_Ext Wall_RC T250_W1_PH
3.1.1.5.5 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_RC_UG_Bitumen |  | EW51B | [23 empty] | UG Wall | [5 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 구조층 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = V | = V | 12.96 | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = V*RE | = V*RE | 1.558 | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A*2 | = A*2 | 64.8 | M2
|  |  |  | 보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Exterior Protection | = A | = A*2 | 64.8 | M2
H_WA_AR_B02_Ext Wall_RC_T400_W1A
H_WA_AR_B02_Ext Wall_RC_T400_W2A
3.1.1.5.6 | System Family |  | WA-Q1 | H_WA_AR_B08_Ext Wall_RC_UG_Pit_Bitumen_Epoxy |  | EW51C | [23 empty] | UG Wall, Pit Wall | [5 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 구조층 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 400MPa<Fy≤470MPa ¦ | A03AD037-00002 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 400MPa<Fy≤470MPa | A03AD037-00002 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 400MPa<Fy≤470MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = V*RE | = V*RE |  | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A*2 | = A*2 |  | M2
|  |  |  | 보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Exterior Protection | = A | = A |  | M2
|  |  |  | 마감층 | Internal Wall Painting ¦ Epoxy Paint ¦ ¦ | A04AM078-00005 Finishing Work Painting Work Internal Wall Painting Epoxy Paint | A04AM078-00005 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Epoxy Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Interior Paint | = A | = A |  | M2
Template
Template
Template
Template
| System Family |  | WA-Q1 | H_WA_AR_B08_Ext Wall_RC_UG_Pit_Bitumen_Insulation |  | EW51C | [23 empty] | UG Wall, Pit Wall | [5 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 구조층 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = V*RE | = V*RE |  | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A*2 | = A*2 |  | M2
|  |  |  | 보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Exterior Protection | = A | = A |  | M2
|  |  |  | 마감층 | Insulation under Ground Floor ¦ Extruded Polystyrene Insulation Board ¦ ¦ | A03AD047-00004 Concrete Work Substructure Work Insulation under Ground Floor Extruded Polystyrene Insulation Board 100mm≤THK | A03AD047-00004 |  | M2 | Concrete Work | Substructure Work | Insulation under Ground Floor | Extruded Polystyrene Insulation Board | 0 | 0 | 0 | 0 |  | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Interior Paint | = A | = A |  | M2
Template
Template
Template
Template
3.1.1.5.7 | System Family |  | WA-Q1 | H_WA_AR_B08_Ext Wall_RC_UG_Trench_Bitumen_Epoxy |  | EW51C | [23 empty] | UG Wall, Trench Wall | [5 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 구조층 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 400MPa<Fy≤470MPa ¦ | A03AD037-00002 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 400MPa<Fy≤470MPa | A03AD037-00002 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 400MPa<Fy≤470MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = V*RE | = V*RE |  | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A*2 | = A*2 |  | M2
|  |  |  | 보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Exterior Protection | = A | = A |  | M2
|  |  |  | 마감층 | Internal Wall Painting ¦ Epoxy Paint ¦ ¦ | A04AM078-00005 Finishing Work Painting Work Internal Wall Painting Epoxy Paint | A04AM078-00005 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Epoxy Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Interior Paint | = A | = A |  | M2
| □ Exterior Wall |  |  | ▶ Single Wall
[Combined Masonry]
3.1.1.5.8 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_Block_Emulsion |  | EW52 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00002 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 100mm<THK≤200mm | A04AL069-00002 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 100mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=( 200 )mm | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Wall Exterior Finish THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Wall Exterior Finish | = A * PR | = A * PR |  | M2
3.1.1.5.9 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_Brick_Emulsion |  | EW53 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00002 Finishing Work Masonry Work Concrete Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL073-00002 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material 1.0B | = A | = A |  | M2
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Wall Exterior Finish THK=(18)mm | = A | = A |  | M2
|  |  |  | 마감층 | External Wall Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Wall Exterior Finish | = A * PR | = A * PR |  | M2
H_WA_AR_B02_Ext Wall_Brick_Emulsion_1.0B
3.1.1.5.10 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_Clay Brick |  | EW54 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
[5 empty] | Burnt Clay Brick ¦ ¦ ¦ | A04AL074-00002 Finishing Work Masonry Work Burnt Clay Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL074-00002 |  | M2 | Finishing Work | Masonry Work | Burnt Clay Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material 1.0B | = A | = A |  | M2
H_WA_AR_B02_Ext Wall_Clay Brick_1.0B
3.1.1.5.11 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_AAC Block |  | EW55 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
[5 empty] | AAC (Autoclaved Aerated Concrete) Block ¦ ¦ ¦ | A04AL070-00002 Finishing Work Masonry Work AAC (Autoclaved Aerated Concrete) Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 100mm<THK≤200mm | A04AL070-00002 |  | M2 | Finishing Work | Masonry Work | AAC (Autoclaved Aerated Concrete) Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 100mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Base Material THK=(200)mm | = A | = A |  | M2
H_WA_AR_B02_Ext Wall_AAC Block_T200
| □ Exterior Wall |  |  | ▶ Single Wall
[Fence]
3.1.1.5.12 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_Chain Link Fence (Fixed Type) |  | EW55 | [29 empty] | 산출기준 >> 매칭실패
[5 empty] | Chain Link Fence (Fixed Type) ¦ Self-Standing Type w/ Steel Frame ¦ ¦ | A04AV212-00001 Finishing Work Misc. Work Chain Link Fence (Fixed Type) Self-Standing Type w/ Steel Frame w/ Fixing Accessories 1500mm≤H<2000mm | A04AV212-00001 |  | M | Finishing Work | Misc. Work | Chain Link Fence (Fixed Type) | Self-Standing Type w/ Steel Frame | 0 | 0 | 0 | 0 | w/ Fixing Accessories | 0 | 1500mm≤H<2000mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | H=1200 | = A | = A |  | M
H_WA_AR_B02_Ext Wall_Chain Link Fence (Fixed Type)_H1200
| □ Exterior Wall |  |  | ▶ Cladding Wall
3.1.1.6.1 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool |  | EW61A | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
[5 empty] | Sandwich Panel ¦ Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A ¦ ¦ Mineral Wool (Rock Wool) | A05ZZ200-00003 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200-00003 |  | M2 | Cladding Work | - | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A | 0 | 0 | Mineral Wool (Rock Wool) | for Wall | w/ Accessories, Flashing | 0 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 120 )mm | = A | = A |  | M2
H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_T120
3.1.1.6.2 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Glass Wool |  | EW61B | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
[5 empty] | Sandwich Panel ¦ Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A ¦ ¦ Glass Wool (Fiberglass) | A05ZZ200-00027 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200-00027 |  | M2 | Cladding Work | - | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A | 0 | 0 | Glass Wool (Fiberglass) | for Wall | w/ Accessories, Flashing | 0 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 135 )mm | = A | = A |  | M2
H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Glass Wool_T135
3.1.1.6.3 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_Single Sheet_Steel |  | EW62 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
[5 empty] | Single Metal Sheet ¦ Corrugated Galvanized Steel Sheet ¦ ¦ | A05ZZ199-00005 Cladding Work - Single Metal Sheet Corrugated Galvanized Steel Sheet for Wall w/ Accessories, Flashing | A05ZZ199-00005 |  | M2 | Cladding Work | - | Single Metal Sheet | Corrugated Galvanized Steel Sheet | 0 | 0 | 0 | for Wall | w/ Accessories, Flashing | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.7 )mm | = A | = A |  | M2
H_WA_AR_B02_Ext Wall_Single Sheet_Steel_T0.7
3.1.1.6.4 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_Sandwich Panel_AL_Mineral Wool |  | EW65A | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
[5 empty] | Sandwich Panel ¦ Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A ¦ ¦ Mineral Wool (Rock Wool) | A05ZZ200-00051 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200-00051 |  | M2 | Cladding Work | - | Sandwich Panel | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A | 0 | 0 | Mineral Wool (Rock Wool) | for Wall | w/ Accessories, Flashing | 0 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 120 )mm | = A | = A |  | M2
H_WA_AR_B02_Ext Wall_Sandwich Panel_AL_Mineral Wool_T120
3.1.1.6.5 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_Sandwich Panel_AL_Glass Wool |  | EW65B | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
[5 empty] | Sandwich Panel ¦ Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A ¦ ¦ Glass Wool (Fiberglass) | A05ZZ200-00075 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200-00075 |  | M2 | Cladding Work | - | Sandwich Panel | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A | 0 | 0 | Glass Wool (Fiberglass) | for Wall | w/ Accessories, Flashing | 0 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 120 )mm | = A | = A |  | M2
H_WA_AR_B02_Ext Wall_Sandwich Panel_AL_Glass Wool_T120
| □ Exterior Wall |  |  | ▶ Cladding + Gypsum/Masonry
3.1.1.7.1 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_1L Gypsum |  | EW91 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드층 | Gypsumboard Partition Wall (Fixed Type) ¦ Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side ¦ ¦ w/o Insulation | A04AS177-00002 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177-00002 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Fixed Type) | Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side | 0 | 0 | w/o Insulation | 0 | Including Supporting Frame(Stud) & Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  |  | 클래딩층 | Sandwich Panel ¦ Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A ¦ ¦ Mineral Wool (Rock Wool) | A05ZZ200-00003 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200-00003 |  | M2 | Cladding Work | - | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A | 0 | 0 | Mineral Wool (Rock Wool) | for Wall | w/ Accessories, Flashing | 0 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 120 )mm | = A | = A |  | M2
H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_1L Gypsum_T120
3.1.1.7.2 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_T100 Block |  | EW92 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00001 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 50mm<THK≤100mm | A04AL069-00001 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 50mm<THK≤100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 100 )mm | = A | = A |  | M2
|  |  |  | 클래딩층 | Sandwich Panel ¦ Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A ¦ ¦ Mineral Wool (Rock Wool) | A05ZZ200-00003 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200-00003 |  | M2 | Cladding Work | - | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A | 0 | 0 | Mineral Wool (Rock Wool) | for Wall | w/ Accessories, Flashing | 0 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 120 )mm | = A | = A |  | M2
H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_T100 Block_T120
3.1.1.7.3 | System Family |  | WA-Q1 | H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_1.0B Brick |  | EW93 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00002 Finishing Work Masonry Work Concrete Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL073-00002 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0B | = A | = A |  | M2
|  |  |  | 클래딩층 | Sandwich Panel ¦ Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A ¦ ¦ Mineral Wool (Rock Wool) | A05ZZ200-00003 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200-00003 |  | M2 | Cladding Work | - | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A | 0 | 0 | Mineral Wool (Rock Wool) | for Wall | w/ Accessories, Flashing | 0 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 120 )mm | = A | = A |  | M2
H_WA_AR_B02_Ext Wall_Sandwich Panel_Steel_Mineral Wool_1.0B Brick_T120
| □ Exterior Wall - F2 Group |  |  | ▶ Exterior Wall Finish Only - F2
[Protection Board]
3.1.2.1.1 | System Family |  | WA-Q1 | H_WA_AR_B07_Ext Wall_Protection Board |  | EWF1 | [23 empty] | Protection Only | [5 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Exterior Protection | = A | = A |  | M2
|  |  |  | 방수층 | Sheet Membrane ¦ Adhesive Rubber Sheet or Bitumen Polyethylene Laminated Waterproofing Membrane ¦ ¦ | A03AH059-00001 Concrete Work Concrete Protective Coating (U/G) Sheet Membrane Adhesive Rubber Sheet or Bitumen Polyethylene Laminated Waterproofing Membrane | A03AH059-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Sheet Membrane | Adhesive Rubber Sheet or Bitumen Polyethylene Laminated Waterproofing Membrane | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 4 )mm | = A | = A |  | M2
|  |  |  | 보드층 | Memebrane Protection Board ¦ Bitumen Impregnated Fiberboard ¦ ¦ | A03AH060-00001 Concrete Work Concrete Protective Coating (U/G) Memebrane Protection Board Bitumen Impregnated Fiberboard | A03AH060-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Memebrane Protection Board | Bitumen Impregnated Fiberboard | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 6 )mm | = A | = A |  | M2
H_WA_AR_B07_Ext Wall_Protection Board_T6
[Plaster]
3.1.2.1.2 | System Family |  | WA-Q1 | H_WA_AR_B07_Ext Wall_Int Plaster |  | EWF1 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보호층 | Plastering ¦ ¦ ¦ | A04AT198-00002 Finishing Work Plastering Work Plastering for Internal Masonry Wall | A04AT198-00002 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for Internal Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
H_WA_AR_B07_Ext Wall_Int Plaster_T12

## 3.Walls_Int
[Family List] - Walls_Interior |  |  |  |  | 표준구성도로 가기
NO | Family Category | Building Tag | Q'ty Cal Type Tag | Standard Type | Family Type Name | Work Master Code /w Description | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Description | 입찰_ 물량산출식 | 실행_ 물량산출식 | Quantity |  | Remark (물량관련)
3 | Walls (WA)
3.2 | Basic Wall - Int (System Family)
| □ Interior Wall |  |  | ▶ Gypsum
[1L Both Gypsum]
3.2.1.1.1 | System Family |  | WA-Q1 | H_WA_AR_B02_Int Wall_1L Both Gypsum_Mineral Wool |  | IW11 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드+단열층 | Gypsumboard Partition Wall (Fixed Type) ¦ Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides ¦ ¦ Mineral Wool (Rock Wool) | A04AS177-00008 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177-00008 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Fixed Type) | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides | 0 | 0 | Mineral Wool (Rock Wool) | 0 | Including Supporting Frame(Stud) & Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 110 )mm | = A | = A |  | M2
H_WA_AR_B02_Int Wall_1L Both Gypsum_Mineral Wool_T110_0Hr
3.2.1.1.2 | System Family |  | WA-Q1 | H_WA_AR_B02_Int Wall_1L Both Gypsum_Glass Wool |  | IW12 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드+단열층 | Gypsumboard Partition Wall (Fixed Type) ¦ Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides ¦ ¦ Glass Wool (Fiberglass) | A04AS177-00012 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS177-00012 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Fixed Type) | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides | 0 | 0 | Glass Wool (Fiberglass) | 0 | Including Supporting Frame(Stud) & Accessories | 0 | 1-Layer Gypsumboard THK=16mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 100 )mm | = A | = A |  | M2
H_WA_AR_B02_Int Wall_1L Both Gypsum_Glass Wool_T100_0Hr
3.2.1.1.3 | System Family |  | WA-Q1 | H_WA_AR_B02_Int Wall_1L Both Gypsum |  | IW13 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드층 | Gypsumboard Partition Wall (Fixed Type) ¦ Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides ¦ ¦ w/o Insulation | A04AS177-00015 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS177-00015 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Fixed Type) | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides | 0 | 0 | w/o Insulation | 0 | Including Supporting Frame(Stud) & Accessories | 0 | 1-Layer Gypsumboard THK=16mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
H_WA_AR_B02_Int Wall_1L Both Gypsum_0Hr
| □ Interior Wall |  |  | ▶ Gypsum
[2L Both Gypsum]
3.2.1.1.4 | System Family |  | WA-Q1 | H_WA_AR_B02_Int Wall_2L Both Gypsum_Mineral Wool |  | IW14 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드+단열층 | Gypsumboard Partition Wall (Fixed Type) ¦ Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides ¦ ¦ Mineral Wool (Rock Wool) | A04AS177-00032 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177-00032 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Fixed Type) | Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides | 0 | 0 | Mineral Wool (Rock Wool) | 0 | Including Supporting Frame(Stud) & Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 100 )mm | = A | = A |  | M2
H_WA_AR_B02_Int Wall_2L Both Gypsum_Mineral Wool_T100_2Hr
3.2.1.1.5 | System Family |  | WA-Q1 | H_WA_AR_B02_Int Wall_2L Both Gypsum_Glass Wool |  | IW15 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드+단열층 | Gypsumboard Partition Wall (Fixed Type) ¦ Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides ¦ ¦ Glass Wool (Fiberglass) | A04AS177-00019 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177-00019 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Fixed Type) | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides | 0 | 0 | Glass Wool (Fiberglass) | 0 | Including Supporting Frame(Stud) & Accessories | 0 | 1-Layer Gypsumboard THK=9.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=(60 )mm | = A | = A |  | M2
H_WA_AR_B02_Int Wall_2L Both Gypsum_Insulation_T128
3.2.1.1.6 | System Family |  | WA-Q1 | H_WA_AR_B02_Int Wall_2L Both Gypsum |  | IW16 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 보드층 | Gypsumboard Partition Wall (Fixed Type) ¦ Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides ¦ ¦ Glass Wool (Fiberglass) | A04AS177-00019 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177-00019 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Fixed Type) | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides | 0 | 0 | Glass Wool (Fiberglass) | 0 | Including Supporting Frame(Stud) & Accessories | 0 | 1-Layer Gypsumboard THK=9.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
H_WA_AR_B02_Int Wall_2L Gypsum_Glass Wool_T128
| □ Interior Wall |  |  | ▶ Masonry
3.2.1.2.1 | System Family |  | WA-Q1 | H_WA_AR_B02_Int Wall_Block |  | IW21 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
[5 empty] | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00002 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 100mm<THK≤200mm | A04AL069-00002 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 100mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 200 )mm | = A | = A |  | M2
[5 empty] | H_WA_AR_B02_Int Wall_Block_T150 | A04AT198-00002 Finishing Work Plastering Work Plastering for Internal Masonry Wall | A04AT198-00002 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for Internal Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A*2 | = A |  | M2
3.2.1.2.2 | System Family |  | WA-Q1 | H_WA_AR_B02_Int Wall_Brick |  | IW22 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
[5 empty] | Concrete Brick ¦ ¦ ¦ | A04AL073-00002 Finishing Work Masonry Work Concrete Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL073-00002 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0 B | = A | = A |  | M2
H_WA_AR_B02_Int Wall_Brick_1.0B
| □ Interior Wall |  |  | ▶ Concrete
3.2.1.3.1 | System Family |  | WA-Q1 | H_WA_AR_B02_Int Wall_RC |  | IW31 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 구조층 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | f'c=28MPa, W/CONSTRUCTION JOINT | = V | = V | 6.66 | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AF037-00003 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AF037-00003 |  | TON | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | - KS D 3504 SD400 OR ASTM A615 GRADE 60 | = V*RE | = V*RE | 0.8 | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (1 time in use) ¦ Flat Form ¦ ¦ | A03AF036-00001 Concrete Work Superstructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF036-00001 |  | M2 | Concrete Work | Superstructure Work | Form Work (1 time in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A*2 | = A*2 | 66.6 | M2
H_WA_AR_B02_Int Wall_RC_T250_W2
| □ Interior Wall |  |  | ▶ Masonry + Gypsum
[Masonry + 1L One Side Gypsum]
3.2.1.4.1 | System Family |  | WA-Q1 | H_WA_AR_B02_Int Wall_Block T200_1L Gypsum_Mineral Wool |  | IW41 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00002 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 100mm<THK≤200mm | A04AL069-00002 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 100mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 200 )mm | = A | = A |  | M2
|  |  |  | 단열층 | Insulation ¦ Mineral Wool (Rock Wool) ¦ ¦ | A04AL076-00002 Finishing Work Masonry Work Insulation Mineral Wool (Rock Wool) Minimum Density of 50 kg/m3 50mm≤THK<75mm | A04AL076-00002 |  | M2 | Finishing Work | Masonry Work | Insulation | Mineral Wool (Rock Wool) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 50 )mm | = A | = A |  | M2
|  |  |  | 보드층 | Gypsumboard Partition Wall (Fixed Type) ¦ Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side ¦ ¦ w/o Insulation | A04AS177-00002 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177-00002 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Fixed Type) | Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side | 0 | 0 | w/o Insulation | 0 | Including Supporting Frame(Stud) & Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
H_WA_AR_B02_Int Wall_Block T200_1L Gypsum_Mineral Wool_T50
3.2.1.4.2 | System Family |  | WA-Q1 | H_WA_AR_B02_Int Wall_Brick 1B_1L Gypsum_Mineral Wool |  | IW42 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00002 Finishing Work Masonry Work Concrete Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL073-00002 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0 B | = A | = A |  | M2
|  |  |  | 단열층 | Insulation ¦ Mineral Wool (Rock Wool) ¦ ¦ | A04AL076-00002 Finishing Work Masonry Work Insulation Mineral Wool (Rock Wool) Minimum Density of 50 kg/m3 50mm≤THK<75mm | A04AL076-00002 |  | M2 | Finishing Work | Masonry Work | Insulation | Mineral Wool (Rock Wool) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 50 )mm | = A | = A |  | M2
|  |  |  | 보드층 | Gypsumboard Partition Wall (Fixed Type) ¦ Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side ¦ ¦ w/o Insulation | A04AS177-00002 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177-00002 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Fixed Type) | Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side | 0 | 0 | w/o Insulation | 0 | Including Supporting Frame(Stud) & Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
H_WA_AR_B02_Int Wall_Brick 1B_1L Gypsum_Mineral Wool_T50
| □ Interior Wall |  |  | ▶ Masonry + Gypsum
[Masonry + 2L One Side Gypsum]
3.2.1.4.3 | System Family |  | WA-Q1 | H_WA_AR_B02_Int Wall_Block T200_2L Gypsum_Mineral Wool |  | IW46 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Reinforced Concrete Block ¦ ¦ ¦ | A04AL069-00002 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 100mm<THK≤200mm | A04AL069-00002 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 100mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 200 )mm | = A | = A |  | M2
|  |  |  | 단열층 | Insulation ¦ Mineral Wool (Rock Wool) ¦ ¦ | A04AL076-00002 Finishing Work Masonry Work Insulation Mineral Wool (Rock Wool) Minimum Density of 50 kg/m3 50mm≤THK<75mm | A04AL076-00002 |  | M2 | Finishing Work | Masonry Work | Insulation | Mineral Wool (Rock Wool) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 50 )mm | = A | = A |  | M2
|  |  |  | 보드층 | Gypsumboard Partition Wall (Fixed Type) ¦ Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side ¦ ¦ w/o Insulation | A04AS177-00005 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177-00005 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Fixed Type) | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side | 0 | 0 | w/o Insulation | 0 | Including Supporting Frame(Stud) & Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
H_WA_AR_B02_Int Wall_Block T200_2L Gypsum_Mineral Wool_T50
3.2.1.4.4 | System Family |  | WA-Q1 | H_WA_AR_B02_Int Wall_Brick 1B_2L Gypsum_Mineral Wool |  | IW47 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Concrete Brick ¦ ¦ ¦ | A04AL073-00002 Finishing Work Masonry Work Concrete Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL073-00002 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0 B | = A | = A |  | M2
|  |  |  | 단열층 | Insulation ¦ Mineral Wool (Rock Wool) ¦ ¦ | A04AL076-00002 Finishing Work Masonry Work Insulation Mineral Wool (Rock Wool) Minimum Density of 50 kg/m3 50mm≤THK<75mm | A04AL076-00002 |  | M2 | Finishing Work | Masonry Work | Insulation | Mineral Wool (Rock Wool) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 50 )mm | = A | = A |  | M2
|  |  |  | 보드층 | Gypsumboard Partition Wall (Fixed Type) ¦ Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side ¦ ¦ w/o Insulation | A04AS177-00005 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177-00005 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Fixed Type) | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side | 0 | 0 | w/o Insulation | 0 | Including Supporting Frame(Stud) & Accessories | 0 | 1-Layer Gypsumboard THK=12.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
H_WA_AR_B02_Int Wall_Brick 1B_2L Gypsum_Mineral Wool_T50
| □ Interior Wall |  |  | ▶ Glass wall
| System Family |  | WA-Q1 | H_WA_AR_B02_Int Wall_Glass wall |  | IW46 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 조적층 | Glass Door w/ SST Frame (UoM: M2) ¦ ¦ ¦ | A04AR118-00001 Finishing Work Door & Window Work Glass Door w/ SST Frame (UoM: M2) w/ Hardware & Accessories | A04AR118-00001 |  | M2 | Finishing Work | Door & Window Work | Glass Door w/ SST Frame (UoM: M2) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 200 )mm | = A | = A |  | M2
H_WA_AR_B02_Interior Curtain Wall
| □ Interior Wall - F2 |  |  | ▶ Interior Wall Finish Only
[Plaster]
3.2.2.1.1 | System Family |  | WA-Q1 | H_WA_AR_B07_Int Wall_Plaster |  | IWF1 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 플라스터층 | Plastering ¦ ¦ ¦ | A04AT198-00002 Finishing Work Plastering Work Plastering for Internal Masonry Wall | A04AT198-00002 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for Internal Masonry Wall |  | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=(12)mm | = A | = A |  | M2
H_WA_AR_B07_Int Wall_Plaster_T12
| □ Interior Wall - F2 |  |  | ▶ Interior Wall Finish Only
[Ceramic Tile]
3.2.2.1.2 | System Family |  | WA-Q1 | H_WA_AR_B07_Int Wall_Ceramic Tile |  | IWF2 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 마감층 | Wall Tile ¦ Unglazed Ceramic Tile ¦ ¦ | A04AN082-00001 Finishing Work Tile Work Wall Tile Unglazed Ceramic Tile w/ Mortar Bond Coat or Adhesive | A04AN082-00001 |  | M2 | Finishing Work | Tile Work | Wall Tile | Unglazed Ceramic Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | = A | = A |  | M2
H_WA_AR_B07_Int Wall_Ceramic Tile_150x150xT6
3.2.2.1.3 | System Family |  | WA-Q1 | H_WA_AR_B07_Int Wall_Ceramic Tile_L Waterproof |  | IWF2A | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 방수층 | Liquid Waterproofing ¦ ¦ ¦ | A04AP085-00001 Finishing Work Waterproofing Work Liquid Waterproofing for Internal Floor Area Min. 2 Coats | A04AP085-00001 |  | M2 | Finishing Work | Waterproofing Work | Liquid Waterproofing | 0 | 0 | 0 | 0 | for Internal Floor Area | Min. 2 Coats | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  |  | 마감층 | Wall Tile ¦ Unglazed Ceramic Tile ¦ ¦ | A04AN082-00001 Finishing Work Tile Work Wall Tile Unglazed Ceramic Tile w/ Mortar Bond Coat or Adhesive | A04AN082-00001 |  | M2 | Finishing Work | Tile Work | Wall Tile | Unglazed Ceramic Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | = A | = A |  | M2
H_WA_AR_B07_Int Wall_Ceramic Tile_L Waterproof_150x150xT6
3.2.2.1.4 | System Family |  | WA-Q1 | H_WA_AR_B07_Int Wall_Ceramic Tile_Membrane |  | IWF2B | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 방수층 | Waterproofing Membrane ¦ ¦ ¦ | A04AP310-00001 Finishing Work Waterproofing Work Waterproofing Membrane for Internal Area | A04AP310-00001 |  | M2 | Finishing Work | Waterproofing Work | Waterproofing Membrane | 0 | 0 | 0 | 0 | for Internal Area |  | 0 |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( )mm | = A | = A |  | M2
|  |  |  | 마감층 | Wall Tile ¦ Unglazed Ceramic Tile ¦ ¦ | A04AN082-00001 Finishing Work Tile Work Wall Tile Unglazed Ceramic Tile w/ Mortar Bond Coat or Adhesive | A04AN082-00001 |  | M2 | Finishing Work | Tile Work | Wall Tile | Unglazed Ceramic Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | = A | = A |  | M2
H_WA_AR_B07_Int Wall_Ceramic Tile_Membrane_150x150xT6
| □ Interior Wall - F2 |  |  | ▶ Interior Wall Finish Only
[Acide Resistant Tile]
3.2.2.1.5 | System Family |  | WA-Q1 | H_WA_AR_B07_Int Wall_Acid R Tile |  | IWF3 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 마감층 | Wall Tile ¦ Acid/Alkaline Resistant Tile ¦ ¦ | A04AN082-00003 Finishing Work Tile Work Wall Tile Acid/Alkaline Resistant Tile w/ Mortar Bond Coat or Adhesive | A04AN082-00003 |  | M2 | Finishing Work | Tile Work | Wall Tile | Acid/Alkaline Resistant Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | = A | = A |  | M2
H_WA_AR_B07_Int Wall_Acid R Tile_150x150xT6
3.2.2.1.6 | System Family |  | WA-Q1 | H_WA_AR_B07_Int Wall_Acid R Tile_L Waterproof |  | IWF3A | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 방수층 | Liquid Waterproofing ¦ ¦ ¦ | A04AP085-00001 Finishing Work Waterproofing Work Liquid Waterproofing for Internal Floor Area Min. 2 Coats | A04AP085-00001 |  | M2 | Finishing Work | Waterproofing Work | Liquid Waterproofing | 0 | 0 | 0 | 0 | for Internal Floor Area | Min. 2 Coats | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  |  | 마감층 | Wall Tile ¦ Acid/Alkaline Resistant Tile ¦ ¦ | A04AN082-00003 Finishing Work Tile Work Wall Tile Acid/Alkaline Resistant Tile w/ Mortar Bond Coat or Adhesive | A04AN082-00003 |  | M2 | Finishing Work | Tile Work | Wall Tile | Acid/Alkaline Resistant Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | = A | = A |  | M2
H_WA_AR_B07_Int Wall_Acid R Tile_L Waterproof_150x150xT6
| □ Interior Wall - F2 |  |  | ▶ Interior Wall Finish Only
[Etc. Tile]
3.2.2.1.7 | System Family |  | WA-Q1 | H_WA_AR_B07_Int Wall_Granite Tile |  | IWF4 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 마감층 | Wall Tile ¦ Granite Tile ¦ ¦ | A04AN082-00004 Finishing Work Tile Work Wall Tile Granite Tile w/ Wet Method (Mortar Bond Coat or Adhesive) or Dry Method (Steel or SST Frame, Angle, Bolt, etc.) | A04AN082-00004 |  | M2 | Finishing Work | Tile Work | Wall Tile | Granite Tile | 0 | 0 | 0 | 0 | w/ Wet Method (Mortar Bond Coat or Adhesive) or Dry Method (Steel or SST Frame, Angle, Bolt, etc.) | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | = A | = A |  | M2
H_WA_AR_B07_Int Wall_Granite Tile_300x300xT9
3.2.2.1.8 | System Family |  | WA-Q1 | H_WA_AR_B07_Int Wall_Marble Tile |  | IWF5 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 마감층 | Wall Tile ¦ Marble Tile ¦ ¦ | A04AN082-00005 Finishing Work Tile Work Wall Tile Marble Tile w/ Wet Method (Mortar Bond Coat or Adhesive) or Dry Method (Steel or SST Frame, Angle, Bolt, etc.) | A04AN082-00005 |  | M2 | Finishing Work | Tile Work | Wall Tile | Marble Tile | 0 | 0 | 0 | 0 | w/ Wet Method (Mortar Bond Coat or Adhesive) or Dry Method (Steel or SST Frame, Angle, Bolt, etc.) | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | = A | = A |  | M2
H_WA_AR_B07_Int Wall_Marble Tile_300x300xT9
| □ Interior Wall - F2 |  |  | ▶ Interior Wall Finish Only
[Insulation + Gypsum]
| System Family |  | WA-Q1 | H_WA_AR_B07_Int Wall_Insulation gypsum |  | IWF4 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 마감층 | Insulation ¦ Glass Wool (Fiberglass) ¦ ¦ | A04AL076-00008 Finishing Work Masonry Work Insulation Glass Wool (Fiberglass) Minimum Density of 50 kg/m3 100mm≤THK | A04AL076-00008 |  | M2 | Finishing Work | Masonry Work | Insulation | Glass Wool (Fiberglass) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | = A | = A |  | M2
|  |  |  | 마감층 | Gypsumboard Partition Wall (Fixed Type) ¦ Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side ¦ ¦ w/o Insulation | A04AS177-00004 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177-00004 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Fixed Type) | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side | 0 | 0 | w/o Insulation | 0 | Including Supporting Frame(Stud) & Accessories | 0 | 1-Layer Gypsumboard THK=9.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | = A | = A |  | M2
H_WA_AR_B02_Int Wall_2L Gypsum_Insulationl_T154
H_WA_AR_B02_Int Wall_2L Gypsum_Insulationl_T119
| □ Interior Wall - F2 |  |  | ▶ Interior Wall Finish Only
[ETC]
3.2.2.1.7 | System Family |  | WA-Q1 | H_WA_AR_B07_Int Wall_Insulation |  | IWF4 | [29 empty] | 산출기준 >> [ 벽체 일반 산출 ]
|  |  |  | 마감층 | Insulation ¦ Glass Wool (Fiberglass) ¦ ¦ | A04AL076-00008 Finishing Work Masonry Work Insulation Glass Wool (Fiberglass) Minimum Density of 50 kg/m3 100mm≤THK | A04AL076-00008 |  | M2 | Finishing Work | Masonry Work | Insulation | Glass Wool (Fiberglass) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=W( )mm x L( )mm x THK( )mm | = A | = A |  | M2
H_WA_AR_B02_Int Wall_Insulation_T140
H_WA_AR_B02_Int Wall_Insulation_T135
3.3 | Curtain Wall (System Family)
| □ Curtain Wall - normal |  |  | ▶ Curtain Wall
3.3.1.1.1 | System Family |  | WA-Q1 | H_WA_AR_B02_Exterior Curtain Wall | [31 empty] | 산출기준 >> [ 벽체 일반 산출 ]
H_WA_AR_B02_Exterior Curtain Wall
3.3.1.1.2 | System Family |  | WA-Q1 | H_WA_AR_B02_Pavillion Curtain Wall | [31 empty] | 산출기준 >> [ 벽체 일반 산출 ]
H_WA_AR_B02_Pavillion Curtain Wall
3.3.1.1.3 | System Family |  | WA-Q1 | H_WA_AR_B02_Storefront Curtain Wall | [31 empty] | 산출기준 >> [ 벽체 일반 산출 ]
H_WA_AR_B02_Storefront Curtain Wall
3.4 | Stacked Wall (System Family)
| □ Stacked Wall - normal |  |  | ▶ Stacked Wall
3.4.1.1.1 | System Family |  | WA-Q1 | H_WA_AR_B02_Exterior-Brick Over CMU w Metal Stud | [31 empty] | 산출기준 >> [ 벽체 일반 산출 ]
H_WA_AR_B02_Exterior-Brick Over CMU w Metal Stud

## 4.St_Fdn
[Family List] - Structural Foundations |  |  |  |  | 표준구성도로 가기
NO | Family Category | Building Tag | Q'ty Cal Type Tag | Standard Type | Family Type Name | Work Master Code /w Description | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Description | 입찰_ 물량산출식 | 실행_ 물량산출식 | Quantity |  | Remark (물량관련)
4 | Structural Foundations ( SF )
4.1 | Foundation Slab (System Family)
| □ Slab |  |  | ▶ Mat Foundation for Building | [32 empty] | 169
4.1.1.1.1 | System Family |  | SF-Q1 | H_SF_AR_S18_MAT_Bitumen | [31 empty] | 산출기준 >> [ Mat, Mass ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 28MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) or KS D 3504 SD400 | = V*RE | = V*RE |  | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * (T/1000) | = (P/1000) * (T/1000) |  | M2
|  |  |  | 측면+하부면 보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * (H2/1000) + A | = (P/1000) * (H2/1000) + A |  | M2
|  |  |  | Insulation | Insulation under Ground Floor ¦ Extruded Polystyrene Insulation Board ¦ ¦ | A03AD047-00004 Concrete Work Substructure Work Insulation under Ground Floor Extruded Polystyrene Insulation Board 100mm≤THK | A03AD047-00004 |  | M2 | Concrete Work | Substructure Work | Insulation under Ground Floor | Extruded Polystyrene Insulation Board | 0 | 0 | 0 | 0 |  | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * (H2/1000) |  |  | M2
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001-00012 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Above GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Above GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001-00013 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Below GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Below GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back |  | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp |  | M3 | * 가상모델링
|  |  |  | 바닥보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =A | =A |  | M2 | * 가상모델링
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =(A+(P/1000)*D1+(4*D1*D1) )*C1 | _by "▶ Lean Concrete" |  | M3 | *적용규칙A, 7.1
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | Insulation | Insulation under Ground Floor ¦ Extruded Polystyrene Insulation Board ¦ ¦ | A03AD047-00004 Concrete Work Substructure Work Insulation under Ground Floor Extruded Polystyrene Insulation Board 100mm≤THK | A03AD047-00004 |  | M2 | Concrete Work | Substructure Work | Insulation under Ground Floor | Extruded Polystyrene Insulation Board | 0 | 0 | 0 | 0 |  | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
H_SF_AR_S18_MAT_Bitumen_T800_MF1
H_SF_AR_S18_MAT_Bitumen_T650_MF2
| □ Slab |  |  | ▶ Mat Foundation for Equipment
4.1.1.2.1 | System Family |  | SF-Q1 | H_SF_AR_B01_EQ FDN_Bitumen | [25 empty] | Mat Foundation for Building/Shelter | [5 empty] | 산출기준 >> [ Mat, Mass ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 28MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) or KS D 3504 SD400 | = V*RE | = V*RE |  | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * (T/1000) | = (P/1000) * (T/1000) |  | M2
|  |  |  | 측면+하부면 보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * (H2/1000) + A | = (P/1000) * (H2/1000) + A |  | M2
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001-00012 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Above GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Above GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001-00013 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Below GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Below GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back |  | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp |  | M3 | * 가상모델링
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =(A+(P/1000)*D1+(4*D1*D1) )*C1 | _by "▶ Lean Concrete" |  | M3 | *적용규칙A, 7.1
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
H_SF_AR_B01_EQ FDN_Bitumen_Mat_T600
| □ Slab |  |  | ▶ Mat Foundation for Equipment (Pad only) |  | <- Equipment pad 용 항목 추가
4.1.1.2.1 | System Family |  | SF-Q1 | H_SF_AR_B01_EQ FDN_Bitumen | [25 empty] | Mat Foundation for Building/Shelter | [5 empty] | 산출기준 >> [ Mat, Mass ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 28MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) or KS D 3504 SD400 | = V*RE | = V*RE |  | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * (T/1000) | = (P/1000) * (T/1000) |  | M2
H_SF_AR_B01_EQ FDN_Bitumen_Mat_T800_EF1
H_SF_AR_B01_EQ FDN_Bitumen_Mat_T200_EF2
H_SF_AR_B01_EQ FDN_Bitumen_Mat_T200_EF3
H_SF_AR_B01_EQ FDN_Bitumen_Mat_T700
4.1.1.2.2 | System Family |  | SF-Q1 | H_SF_AR_B01_EQ FDN_CEP Can_Bitumen | [25 empty] | Mat Foundation for Equipment | [5 empty] | 산출기준 >> [ Mat, Mass ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V*RE | = V*RE |  | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * (T/1000) | = (P/1000) * (T/1000) |  | M2
|  |  |  | 측면+하부면 보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * (H2/1000) + A | = (P/1000) * (H2/1000) + A |  | M2
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001-00012 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Above GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Above GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001-00013 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Below GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Below GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back |  | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp |  | M3 | * 가상모델링
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =(A+(P/1000)*D1+(4*D1*D1) )*C1 | _by "▶ Lean Concrete" |  | M3 | *적용규칙A, 7.1
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
H_SF_AR_B01_EQ FDN_CEP Can_Bitumen_Mat T1000
| □ Slab |  |  | ▶ Mass Concrete (Temperature Control) for Equipment
4.1.1.3.1 | System Family |  | SF-Q1 | H_SF_AR_B01_Mass_Bitumen | [25 empty] | Mass Concrete, Temperature Control | [5 empty] | 산출기준 >> [ Mat, Mass ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AE032-00022 Concrete Work Mass Concrete Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032-00022 |  | M3 | Concrete Work | Mass Concrete Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 30MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 400MPa<Fy≤470MPa ¦ | A03AE037-00002 Concrete Work Mass Concrete Work Rebar Work Deformed Bar (Non-Coat.) 400MPa<Fy≤470MPa | A03AE037-00002 |  | TON | Concrete Work | Mass Concrete Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 400MPa<Fy≤470MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V*RE | = V*RE |  | TON | RE=0.12
|  |  |  | 거푸집 | System Form ¦ Heavy Duty Forms, Metal Framed Playwood forms ¦ ¦ | A03AE054-00001 Concrete Work Mass Concrete Work System Form Heavy Duty Forms, Metal Framed Playwood forms Including Form Tie, All Accessories, Sealing of Form Tie Hole, Separator & Anchor Box out, Chamfer for Exposed Edge, Opening & Sleeve, Shoring, Scaffording, Safety Measures and Shop Drawing | A03AE054-00001 |  | M3 | Concrete Work | Mass Concrete Work | System Form | Heavy Duty Forms, Metal Framed Playwood forms | 0 | 0 | 0 | 0 | Including Form Tie, All Accessories, Sealing of Form Tie Hole, Separator & Anchor Box out, Chamfer for Exposed Edge, Opening & Sleeve, Shoring, Scaffording, Safety Measures and Shop Drawing | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * (T/1000) | = (P/1000) * (T/1000) |  | M3
|  |  |  | 측면+상부+하부 보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * (H2/1000) + 2*A | = (P/1000) * (H2/1000) + 2*A |  | M2
|  |  |  | 수화열 모니터링 | Concrete Temperature Monitoring ¦ ¦ ¦ | A03AE052-00001 Concrete Work Mass Concrete Work Concrete Temperature Monitoring Including Themo Coupler, Monitoring & Record Acc. To Approved MS | A03AE052-00001 |  | SET | Concrete Work | Mass Concrete Work | Concrete Temperature Monitoring | 0 | 0 | 0 | 0 | 0 | Including Themo Coupler, Monitoring & Record Acc. To Approved MS | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = Q | = Q |  | SET
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001-00012 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Above GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Above GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001-00013 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Below GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Below GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back |  | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp |  | M3 | * 가상모델링
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =(A+(P/1000)*D1+(4*D1*D1) )*C1 | _by "▶ Lean Concrete" |  | M3 | *적용규칙A, 7.1
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
H_SF_AR_B01_Mass_Bitumen_STG Mat_T2500
| □ Slab |  |  | ▶ SOG Slab
4.1.1.4.1 | System Family |  | SF-Q2 | H_SF_AR_S17_SOG | [25 empty] | SOG | [5 empty] | 산출기준 >> [ SOG ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V + (TCS * P/1000) | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = (V + (TCS * P/1000) )*RE | = V*RE |  | TON | RE=0.09
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * (T/1000) |  |  | M2 | *Slab 옆면만 산출
|  |  |  | 줄눈 | Isolation Joint (Separation Joint) ¦ ¦ ¦ | A03AD044-00001 Concrete Work Substructure Work Isolation Joint (Separation Joint) w/ Flexible Joint Filler, Sealant | A03AD044-00001 |  | M | Concrete Work | Substructure Work | Isolation Joint (Separation Joint) | 0 | 0 | 0 | 0 | 0 | w/ Flexible Joint Filler, Sealant | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | H=200, T=12 | = P/1000 |  |  | M
|  |  |  | 줄눈 | Control Joint ¦ ¦ ¦ | A03AD045-00001 Concrete Work Substructure Work Control Joint w/ Joint Sealant, Backstop | A03AD045-00001 |  | M | Concrete Work | Substructure Work | Control Joint | 0 | 0 | 0 | 0 | 0 | w/ Joint Sealant, Backstop | 0 | 0 | 0 | Saw Cut: W( )mm x D( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | H=200, T=12 | =25 | =39 |  | M | *수동입력 추가 (수동입력시 반드시 문자 형식 적용)
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001-00012 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Above GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Above GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001-00013 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Below GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Below GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back |  | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp |  | M3 | * 가상모델링
|  |  |  | 바닥보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | *기초바닥 Protection 은 Lean에 적용 | =A |  |  | M2
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =(A+(P/1000)*D1+(4*D1*D1) )*C1 | _by "▶ Lean Concrete" |  | M3 | *적용규칙A, 7.1
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
4.1.1.4.2 | System Family |  | SF-Q2 | H_SF_AR_S17_SOG_S Trowel | [25 empty] | SOG | [5 empty] | 산출기준 >> [ SOG ]
|  |  |  | 표면처리 | Steel Trowel Finish ¦ ¦ ¦ | A04AS173-00001 Finishing Work Exterior/Interior Finish Work Steel Trowel Finish | A04AS173-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Steel Trowel Finish | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V + (TCS * P/1000) | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = (V + (TCS * P/1000) )*RE | = V*RE |  | TON | RE=0.09
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * (T/1000) | = (P/1000) * (T/1000) |  | M2 | *Slab 옆면만 산출
|  |  |  | 줄눈 | Isolation Joint (Separation Joint) ¦ ¦ ¦ | A03AD044-00001 Concrete Work Substructure Work Isolation Joint (Separation Joint) w/ Flexible Joint Filler, Sealant | A03AD044-00001 |  | M | Concrete Work | Substructure Work | Isolation Joint (Separation Joint) | 0 | 0 | 0 | 0 | 0 | w/ Flexible Joint Filler, Sealant | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | H=200, T=12 | = P/1000 | = P/1000 |  | M
|  |  |  | 줄눈 | Control Joint ¦ ¦ ¦ | A03AD045-00001 Concrete Work Substructure Work Control Joint w/ Joint Sealant, Backstop | A03AD045-00001 |  | M | Concrete Work | Substructure Work | Control Joint | 0 | 0 | 0 | 0 | 0 | w/ Joint Sealant, Backstop | 0 | 0 | 0 | Saw Cut: W( )mm x D( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | H=200, T=12 | =25 | =25 |  | M | *수동입력 추가 (수동입력시 반드시 문자 형식 적용)
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001-00012 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Above GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Above GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001-00013 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Below GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Below GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back |  | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp |  | M3 | * 가상모델링
|  |  |  | 바닥보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | *기초바닥 Protection 은 Lean에 적용 | =A | =A |  | M2
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =(A+(P/1000)*D1+(4*D1*D1) )*C1 | _by "▶ Lean Concrete" |  | M3 | *적용규칙A, 7.1
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
H_SF_AR_S17_SOG_S Trowel_T200
4.1.1.4.2 | System Family |  | SF-Q2A | H_SF_AR_S17_Suspended | [25 empty] | SOG | [5 empty] | 산출기준 >> [ Suspended Slab ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V + (TCS * P/1000) | = V | 17.706 | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = (V + (TCS * P/1000) )*RE | = V*RE | 2.126 | TON | RE=0.09
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * (T/1000) | = (P/1000) * (T/1000) | 0 | M2 | *Slab 옆면만 산출
|  |  |  | 줄눈 | Isolation Joint (Separation Joint) ¦ ¦ ¦ | A03AD044-00001 Concrete Work Substructure Work Isolation Joint (Separation Joint) w/ Flexible Joint Filler, Sealant | A03AD044-00001 |  | M | Concrete Work | Substructure Work | Isolation Joint (Separation Joint) | 0 | 0 | 0 | 0 | 0 | w/ Flexible Joint Filler, Sealant | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | H=200, T=12 | = P/1000 | = P/1000 | 162.2 | M
|  |  |  | 줄눈 | Control Joint ¦ ¦ ¦ | A03AD045-00001 Concrete Work Substructure Work Control Joint w/ Joint Sealant, Backstop | A03AD045-00001 |  | M | Concrete Work | Substructure Work | Control Joint | 0 | 0 | 0 | 0 | 0 | w/ Joint Sealant, Backstop | 0 | 0 | 0 | Saw Cut: W( )mm x D( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | H=200, T=12 |  |  |  | M | *수동입력 추가 (수동입력시 반드시 문자 형식 적용)
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001-00012 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Above GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Above GWL | =Exca | =Exca | 61.852 | M3 | * 가상모델링
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001-00013 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Below GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Below GWL | =Exca | =Exca | 0 | M3 | * 가상모델링
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back | 26.222 | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp | 36.81 | M3 | * 가상모델링
|  |  |  | 바닥보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | *기초바닥 Protection 은 Lean에 적용 | =A | =A | 118.03 | M2
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =(A+(P/1000)*D1+(4*D1*D1) )*C1 | _by "▶ Lean Concrete" | 0 | M3 | *적용규칙A, 7.1
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" | 0 | M2 | *적용규칙A, 7.1
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" | 0 | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" | 0 | M2 | *적용규칙A, 7.1
H_SF_AR_S17_Gr Suspended Slab_T150_GS1
4.1.1.4.2 | System Family |  | SF-Q2 | H_SF_AR_S17_Suspended_S Trowel | [25 empty] | SOG | [5 empty] | 산출기준 >> [ SOG ]
|  |  |  | 표면처리 | Steel Trowel Finish ¦ ¦ ¦ | A04AS173-00001 Finishing Work Exterior/Interior Finish Work Steel Trowel Finish | A04AS173-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Steel Trowel Finish | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V + (TCS * P/1000) | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = (V + (TCS * P/1000) )*RE | = V*RE |  | TON | RE=0.09
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * (T/1000) |  |  | M2 | *Slab 옆면만 산출
|  |  |  | 줄눈 | Control Joint ¦ ¦ ¦ | A03AD045-00001 Concrete Work Substructure Work Control Joint w/ Joint Sealant, Backstop | A03AD045-00001 |  | M | Concrete Work | Substructure Work | Control Joint | 0 | 0 | 0 | 0 | 0 | w/ Joint Sealant, Backstop | 0 | 0 | 0 | Saw Cut: W( )mm x D( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | H=200, T=12 |  |  |  | M | *수동입력 추가 (수동입력시 반드시 문자 형식 적용)
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001-00012 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Above GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Above GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001-00013 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Below GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Below GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back |  | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp |  | M3 | * 가상모델링
|  |  |  | 바닥보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | *기초바닥 Protection 은 Lean에 적용 | =A | =A |  | M2
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =(A+(P/1000)*D1+(4*D1*D1) )*C1 | _by "▶ Lean Concrete" |  | M3 | *적용규칙A, 7.1
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(A+(P/1000)*D1+(4*D1*D1)) | =A |  | M2 | *적용규칙A, 7.1
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | =A | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
| □ Concrete Slab |  |  | ▶ Pit, Trench Slab
4.1.1.5.1 | System Family |  | SF-Q2A | H_FL_AR_B08_UG RC Slab_Pit | [31 empty] | 산출기준 >> [ Suspended Slab ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM C150 Type I or Type IA F'c (Cylinder Strength) = 28MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AF037-00003 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AF037-00003 |  | TON | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | KS D3504 SD400 (Fy=400MPa) | = V*RE | = V*RE |  | TON | RE=0.10
|  |  |  | 거푸집 | Form Work (1 time in use) ¦ Flat Form ¦ ¦ | A03AF036-00001 Concrete Work Superstructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF036-00001 |  | M2 | Concrete Work | Superstructure Work | Form Work (1 time in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | M2 | *Form물량: Pit,Trench Wall에서 산출
|  |  |  | Protection -하부 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =A | =A |  | M2 | *Side Protection : Pit,Trench Wall에서 산출
|  |  |  | 페인팅 | Floor Painting ¦ Epoxy Paint ¦ ¦ | A04AM080-00006 Finishing Work Painting Work Floor Painting Epoxy Paint | A04AM080-00006 |  | M2 | Finishing Work | Painting Work | Floor Painting | Epoxy Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001-00012 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Above GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Above GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001-00013 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Below GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Below GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back |  | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp |  | M3 | * 가상모델링
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =(A+(P/1000)*D1+(4*D1*D1) )*C1 | _by "▶ Lean Concrete" |  | M3 | *적용규칙A, 7.1
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
H_FL_AR_B08_UG RC Slab_Pit_Bitumen_Epoxy_T150
|  | Template |  |  | H_FL_AR_B08_UG RC Slab_Pit_Bitumen_Epoxy_T200
|  | Template |  |  | H_FL_AR_B08_UG RC Slab_Pit_Bitumen_Epoxy_T250
|  | Template |  |  | H_FL_AR_B08_UG RC Slab_Pit_Bitumen_Epoxy_T300
|  | Template |  |  | H_FL_AR_B08_UG RC Slab_Pit_Bitumen_Epoxy_T1000_MF1
|  | Template |  |  | H_FL_AR_B08_UG RC Slab_Pit_Bitumen_Epoxy_T1000_MF2
4.1.1.5.2 | System Family |  | SF-Q2A | H_FL_AR_B08_UG RC Slab_Trench | [31 empty] | 산출기준 >> [ Suspended Slab ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 20MPa ≤ F'c (Cylinder Strength) < 25MPa ¦ | A03AF032-00025 Concrete Work Superstructure Work Structural Concrete Cement Type-1 20MPa ≤ F'c (Cylinder Strength) < 25MPa | A03AF032-00025 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 20MPa ≤ F'c (Cylinder Strength) < 25MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM C150 Type I or Type IA F'c (Cylinder Strength) = 24MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AF037-00003 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AF037-00003 |  | TON | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | KS D3504 SD400 (Fy=400MPa) | = V*RE | = V*RE |  | TON | RE=0.10
|  |  |  | 거푸집 | Form Work (1 time in use) ¦ Flat Form ¦ ¦ | A03AF036-00001 Concrete Work Superstructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF036-00001 |  | M2 | Concrete Work | Superstructure Work | Form Work (1 time in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | M2 | *Form물량: Pit,Trench Wall에서 산출
|  |  |  | Protection -하부 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =A | =A |  | M2 | *Side Protection : Pit,Trench Wall에서 산출
|  |  |  | 페인팅 | Floor Painting ¦ Epoxy Paint ¦ ¦ | A04AM080-00006 Finishing Work Painting Work Floor Painting Epoxy Paint | A04AM080-00006 |  | M2 | Finishing Work | Painting Work | Floor Painting | Epoxy Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A | = A |  | M2
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001-00012 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Above GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Above GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001-00013 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Below GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Below GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back |  | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp |  | M3 | * 가상모델링
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =(A+(P/1000)*D1+(4*D1*D1) )*C1 | _by "▶ Lean Concrete" |  | M3 | *적용규칙A, 7.1
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
H_FL_AR_B08_UG RC Slab_Trench_Bitumen_Epoxy_T200
| □ Slab |  |  | ▶ SOG Slab Edge
4.1.1.6.1 | System Family |  | SF-Q2 | H_SF_AR_S17_SOG Edge | [25 empty] | SOG | [5 empty] | 산출기준 >> [ SOG ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | _by "H_SF_AR_S17_SOG" | = V | 1.008 | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | _by "H_SF_AR_S17_SOG" | = V*RE | 0.09 | TON | RE=0.10
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001-00012 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Above GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Above GWL | _by "H_SF_AR_S17_SOG" | =Exca | 19.16 | M3 | * 가상모델링
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001-00013 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Below GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Below GWL | _by "H_SF_AR_S17_SOG" | =Exca | 0 | M3 | * 가상모델링
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | _by "H_SF_AR_S17_SOG" | =Back | 8.122 | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | _by "H_SF_AR_S17_SOG" | =Disp | 11.404 | M3 | * 가상모델링
|  |  |  | Protection-바닥 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | *기초바닥 Protection 은 Lean에 적용 | _N/A | _by "▶ Lean Concrete" | 0 | M2
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | _by "▶ SOG Slab Edge" | _by "▶ Lean Concrete" | 0 | M3 | *적용규칙A, 7.1
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | _N/A | _by "▶ Lean Concrete" | 0 | M2 | *적용규칙A, 7.1
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | _by "▶ SOG Slab Edge" | _by "▶ Lean Concrete" | 0 | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | _by "▶ SOG Slab Edge" | _by "▶ Lean Concrete" | 0 | M2 | *적용규칙A, 7.1
H_SF_AR_S17_SOG Edge_1625x700
|  | Template |  |  | H_SF_AR_S17_SOG Edge_1400x700
|  | Template |  |  | H_SF_AR_S17_SOG Edge_1500x100
| □ Slab |  |  | ▶ Stoop, Pathway with Haunch
4.1.1.7.1 | System Family |  | SF-Q2 | H_SF_AR_B08_Stoop | [31 empty] | 산출기준 >> [ SOG ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V + (TCS * P/1000) | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V + (TCS * P/1000)*RE | = V*RE |  | TON | RE=0.10
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * (T/1000) | = (P/1000) * (T/1000) |  | M2 | *Slab 옆면만 산출
|  |  |  | Protection-바닥 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | *기초바닥 Protection 은 Lean에 적용 | =A | =A |  | M2
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =(A+(P/1000)*D1+(4*D1*D1) )*C1 | _by "▶ Lean Concrete" |  | M3 | *적용규칙A, 7.1
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
H_SF_AR_B08_Stoop_T150
H_SF_AR_B08_Stoop_T125
4.1.1.7.2 | System Family |  | SF-Q2 | H_SF_AR_B08_Ramp | [31 empty] | 산출기준 >> [ SOG ]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V + (TCS * P/1000) | = V | 2.302 | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V + (TCS * P/1000)*RE | = V*RE | 0.208 | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (P/1000) * (T/1000) | = (P/1000) * (T/1000) | 5.272 | M2 | *Slab 옆면만 산출
|  |  |  | Protection-바닥 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | *기초바닥 Protection 은 Lean에 적용 | =A | _by "▶ Lean Concrete" | 0 | M2
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =(A+(P/1000)*D1+(4*D1*D1) )*C1 | _by "▶ Lean Concrete" | 0 | M3 | *적용규칙A, 7.1
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" | 0 | M2 | *적용규칙A, 7.1
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" | 0 | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | =(A+(P/1000)*D1+(4*D1*D1)) | _by "▶ Lean Concrete" | 0 | M2 | *적용규칙A, 7.1
|  | Template |  |  | H_SF_AR_B08_Ramp_T150
| □ Slab |  |  | ▶ Lean Concrete
4.1.1.8.1 | System Family |  | SF-Q3 | H_SF_AR_S18_Lean | [31 empty] | 산출기준 >> [ Lean ]
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 18MPa | _by " ▶ 해당 기초" | = V |  | M3 | *적용규칙A, 7.1
4.1.1.8.2 | System Family |  | SF-Q3 | H_SF_AR_S18_Lean_Base_Subbase | [31 empty] | 산출기준 >> [ Lean ]
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 18MPa | _by " ▶ 해당 기초" | = V |  | M3 | *적용규칙A, 7.1
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | _by " ▶ 해당 기초" | = A |  | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | _by " ▶ 해당 기초" | = A |  | M2 | *적용규칙A, 7.1
4.1.1.8.3 | System Family |  | SF-Q3 | H_SF_AR_S18_Lean_Bitumen_PE_Base_Subbase | [31 empty] | 산출기준 >> [ Lean ]
|  |  |  | 보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | *기초바닥 Protection 은 Lean에 적용 | _by " ▶ 해당 기초" | = A | 0 | M2 | *적용규칙A, 7.1
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 18MPa | _by " ▶ 해당 기초" | = V | 12.435 | M3 | *적용규칙A, 7.1
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | _by " ▶ 해당 기초" | = A | 0 | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | _by " ▶ 해당 기초" |  |  | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | _by " ▶ 해당 기초" | = A |  | M2 | *적용규칙A, 7.1
H_SF_AR_S18_Lean_T50
H_SF_AR_S18_Lean_T50_100X100
4.2 | Wall Foundation (System Family)
| □ Wall Foundation - normal |  |  | ▶ Wall Foundation
| System Family |  | SF-Q4 | H_SF_AR_S18_Wall Foundation(Wall part) | [31 empty] | 산출기준 >> [Wall Foundation]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V*RE | = V*RE |  | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * 2 | = A * 2 |  | M2
|  |  |  | Protection -Side | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = A * 2 | = A * 2 |  | M2
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001-00012 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Above GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Above GWL | _N/A | _N/A |  | M3 | * 가상모델링
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001-00013 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Below GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Below GWL | _N/A | _N/A |  | M3 | * 가상모델링
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back |  | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp |  | M3 | * 가상모델링
| System Family |  | SF-Q4 | H_SF_AR_S18_Wall Foundation(FDN part) | [31 empty] | 산출기준 >> [Wall Foundation]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V | = V | 44.044 | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V*RE | = V*RE | 5.286 | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (L/1000) * (T/1000) * 2 | = (L/1000) * (T/1000) * 2 | 73.8 | M2 | *옆면만 산출 | 60.48
|  |  |  | 측면+상부+하부 보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = (L/1000) * (T/1000) * 2 + 2*(L/1000)*(W/1000) | = (L/1000) * (T/1000) * 2 + (L/1000)*((W-400)/1000) | 126.074 | M2
|  |  |  | insulation | Insulation under Ground Floor ¦ Extruded Polystyrene Insulation Board ¦ ¦ | A03AD047-00004 Concrete Work Substructure Work Insulation under Ground Floor Extruded Polystyrene Insulation Board 100mm≤THK | A03AD047-00004 |  | M2 | Concrete Work | Substructure Work | Insulation under Ground Floor | Extruded Polystyrene Insulation Board | 0 | 0 | 0 | 0 |  | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | M2
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001-00012 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Above GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Above GWL | =Exca | =Exca | 109.834 | M3 | * 가상모델링
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001-00013 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Below GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Below GWL | =Exca | =Exca | 50.861 | M3 | * 가상모델링
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back | 65.194 | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp | 91.523 | M3 | * 가상모델링
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | = (L/1000) * ((W/1000) + D1*2 ) * C1 | _by "▶ Lean Concrete" | 0 | M3
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(W/1000+2*D1)*(L/1000+2*D1) | _by "▶ Lean Concrete" | 0 | M2
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | = (L/1000) * ((W/1000) + D1*2 ) | _by "▶ Lean Concrete" | 0 | M2
|  |  |  | insulation | Insulation under Ground Floor ¦ Extruded Polystyrene Insulation Board ¦ ¦ | A03AD047-00004 Concrete Work Substructure Work Insulation under Ground Floor Extruded Polystyrene Insulation Board 100mm≤THK | A03AD047-00004 |  | M2 | Concrete Work | Substructure Work | Insulation under Ground Floor | Extruded Polystyrene Insulation Board | 0 | 0 | 0 | 0 |  | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | = (L/1000) * ((W/1000) + D1*2 ) | _by "▶ Lean Concrete" | 0 | M2
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | = (L/1000) * ((W/1000) + D1*2 ) | _by "▶ Lean Concrete" | 0 | M2
H_SF_AR_S18_MAT_Bitumen_T800_WF1
4.3 | Stacked Wall (System Family)
| □ Stacked Wall - normal |  |  | ▶ Stacked Wall
4.3.1.1.1 | System Family |  |  | H_SF_AR_S18_Stacked Wall
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V | = V |  | M3
[5 empty] | Exterior-Brick Over CMU w Metal Stud | [24 empty] | Revit Sample - Arch Link Model.rvt
4.4 | Foundation Rectangular (Non-Pile)
| □ Foundation Rectangular (Non-Pile) |  |  | ▶ Shallow Foundation / Pile Cap(Pile 별도모델링)
4.4.1.1.1 | Load Family |  | SF-Q5 | H_SF_AR_S18_Shallow Fdn_Bitumen | [31 empty] | 산출기준 >> [독립기초]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | =V | =V | 0.937 | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | =V*RE | =V*RE | 0.112 | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =2*(W/1000 + D/1000) * (T/1000) | =2*(W/1000 + D/1000) * (T/1000) | 3 | M2
|  |  |  | 측면+상부+하부 보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =2*(W/1000 + D/1000) * (T/1000)+2*(W/1000*D/1000) | =2*(W/1000 + D/1000) * (T/1000)+(W/1000*D/1000) | 4.562 | M2
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001-00012 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Above GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Above GWL | =Exca | =Exca | 2.337 | M3 | * 가상모델링
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001-00013 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Below GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Below GWL | =Exca | =Exca | 1.082 | M3 | * 가상모델링
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back | 1.387 | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp | 1.947 | M3 | * 가상모델링
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =(W/1000+2*D1)*(D/1000+2*D1) * C1 | _by "▶ Lean Concrete" | 0 | M3 | *적용규칙A, 7.1
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(W/1000+2*D1)*(D/1000+2*D1) | _by "▶ Lean Concrete" | 0 | M2 | *적용규칙A, 7.1
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | =(W/1000+2*D1)*(D/1000+2*D1) | _by "▶ Lean Concrete" | 0 | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | =(W/1000+2*D1)*(D/1000+2*D1) | _by "▶ Lean Concrete" | 0 | M2 | *적용규칙A, 7.1
H_SF_AR_S18_Shallow Fdn_Bitumen_1250x1250xT500_F2
H_SF_AR_S18_Shallow Fdn_Bitumen_2500x2500xT1000_F1
H_SF_AR_S18_Shallow Fdn_Bitumen_2500x2500xT1000_F1A
| Load Family |  | SF-Q5 | H_SF_AR_S18_Shallow Fdn_Bitumen_Insulation | [31 empty] | 산출기준 >> [독립기초]
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | =V | =V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | =V*RE | =V*RE |  | TON | RE=0.12
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =2*(W/1000 + D/1000) * (T/1000) | =2*(W/1000 + D/1000) * (T/1000) |  | M2
|  |  |  | 측면+상부+하부 보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =2*(W/1000 + D/1000) * (T/1000)+2*(W/1000*D/1000) | =2*(W/1000 + D/1000) * (T/1000)+2*(W/1000*D/1000) |  | M2
|  |  |  | insulation | Insulation under Ground Floor ¦ Extruded Polystyrene Insulation Board ¦ ¦ | A03AD047-00004 Concrete Work Substructure Work Insulation under Ground Floor Extruded Polystyrene Insulation Board 100mm≤THK | A03AD047-00004 |  | M2 | Concrete Work | Substructure Work | Insulation under Ground Floor | Extruded Polystyrene Insulation Board | 0 | 0 | 0 | 0 |  | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =2*(W/1000 + D/1000) * (T/1000)+2*(W/1000*D/1000) | =2*(W/1000 + D/1000) * (T/1000)+2*(W/1000*D/1000) |  | M2
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001-00012 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Above GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Above GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001-00013 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Below GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Below GWL | =Exca | =Exca |  | M3 | * 가상모델링
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back |  | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp |  | M3 | * 가상모델링
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =(W/1000+2*D1)*(D/1000+2*D1) * C1 | _by "▶ Lean Concrete" |  | M3 | *적용규칙A, 7.1
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(W/1000+2*D1)*(D/1000+2*D1) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | insulation | Insulation under Ground Floor ¦ Extruded Polystyrene Insulation Board ¦ ¦ | A03AD047-00004 Concrete Work Substructure Work Insulation under Ground Floor Extruded Polystyrene Insulation Board 100mm≤THK | A03AD047-00004 |  | M2 | Concrete Work | Substructure Work | Insulation under Ground Floor | Extruded Polystyrene Insulation Board | 0 | 0 | 0 | 0 |  | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | =(W/1000+2*D1)*(D/1000+2*D1) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | =(W/1000+2*D1)*(D/1000+2*D1) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | =(W/1000+2*D1)*(D/1000+2*D1) | _by "▶ Lean Concrete" |  | M2 | *적용규칙A, 7.1
H_SF_AR_S18_W2500xL2500xT1000_Bitumen_F1
H_SF_AR_S18_W1250xL1250xT500_Bitumen_F2
4.5 | Pile
| □ Pile - normal |  |  | ▶ Only Pile
4.5.1.1.1 | Load Family |  | SF-Q6 | H_SF_AR_S19_Steel Pile | [25 empty] | Pile Only | [5 empty] | 산출기준 >> [Pile]
|  |  |  | 파일 | Steel Pipe Pile Work ¦ Direct Driving ¦ ¦ | A02AA020-00004 Pile Work Piling Work Steel Pipe Pile Work Direct Driving Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA020-00004 |  | M | Pile Work | Piling Work | Steel Pipe Pile Work | Direct Driving | 0 | 0 | 0 | 0 | Including Pile Connection and Joint Welding Work | 0 | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | D=( 508 )mm / THK=(12 )mm Pile Length per Hole=( 30 )M | =L | =L |  | M
|  |  |  | 파일 두부 | Pretensioned High-strength Concrete Pile (Type-A) ¦ ¦ ¦ | A02AB018-00004 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) 500 ≤ DIA <600 | A02AB018-00004 |  | EA | Pile Work | Pile Head Treatment | Pretensioned High-strength Concrete Pile (Type-A) | 0 | 0 | 0 | 0 | 0 |  | 0 | 500 ≤ DIA <600 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | D=( 508 )mm / THK=(12 )mm Pile Length per Hole=( 30 )M | =Q | =Q |  | EA
H_SF_AR_S19_Steel Pile_D508x12t_L10
4.5.1.1.2 | Load Family |  | SF-Q6 | H_SF_AR_S19_PHC Pile_Driven | [25 empty] | Pile Only | [5 empty] | 산출기준 >> [Pile]
|  |  |  | 파일 | Pretensioned High-strength Concrete Pile (Type-A) ¦ Direct Driving ¦ ¦ | A02AA018-00009 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA018-00009 |  | M | Pile Work | Piling Work | Pretensioned High-strength Concrete Pile (Type-A) | Direct Driving | 0 | 0 | 0 | 0 | Including Pile Connection and Joint Welding Work | 0 | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | D=( 500 )mm Pile Length per Hole=( 30 )M | =L | =L |  | M
|  |  |  | 파일 두부 | Pretensioned High-strength Concrete Pile (Type-A) ¦ ¦ ¦ | A02AB018-00004 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) 500 ≤ DIA <600 | A02AB018-00004 |  | EA | Pile Work | Pile Head Treatment | Pretensioned High-strength Concrete Pile (Type-A) | 0 | 0 | 0 | 0 | 0 |  | 0 | 500 ≤ DIA <600 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | D=( 500 )mm Pile Length per Hole=( 30 )M | =Q | =Q |  | EA
H_SF_AR_S19_PHC Pile_Driven_D500_L30
4.5.1.1.3 | Load Family |  | SF-Q6 | H_SF_AR_S19_PHC Pile_Pre-boring | [25 empty] | Pile Only | [5 empty] | 산출기준 >> [Pile]
|  |  |  | 파일 | Pretensioned High-strength Concrete Pile (Type-A) ¦ Augering without Casing ¦ ¦ | A02AA018-00025 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA018-00025 |  | M | Pile Work | Piling Work | Pretensioned High-strength Concrete Pile (Type-A) | Augering without Casing | 0 | 0 | 0 | 0 | Including Pile Connection and Joint Welding Work | 0 | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | D=( 500 )mm Pile Length per Hole=( 30 )M | =L | =L |  | M
|  |  |  | 파일 두부 | Pretensioned High-strength Concrete Pile (Type-A) ¦ ¦ ¦ | A02AB018-00004 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) 500 ≤ DIA <600 | A02AB018-00004 |  | EA | Pile Work | Pile Head Treatment | Pretensioned High-strength Concrete Pile (Type-A) | 0 | 0 | 0 | 0 | 0 |  | 0 | 500 ≤ DIA <600 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | D=( 500 )mm Pile Length per Hole=( 30 )M | =Q | =Q |  | EA
H_SF_AR_S19_PHC Pile_Pre-boring_D500_L30
4.5.1.1.3 | Load Family |  | SF-Q6 | H_SF_AR_S19_PHC Pile_Direct Driving | [25 empty] | Pile Only | [5 empty] | 산출기준 >> [Pile]
|  |  |  | 파일 | Pretensioned High-strength Concrete Pile (Type-A) ¦ Direct Driving ¦ ¦ | A02AA018-00009 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA018-00009 |  | M | Pile Work | Piling Work | Pretensioned High-strength Concrete Pile (Type-A) | Direct Driving | 0 | 0 | 0 | 0 | Including Pile Connection and Joint Welding Work | 0 | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | D=( 500 )mm Pile Length per Hole=( 30 )M | =L | =L/1000 | 337.2 | M
|  |  |  | 파일 두부 | Pretensioned High-strength Concrete Pile (Type-A) ¦ ¦ ¦ | A02AB018-00004 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) 500 ≤ DIA <600 | A02AB018-00004 |  | EA | Pile Work | Pile Head Treatment | Pretensioned High-strength Concrete Pile (Type-A) | 0 | 0 | 0 | 0 | 0 |  | 0 | 500 ≤ DIA <600 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | D=( 500 )mm Pile Length per Hole=( 30 )M | =Q | =Q | 12 | EA
H_SF_AR_S19_PHC Pile_Direct Driving_D500_L28.1
해당 SOG에서 산출 ?
=> 전부 N.A?
Stoop, Ramp, Walkway의 Joint 산출방식을 Perimeter 기준으로 할 경우 과다산출
Family 분리
R4- 삭제 ?
Stoop, Ramp, Walkway의 Joint 산출방식을 Perimeter 기준으로 할 경우 과다산출

## 5.St_Col
[Family List] - Structural Columns |  |  |  |  | 표준구성도로 가기
NO | Family Category | Building Tag | Q'ty Cal Type Tag | Standard Type | Family Type Name | Work Master Code /w Description | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Description | 입찰_ 물량산출식 | 실행_ 물량산출식 | Quantity |  | Remark (물량관련)
5 | Structural Columns [SC]
5.1 | RC_UG Pedestal
| □ RC_UG Pedestal |  |  | ▶ RC_UG Pedestal
5.1.1.1.1 | Load Family |  | SC-Q1A | H_SC_AR_S15_UG PED_Bit | [25 empty] | F'c (Cylinder Strength) = 24MPa | [5 empty] | 산출기준 >> [Concrete Column]-UG
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V | = V | 1.8 | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V*RE | = V*RE | 0.54 | TON | RE=0.3
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =2*( (W/1000)+(D/1000) ) * (H/1000) | =2*( (W/1000)+(D/1000) ) * (H/1000) | 0 | M2
|  |  |  | 줄눈 | Isolation Joint (Separation Joint) ¦ ¦ ¦ | A03AD044-00001 Concrete Work Substructure Work Isolation Joint (Separation Joint) w/ Flexible Joint Filler, Sealant | A03AD044-00001 |  | M | Concrete Work | Substructure Work | Isolation Joint (Separation Joint) | 0 | 0 | 0 | 0 | 0 | w/ Flexible Joint Filler, Sealant | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | = 2*( (W/1000)+(L/1000) ) |  |  | M | 분리줄눈 공통 WBS로 반영
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back | 0.756 | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp | 1.068 | M3 | * 가상모델링
|  |  |  | 보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =2*( (W/1000)+(D/1000) ) * (H/1000) | =2*( (W/1000)+(D/1000) ) * (H/1000) | 0 | M2
[5 empty] | H_SC_AR_S15_UG Column_Bit_500x500_C1 | [25 empty] | = 2*( (W/1000)+(L/1000) )
[5 empty] | H_SC_AR_S15_UG Column_Bit_500x500_C1A | [25 empty] | = 2*( (W/1000)+(L/1000) )
= 2*( (W/1000)+(L/1000) )
5.1.1.1.2 | Load Family |  | SC-Q1A | H_SC_AR_S15_UG PED_Bit_Anchor | [25 empty] | Pedestal, UG | [5 empty] | 산출기준 >> [Concrete Column]-UG
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V | = V |  | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V*RE | = V*RE |  | TON | RE=0.3
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =2*( (W/1000)+(D/1000) ) * (H/1000) | =2*( (W/1000)+(D/1000) ) * (H/1000) |  | M2
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back |  | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp |  | M3 | * 가상모델링
|  |  |  | 보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =2*( (W/1000)+(D/1000) ) * (H/1000) | =2*( (W/1000)+(D/1000) ) * (H/1000) |  | M2
|  |  |  | 앵커설치 | Anchor Bolt (Installation only) ¦ ¦ ¦ | A03AD029-00008 Concrete Work Substructure Work Anchor Bolt (Installation only) M36 | A03AD029-00008 |  | EA | Concrete Work | Substructure Work | Anchor Bolt (Installation only) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = 12 | = 12 |  | EA | 타입별 앵커볼트 개수 상이하므로, 개별입력 필요
|  |  |  | 그라우트 | Non-Shrink Grouting ¦ ¦ ¦ | S03AA030-00001 Main Steel Structure Erection Work Shelter/Building Non-Shrink Grouting | S03AA030-00001 |  | M3 | Main Steel Structure Erection Work | Shelter/Building | Non-Shrink Grouting | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | THK=( )mm | 0 | 0 |  | = (W/1000) * (D/1000) * GT | = (W/1000) * (D/1000) * GT |  | M3
[5 empty] | H_SC_AR_S15_UG PED_Bit_Anchor_1000x1800 | A03AD029-00008 Concrete Work Substructure Work Anchor Bolt (Installation only) M36 | A03AD029-00008 |  | EA | Concrete Work | Substructure Work | Anchor Bolt (Installation only) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =12 |  |  | EA | 칼럼당 앵커볼트 개수 입력
5.1.1.1.3 | Load Family |  | SC-Q1A | H_SC_AR_S15_UG PED_Grout only | [25 empty] | Grout modeling 별도 적용할 경우 | [5 empty] | 산출기준 >> [Concrete Column]-UG
|  |  |  | 그라우트 | Non-Shrink Grouting ¦ ¦ ¦ | S03AA030-00001 Main Steel Structure Erection Work Shelter/Building Non-Shrink Grouting | S03AA030-00001 |  | M3 | Main Steel Structure Erection Work | Shelter/Building | Non-Shrink Grouting | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | THK=( )mm | 0 | 0 |  | = (W/1000) * (D/1000) * GT | = (W/1000) * (D/1000) * GT |  | M3
H_SC_AR_S15_UG PED_Grout only_500x500
| □ RC_Column_Rectangular |  |  | ▶ RC_Column Rectangular
5.1.2.1.1 | Load Family |  | SC-Q1 | H_SC_AR_S15_AG Column | [31 empty] | 산출기준 >> [Concrete Column]-AG
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V | = V | 10.175 | M3
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AF037-00003 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AF037-00003 |  | TON | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V*RE | = V*RE | 3.058 | TON | RE=0.3
|  |  |  | 거푸집 | Form Work (1 time in use) ¦ Flat Form ¦ ¦ | A03AF036-00001 Concrete Work Superstructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF036-00001 |  | M2 | Concrete Work | Superstructure Work | Form Work (1 time in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =2*( (W/1000)+(D/1000) ) * (H/1000) | =2*( (W/1000)+(D/1000) ) * (H/1000) | 0 | M2 | *HGEN SGB - Roof Steel Frame 용 Steel Column
[5 empty] | H_SC_AR_S15_AG Column_500x500_C1 | [25 empty] | = (W/1000) * (D/1000) * GT | = (W/1000) * (D/1000) * GT
[31 empty] | = (W/1000) * (D/1000) * GT | = (W/1000) * (D/1000) * GT
[31 empty] | = (W/1000) * (D/1000) * GT | = (W/1000) * (D/1000) * GT
5.2 | Steel Column_W
[5 empty] | Extra Heavy Steel | 200
[5 empty] | Heavy Steel | 90
Medium Steel
[5 empty] | Light Steel | 30
[5 empty] | Extra Light Steel | 10
| □ Steel Column_W |  |  | ▶ Steel Column_W_ASTM A6M
[W-Extra Heavy Steel]
5.2.1.1.1 | Load Family |  | SC-Q2 | H_SC_AR_S01_W (Extra Heavy) | [25 empty] | ASTM A992 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Extra Heavy Steel - Standard ¦ ¦ ¦ | S01AA071-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Heavy Steel - Standard | S01AA071-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥( )KG/M | - Material: ( ASTM A992 ) - Weight≥( 200 )KG/M | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Heavy Steel ¦ ¦ ¦ | S03AA081-00001 Main Steel Structure Erection Work Shelter/Building Extra Heavy Steel | S03AA081-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( ASTM A992 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
[W-Heavy Steel]
5.2.1.1.2 | Load Family |  | SC-Q2 | H_SC_AR_S01_W (Heavy) | [25 empty] | ASTM A36 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | - Material: ( ASTM A36 ) - Weight≥( 90 )KG/M | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( - Material: ( ASTM A36 ) - Weight≥( 90 )KG/M ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
H_SC_AR_S01_W-360x91
[W-Medium Steel]
5.2.1.1.3 | Load Family |  | SC-Q2 | H_SC_AR_S01_W (Medium) | [25 empty] | ASTM A6M | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | - Material: ( ASTM A6M ) - (90)KG/M>Weight≥(30)KG/M | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( - Material: ( ASTM A6M ) - (90)KG/M>Weight≥(30)KG/M ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
H_SC_AR_S01_W-200x31.3
[W-Light Steel]
5.2.1.1.4 | Load Family |  | SC-Q2 | H_SC_AR_S01_W (Light) | [25 empty] | ASTM A6M | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | - Material: ( ASTM A6M ) - (30)KG/M>Weight | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( - Material: ( ASTM A6M ) - (30)KG/M>Weight ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
H_SC_AR_S01_W-200x22.5
[W-Extra Light Steel]
5.2.1.1.5 | Load Family |  | SC-Q2 | H_SC_AR_S01_W (Extra Light) | [25 empty] | ASTM A6M | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Extra Light Steel - Standard ¦ ¦ ¦ | S01AA075-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Light Steel - Standard | S01AA075-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | ( )KG/M>Weight | - Material: ( ASTM A6M ) - (10)KG/M>Weight | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Light Steel ¦ ¦ ¦ | S03AA085-00001 Main Steel Structure Erection Work Shelter/Building Extra Light Steel | S03AA085-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( - Material: ( ASTM A6M ) - (10)KG/M>Weight ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
| □ Steel Column_H |  |  | ▶ Steel Column_H_KSD3502
[H-Extra Heavy Steel]
5.2.2.1.1 | Load Family |  | SC-Q2 | H_SC_AR_S01_H (Extra Heavy) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Extra Heavy Steel - Standard ¦ ¦ ¦ | S01AA071-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Heavy Steel - Standard | S01AA071-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥( )KG/M | - Material: ( KSD3502 ) - Weight≥( 200 )KG/M | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Heavy Steel ¦ ¦ ¦ | S03AA081-00001 Main Steel Structure Erection Work Shelter/Building Extra Heavy Steel | S03AA081-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
[H-Heavy Steel]
5.2.2.1.2 | Load Family |  | SC-Q2 | H_SC_AR_S01_H (Heavy) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | - Material: ( KSD3502 ) - Weight≥( 90 )KG/M | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
H_SC_AR_S01_H-400x400x13x21
|  | Template |  |  | H_SC_AR_S01_H-300x300x10x15_PLATFORM
[H-Medium Steel]
5.2.2.1.3 | Load Family |  | SC-Q2 | H_SC_AR_S01_H (Medium) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | - Material: ( KSD3502 ) - (90)KG/M>Weight≥(30)KG/M | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 | 0.472 | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 | 0.56 | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 | 0.096 | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) | 13.088 | M2
H_SC_AR_S01_H-200x200x8x12_SC20
Template
[H-Light Steel]
5.2.2.1.4 | Load Family |  | SC-Q2 | H_SC_AR_S01_H (Light) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | - Material: ( KSD3502 ) - (30)KG/M>Weight | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
H_SC_AR_S01_H-100x100x6x8
[H-Extra Light Steel]
5.2.2.1.5 | Load Family |  | SC-Q2 | H_SC_AR_S01_H (Extra Light) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Extra Light Steel - Standard ¦ ¦ ¦ | S01AA075-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Light Steel - Standard | S01AA075-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | ( )KG/M>Weight | - Material: ( KSD3502 ) - (10)KG/M>Weight | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Light Steel ¦ ¦ ¦ | S03AA085-00001 Main Steel Structure Erection Work Shelter/Building Extra Light Steel | S03AA085-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
| □ Steel Column_H_Built Up |  |  | ▶ Steel Column_H_Built Up
[BH-Extra Heavy Steel]
5.2.3.1.1 | Load Family |  | SC-Q2 | H_SC_AR_S01_BH (Extra Heavy) | [25 empty] | KS D 3503 SS275 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Extra Heavy Steel - Built up ¦ ¦ ¦ | S01AA076-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Heavy Steel - Built up | S01AA076-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Heavy Steel - Built up | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥( )KG/M | - Material: ( KS D 3503 SS275 ) - Weight≥( 200 )KG/M | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Heavy Steel ¦ ¦ ¦ | S03AA081-00001 Main Steel Structure Erection Work Shelter/Building Extra Heavy Steel | S03AA081-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KS D 3503 SS275 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
[5 empty] | H_SC_AR_S01_BH-1000x300x20x40_SC1 | [24 empty] | (338 kg/m)
[BH-Heavy Steel]
5.2.3.1.2 | Load Family |  | SC-Q2 | H_SC_AR_S01_BH (Heavy) | [25 empty] | KS D 3503 SS275 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Heavy Steel - Built up ¦ ¦ ¦ | S01AA077-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Built up | S01AA077-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Built up | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | - Material: ( KS D 3503 SS275 ) - Weight≥( 90 )KG/M | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KS D 3503 SS275 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
[BH-Medium Steel]
5.2.3.1.3 | Load Family |  | SC-Q2 | H_SC_AR_S01_BH (Medium) | [25 empty] | KS D 3503 SS275 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Medium Steel - Built up ¦ ¦ ¦ | S01AA078-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Built up | S01AA078-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Built up | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | - Material: ( KS D 3503 SS275 ) - (90)KG/M>Weight≥(30)KG/M | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KS D 3503 SS275 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
| □ Steel Column_SHS (Square Hollow Section) |  |  | ▶ Steel Column_SHS_KSD3502
[SHS-Heavy Steel]
5.2.4.1.1 | Load Family |  | SC-Q2 | H_SC_AR_S01_SHS (Heavy) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | - Material: ( KSD3502 ) - Weight≥( 90 )KG/M | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
[5 empty] | H_SC_AR_S01_SHS-350x350x12_SC1 | [24 empty] | (124.4kg/m)
[SHS-Medium Steel]
5.2.4.1.2 | Load Family |  | SC-Q2 | H_SC_AR_S01_SHS (Medium) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | - Material: ( KSD3502 ) - (90)KG/M>Weight≥(30)KG/M | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
[5 empty] | H_SC_AR_S01_SHS-250x250x12_SC2 | [24 empty] | (86.7kg/m)
[SHS-Light Steel]
5.2.4.1.3 | Load Family |  | SC-Q2 | H_SC_AR_S01_SHS (Light) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | - Material: ( KSD3502 ) - (30)KG/M>Weight | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
[5 empty] | H_SC_AR_S01_SHS-100x100x9_SC3 | [24 empty] | (24.1kg/m)
[SHS-Extra Light Steel]
5.2.4.1.4 | Load Family |  | SC-Q2 | H_SC_AR_S01_SHS (Extra Light) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Extra Light Steel - Standard ¦ ¦ ¦ | S01AA075-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Light Steel - Standard | S01AA075-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | ( )KG/M>Weight | - Material: ( KSD3502 ) - (10)KG/M>Weight | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Light Steel ¦ ¦ ¦ | S03AA085-00001 Main Steel Structure Erection Work Shelter/Building Extra Light Steel | S03AA085-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
[5 empty] | H_SC_AR_S01_SHS-40x40x1.6_SC4 | [24 empty] | (1.9kg/m)
| □ Steel Column_RHS (Rectangular Hollow Section) |  |  | ▶ Steel Column_RHS_KSD3502
[RHS-Heavy Steel]
5.2.5.1.1 | Load Family |  | SC-Q2 | H_SC_AR_S01_RHS (Heavy) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | - Material: ( KSD3502 ) - Weight≥( 90 )KG/M | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
[5 empty] | H_SC_AR_S01_RHS-400x200x12_SC1 | [24 empty] | (105.6kg/m)
[RHS-Medium Steel]
5.2.5.1.2 | Load Family |  | SC-Q2 | H_SC_AR_S01_RHS (Medium) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | - Material: ( KSD3502 ) - (90)KG/M>Weight≥(30)KG/M | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
[5 empty] | H_SC_AR_S01_RHS-250x150x12_SC2 | [24 empty] | (67.9kg/m)
[RHS-Light Steel]
5.2.5.1.3 | Load Family |  | SC-Q2 | H_SC_AR_S01_RHS (Light) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | - Material: ( KSD3502 ) - (30)KG/M>Weight | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
[5 empty] | H_SC_AR_S01_RHS-200x100x4.5_SC3 | [24 empty] | (20.2kg/m)
[RHS-Extra Light Steel]
5.2.5.1.4 | Load Family |  | SC-Q2 | H_SC_AR_S01_RHS (Extra Light) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Extra Light Steel - Standard ¦ ¦ ¦ | S01AA075-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Light Steel - Standard | S01AA075-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | ( )KG/M>Weight | - Material: ( KSD3502 ) - (10)KG/M>Weight | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Light Steel ¦ ¦ ¦ | S03AA085-00001 Main Steel Structure Erection Work Shelter/Building Extra Light Steel | S03AA085-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) | = P * (H/1000) |  | M2
[5 empty] | H_SC_AR_S01_RHS-50x20x1.6_SC4 | [24 empty] | (1.6kg/m)
| □ Steel Column_CHS (Circular Hollow Section) |  |  | ▶ Steel Column_CHS_KSD3502
[CHS-Extra Heavy Steel]
5.2.6.1.1 | Load Family |  | SC-Q2 | H_SC_AR_S01_CHS (Extra Heavy) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Extra Heavy Steel - Standard ¦ ¦ ¦ | S01AA071-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Heavy Steel - Standard | S01AA071-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥( )KG/M | - Material: ( KSD3502 ) - Weight≥( 200 )KG/M | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Heavy Steel ¦ ¦ ¦ | S03AA081-00001 Main Steel Structure Erection Work Shelter/Building Extra Heavy Steel | S03AA081-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) | = P * (H/1000) |  | M2
[5 empty] | H_SC_AR_S01_CHS-1016x16_SC1 | [24 empty] | (395 kg/m)
[CHS-Heavy Steel]
5.2.6.1.2 | Load Family |  | SC-Q2 | H_SC_AR_S01_CHS (Heavy) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | - Material: ( KSD3502 ) - Weight≥( 90 )KG/M | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) | = P * (H/1000) |  | M2
[5 empty] | H_SC_AR_S01_CHS-558.8x9.5_SC2 | [24 empty] | (129 kg/m)
[CHS-Medium Steel]
5.2.6.1.3 | Load Family |  | SC-Q2 | H_SC_AR_S01_CHS (Medium) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | - Material: ( KSD3502 ) - (90)KG/M>Weight≥(30)KG/M | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) | = P * (H/1000) |  | M2
[5 empty] | H_SC_AR_S01_CHS-267.4x6.6_SC3 | [24 empty] | (42.4 kg/m)
[CHS-Light Steel]
5.2.6.1.4 | Load Family |  | SC-Q2 | H_SC_AR_S01_CHS (Light) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | - Material: ( KSD3502 ) - (30)KG/M>Weight | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
[5 empty] | H_SC_AR_S01_CHS-165.2x4.5_SC4 | [24 empty] | (17.8 kg/m)
[CHS-Extra Light Steel]
5.2.6.1.5 | Load Family |  | SC-Q2 | H_SC_AR_S01_CHS (Extra Light) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Column]
|  |  |  | 철골제작 | Extra Light Steel - Standard ¦ ¦ ¦ | S01AA075-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Light Steel - Standard | S01AA075-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | ( )KG/M>Weight | - Material: ( KSD3502 ) - (10)KG/M>Weight | = ( (H/1000) * W )/1000 | = ( (H/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Light Steel ¦ ¦ ¦ | S03AA085-00001 Main Steel Structure Erection Work Shelter/Building Extra Light Steel | S03AA085-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (H/1000) * W ) * (1+SE) / 1000 | = ( (H/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (H/1000) * W ) * SE / 1000 | = ( (H/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (H/1000) * (1+PE) | = P * (H/1000) * (1+PE) |  | M2
[5 empty] | H_SC_AR_S01_CHS-21.7x1.9_SC5 | [24 empty] | (0.928 kg/m)
74
=2*( (500.0/1000)+(3700.0/1000) ) * (3700.0/1000)
- Length 500, Length 1150
-Column 단면 Length 매개변수명 변경 필요
L=>D
L=>D
이름 변경
: H_SC_AR_S15_UG PED_Bit_Grout

## 6.St_Framing
[Family List] - Structural Framing |  |  |  |  | 표준구성도로 가기
NO | Family Category | Building Tag | Q'ty Cal Type Tag | Standard Type | Family Type Name | Work Master Code /w Description | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Description | 입찰_ 물량산출식 | 실행_ 물량산출식 | Quantity |  | Remark (물량관련)
6 | Structural Framing [SB]
6.1 | RC_Tie Girder
| □ RC_Beam / Girder |  |  | ▶ Tie Girder
6.1.1.1.1 | Load Family |  | SB-Q1A | H_SB_AR_S16_TG | [25 empty] | Tie Girder | [5 empty] | 산출기준 >> [Concrete Beam] - UG
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032-00022 |  | M3 | Concrete Work | Substructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V | = V | 12.072 | M3 |  | * 기준 : 슬라브 두께 미공제
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037-00003 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V*RE | = V*RE | 1.69 | TON | RE=0.14
|  |  |  | 거푸집 | Form Work (3 times in use) ¦ Flat Form ¦ ¦ | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035-00001 |  | M2 | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | = 2 * (L/1000) * (D/1000) | = 2 * (L/1000) * (D/1000) | 63.24 | M2
|  |  |  | 측면보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Bitumen/Bituminous/Asphalt Coating | = 2 * (L/1000) * (H2/1000) | = 2 * (L/1000) * (H2/1000) | 0.033 | M2
|  |  | 비가 그래도 | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001-00012 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Above GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Above GWL | =Exca | =Exca | 24.075 | M3 | * 가상모델링
|  |  |  | 터파기 | Excavation ¦ Soil, Mech. ¦ ¦ | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001-00013 |  | M3 | Earth Work | - | Excavation | Soil, Mech. | 0 | 0 | 0 | 0 |  | Manual Excavation Below GWL |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Below GWL | =Exca | =Exca | 0 | M3 | * 가상모델링
|  |  |  | 되메우기 | Backfill ¦ Re-use, Soil ¦ ¦ | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003-00001 |  | M3 | Earth Work | - | Backfill | Re-use, Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | Compaction=( 95 )% | =Back | =Back | 10.207 | M3 | * 가상모델링
|  |  |  | 잔토처리 | Disposal ¦ Soil ¦ ¦ | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004-00001 |  | M3 | Earth Work | - | Disposal | Soil | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | =Disp | =Disp | 14.33 | M3 | * 가상모델링
|  |  |  | 바닥보호층 | Bitumen/Bituminous/Asphalt Coating ¦ ¦ ¦ | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 |  | M2 | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | *기초바닥 Protection 은 Lean에 적용 | = (W/1000) * (L/1000) | _by "▶ Lean Concrete" | 0 | M2
|  |  |  | 버림 | Lean Concrete (including Form work) ¦ ¦ 10MPa ≤ F'c (Cylinder Strength) < 15MPa ¦ | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034-00013 |  | M3 | Concrete Work | Substructure Work | Lean Concrete (including Form work) | 0 | Cement Type-1 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Disposal Distance=Appx. (20 )km from Site | = ( (W/1000) + 2*D1 ) * (L/1000) * C1 | _by "▶ Lean Concrete" | 0 | M3
|  |  |  | 차단층 | PE Sheet (Vapor Barrier) ¦ ¦ ¦ | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012-00002 |  | M2 | Earth Work | - | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 |  | 0 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | THK=( 0.1 )mm | = ( (W/1000) + 2*D1 ) * (L/1000) | _by "▶ Lean Concrete" | 0 | M2
|  |  |  | 기층 | Base Course ¦ ¦ ¦ | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005-00001 |  | M2 | Earth Work | - | Base Course | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | THK=( 150 )mm CBR=( )% | = ( (W/1000) + 2*D1 ) * (L/1000) | _by "▶ Lean Concrete" | 0 | M2
|  |  |  | 보조기층 | Subbase Course ¦ ¦ ¦ | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006-00001 |  | M2 | Earth Work | - | Subbase Course | 0 | 0 | 0 | 0 | 0 | Including Compaction of Sub-Grade | 0 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase | = ( (W/1000) + 2*D1 ) * (L/1000) | _by "▶ Lean Concrete" | 0 | M2
H_SB_AR_S16_TG_400x600_GB1
H_SB_AR_S16_TG_400x600_GG1
H_SB_AR_S16_TG_400x600_GG2
| □ RC_Beam / Girder |  |  | ▶ RC Beam / Girder
6.1.1.2.1 | Load Family |  | SB-Q1 | H_SB_AR_S16_AG | [25 empty] | Tie Girder | [5 empty] | 산출기준 >> [Concrete Beam] - AG
|  |  |  | 구체 | Structural Concrete ¦ ¦ 25MPa ≤ F'c (Cylinder Strength) < 30MPa ¦ | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = V | = V | 11.252 | M3 |  | * 기준 : 슬라브 두께 미공제
|  |  |  | 철근 | Rebar Work ¦ Deformed Bar (Non-Coat.) ¦ 300MPa<Fy≤400MPa ¦ | A03AF037-00003 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AF037-00003 |  | TON | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 300MPa<Fy≤400MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = V*RE | = V*RE | 1.578 | TON | RE=0.14
|  |  |  | 거푸집 | Form Work (1 time in use) ¦ Flat Form ¦ ¦ | A03AF036-00001 Concrete Work Superstructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF036-00001 |  | M2 | Concrete Work | Superstructure Work | Form Work (1 time in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = 2*(L/1000)*(D/1000) + (W/1000)*(L/1000) | = 2*(L/1000)*(D/1000) + (W/1000)*(L/1000) | 67.5 | M2
H_SB_AR_S16_AG_500x500_WG1
6.2 | Steel Beam
[5 empty] | Extra Heavy Steel | 200
[5 empty] | Heavy Steel | 90
Medium Steel
[5 empty] | Light Steel | 30
[5 empty] | Extra Light Steel | 10
| □ Steel Beam_W |  |  | ▶ Steel Beam_W_ASTM A6 M
[W-Extra Heavy Steel]
6.2.1.1.1 | Load Family |  | SB-Q2 | H_SB_AR_S02_W (Extra Heavy) | [25 empty] | ASTM A36 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Extra Heavy Steel - Standard ¦ ¦ ¦ | S01AA071-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Heavy Steel - Standard | S01AA071-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥( )KG/M | - Material: ( ASTM A36 ) - Weight≥( 200 )KG/M | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Heavy Steel ¦ ¦ ¦ | S03AA081-00001 Main Steel Structure Erection Work Shelter/Building Extra Heavy Steel | S03AA081-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( ASTM A36 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_W-1100x400x499_SG1 | [24 empty] | (498.6 kg/m)
[W-Heavy Steel]
6.2.1.1.2 | Load Family |  | SB-Q2 | H_SB_AR_S02_W (Heavy) | [25 empty] | ASTM A36 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | - Material: ( ASTM A36 ) - Weight≥( 90 ) | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( ASTM A36 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_W-530x210x101_SG2 | [24 empty] | (101.5 kg/m)
[W-Medium Steel]
6.2.1.1.3 | Load Family |  | SB-Q2 | H_SB_AR_S02_W (Medium) | [25 empty] | ASTM A36 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | - Material: ( ASTM A36 ) - (90)KG/M>Weight≥(30)KG/M | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( ASTM A36 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_W-310x200x60_SG3 | [24 empty] | (59.6 kg/m)
[W-Light Steel]
6.2.1.1.4 | Load Family |  | SB-Q2 | H_SB_AR_S02_W (Light) | [25 empty] | ASTM A36 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | - Material: ( ASTM A36 ) - (30)KG/M>Weight | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( ASTM A36 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_W-250x100x22.3_SG4 | [24 empty] | (22.4 kg/m)
[W-Extra Light Steel]
6.2.1.1.5 | Load Family |  | SB-Q2 | H_SB_AR_S02_W (Extra Light) | [25 empty] | ASTM A36 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Extra Light Steel - Standard ¦ ¦ ¦ | S01AA075-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Light Steel - Standard | S01AA075-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | ( )KG/M>Weight | - Material: ( ASTM A36 ) - (10)KG/M>Weight | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Light Steel ¦ ¦ ¦ | S03AA085-00001 Main Steel Structure Erection Work Shelter/Building Extra Light Steel | S03AA085-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( ASTM A36 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
N.A
| □ Steel Beam_H |  |  | ▶ Steel Beam_H-KSD3502
[H-Extra Heavy Steel]
6.2.2.1.1 | Load Family |  | SB-Q2 | H_SB_AR_S02_H (Extra Heavy) | [25 empty] | ASTM A36 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Extra Heavy Steel - Standard ¦ ¦ ¦ | S01AA071-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Heavy Steel - Standard | S01AA071-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥( )KG/M | - Material: ( ASTM A36 ) - Weight≥( 200 ) | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Heavy Steel ¦ ¦ ¦ | S03AA081-00001 Main Steel Structure Erection Work Shelter/Building Extra Heavy Steel | S03AA081-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( ASTM A36 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
(240.0 kg/m)
[H-Heavy Steel]
6.2.2.1.2 | Load Family |  | SB-Q2 | H_SB_AR_S02_H (Heavy) | [25 empty] | ASTM A36 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | - Material: ( ASTM A36 ) - Weight≥( 90 ) | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( ASTM A36 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
(151.0 kg/m)
[H-Medium Steel]
6.2.2.1.3 | Load Family |  | SB-Q2 | H_SB_AR_S02_H (Medium) | [25 empty] | ASTM A36 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | - Material: ( ASTM A36 ) - (90)KG/M>Weight≥(30)KG/M | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 | 14.494 | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( ASTM A36 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 | 17.38 | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 | 2.908 | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) | 410.728 | M2
[5 empty] | H_SB_AR_S02_H-200x100x5.5x8_SB20 | [24 empty] | (66.0 kg/m)
|  | Template |  |  | H_SB_AR_S02_H-250x125x6x9_SB25
H_SB_AR_S02_H-250x125x6x9_SCG25
H_SB_AR_S02_H-300x150x6.5x9_SB30
H_SB_AR_S02_H-300x150x6.5x9_SCG30
H_SB_AR_S02_H-300x150x6.5x9_SG30
|  | Template |  |  | H_SB_AR_S02_H-400x200x8x13_SG40
Template
Template
[H-Light Steel]
6.2.2.1.4 | Load Family |  | SB-Q2 | H_SB_AR_S02_H (Light) | [25 empty] | ASTM A36 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | - Material: ( ASTM A36 ) - (30)KG/M>Weight | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( ASTM A36 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_H-100x100x6x8_RSG3 | [24 empty] | (17.2 kg/m)
[H-Extra Light Steel]
6.2.2.1.5 | Load Family |  | SB-Q2 | H_SB_AR_S02_H (Extra Light) | [25 empty] | ASTM A36 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Extra Light Steel - Standard ¦ ¦ ¦ | S01AA075-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Light Steel - Standard | S01AA075-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | ( )KG/M>Weight | - Material: ( ASTM A36 ) - (10)KG/M>Weight | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Light Steel ¦ ¦ ¦ | S03AA085-00001 Main Steel Structure Erection Work Shelter/Building Extra Light Steel | S03AA085-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( ASTM A36 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
N.A
| □ Steel Beam_BH |  |  | ▶ Steel Beam_H-Built Up
[BH-Extra Heavy Steel]
6.2.3.1.1 | Load Family |  | SB-Q2 | H_SB_AR_S02_BH (Extra Heavy) | [25 empty] | KS D 3515 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Extra Heavy Steel - Built up ¦ ¦ ¦ | S01AA076-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Heavy Steel - Built up | S01AA076-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Heavy Steel - Built up | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥( )KG/M | - Material: ( KS D 3515 ) - Weight≥( 200 ) | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Heavy Steel ¦ ¦ ¦ | S03AA081-00001 Main Steel Structure Erection Work Shelter/Building Extra Heavy Steel | S03AA081-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KS D 3515 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_BH-1000x300x20x40_SG1 | [24 empty] | (338 kg/m)
[BH-Heavy Steel]
6.2.3.1.2 | Load Family |  | SB-Q2 | H_SB_AR_S02_BH (Heavy) | [25 empty] | KS D 3515 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Heavy Steel - Built up ¦ ¦ ¦ | S01AA077-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Built up | S01AA077-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Built up | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | - Material: ( KS D 3515 ) - Weight≥( 90 ) | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KS D 3515 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[BH-Medium Steel]
6.2.3.1.3 | Load Family |  | SB-Q2 | H_SB_AR_S02_BH (Medium) | [25 empty] | KS D 3515 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Medium Steel - Built up ¦ ¦ ¦ | S01AA078-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Built up | S01AA078-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Built up | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | - Material: ( KS D 3515 ) - (90)KG/M>Weight≥(30)KG/M | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KS D 3515 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
| □ Steel Beam_SHS (Square Hollow Section) |  |  | ▶ Steel Beam_SHS_KSD
[SHS-Heavy Steel]
6.2.4.1.1 | Load Family |  | SB-Q2 | H_SB_AR_S02_SHS (Heavy) | [25 empty] | KSD3568 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | - Material: ( KSD3568 ) - Weight≥( 90 ) | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3568 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_SHS-350x350x12_SG1 | [24 empty] | (124.4kg/m)
[SHS-Medium Steel]
6.2.4.1.2 | Load Family |  | SB-Q2 | H_SB_AR_S02_SHS (Medium) | [25 empty] | KSD3568 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | - Material: ( KSD3568 ) - (90)KG/M>Weight≥(30)KG/M | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3568 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_SHS-250x250x12_SG2 | [24 empty] | (86.7kg/m)
[SHS-Light Steel]
6.2.4.1.3 | Load Family |  | SB-Q2 | H_SB_AR_S02_SHS (Light) | [25 empty] | KSD3568 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | - Material: ( KSD3568 ) - (30)KG/M>Weight | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3568 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_SHS-100x100x9_SG3 | [24 empty] | (24.1kg/m)
[SHS-Extra Light Steel]
6.2.4.1.4 | Load Family |  | SB-Q2 | H_SB_AR_S02_SHS (Extra Light) | [25 empty] | KSD3568 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Extra Light Steel - Standard ¦ ¦ ¦ | S01AA075-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Light Steel - Standard | S01AA075-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | ( )KG/M>Weight | - Material: ( KSD3568 ) - (10)KG/M>Weight | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Light Steel ¦ ¦ ¦ | S03AA085-00001 Main Steel Structure Erection Work Shelter/Building Extra Light Steel | S03AA085-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3568 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_SHS-40x40x1.6_SG4 | [24 empty] | (1.9kg/m)
| □ Steel Beam_RHS (Rectangular Hollow Section) |  |  | ▶ Steel Beam_RHS_KSD
[RHS-Heavy Steel]
6.2.5.1.1 | Load Family |  | SB-Q2 | H_SB_AR_S02_RHS (Heavy) | [25 empty] | KSD3568 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | - Material: ( KSD3568 ) - Weight≥( 90 ) | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3568 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_RHS-400x200x12_SG1 | [24 empty] | (105.6kg/m)
[RHS-Medium Steel]
6.2.5.1.2 | Load Family |  | SB-Q2 | H_SB_AR_S02_RHS (Medium) | [25 empty] | KSD3568 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | - Material: ( KSD3568 ) - (90)KG/M>Weight≥(30)KG/M | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3568 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_RHS-250x150x12_SG2 | [24 empty] | (67.9kg/m)
[RHS-Light Steel]
6.2.5.1.3 | Load Family |  | SB-Q2 | H_SB_AR_S02_RHS (Light) | [25 empty] | KSD3568 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | - Material: ( KSD3568 ) - (30)KG/M>Weight | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3568 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SBC_AR_S02_RHS-200x100x4.5_SG3 | [24 empty] | (20.2kg/m)
[RHS-Extra Light Steel]
6.2.5.1.4 | Load Family |  | SB-Q2 | H_SB_AR_S02_RHS (Extra Light) | [25 empty] | KSD3568 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Extra Light Steel - Standard ¦ ¦ ¦ | S01AA075-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Light Steel - Standard | S01AA075-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | ( )KG/M>Weight | - Material: ( KSD3568 ) - (10)KG/M>Weight | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Light Steel ¦ ¦ ¦ | S03AA085-00001 Main Steel Structure Erection Work Shelter/Building Extra Light Steel | S03AA085-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3568 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_RHS-50x20x1.6_SG4 | [24 empty] | (1.6kg/m)
| □ Steel Beam_CHS (Circular Hollow Section) |  |  | ▶ Steel Beam_CHS_KSD
[CHS-Extra Heavy Steel]
6.2.6.1.1 | Load Family |  | SB-Q2 | H_SB_AR_S02_CHS (Extra Heavy) | [25 empty] | KSD3566 | 일반구종용 강관 |  |  |  |  | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Extra Heavy Steel - Standard ¦ ¦ ¦ | S01AA071-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Heavy Steel - Standard | S01AA071-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥( )KG/M | - Material: ( KSD3566 ) - Weight≥( 200 ) | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Heavy Steel ¦ ¦ ¦ | S03AA081-00001 Main Steel Structure Erection Work Shelter/Building Extra Heavy Steel | S03AA081-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3566 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_CHS-1016x16_SG1 | [24 empty] | (395 kg/m)
[CHS-Heavy Steel]
6.2.6.1.2 | Load Family |  | SB-Q2 | H_SB_AR_S02_CHS (Heavy) | [25 empty] | KSD3566 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | - Material: ( KSD3566 ) - Weight≥( 90 ) | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3566 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_CHS-558.8x9.5_SG2 | [24 empty] | (129 kg/m)
[CHS-Medium Steel]
6.2.6.1.3 | Load Family |  | SB-Q2 | H_SB_AR_S02_CHS (Medium) | [25 empty] | KSD3566 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | - Material: ( KSD3566 ) - (90)KG/M>Weight≥(30)KG/M | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3566 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_CHS-267.4x6.6_SG3 | [24 empty] | (42.4 kg/m)
[CHS-Light Steel]
6.2.6.1.4 | Load Family |  | SB-Q2 | H_SB_AR_S02_CHS (Light) | [25 empty] | KSD3566 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | - Material: ( KSD3566 ) - (30)KG/M>Weight | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3566 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_CHS-165.2x4.5_SG4 | [24 empty] | (17.8 kg/m)
[CHS-Extra Light Steel]
6.2.6.1.5 | Load Family |  | SB-Q2 | H_SB_AR_S02_CHS (Extra Light) | [25 empty] | KSD3566 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Extra Light Steel - Standard ¦ ¦ ¦ | S01AA075-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Light Steel - Standard | S01AA075-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Extra Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | ( )KG/M>Weight | - Material: ( KSD3566 ) - (10)KG/M>Weight | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Extra Light Steel ¦ ¦ ¦ | S03AA085-00001 Main Steel Structure Erection Work Shelter/Building Extra Light Steel | S03AA085-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Extra Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3566 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_CHS-21.7x1.9_SG5 | [24 empty] | (0.928 kg/m)
| □ Steel Beam_Channel |  |  | ▶ Steel Beam_Channel_KSD
[C-Heavy Steel]
6.2.7.1.1 | Load Family |  | SB-Q2 | H_SB_AR_S02_C (Heavy) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | - Material: ( KSD3502 ) - Weight≥( 90 ) | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[C-Medium Steel]
6.2.7.1.2 | Load Family |  | SB-Q2 | H_SB_AR_S02_C (Medium) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | - Material: ( KSD3502 ) - (90)KG/M>Weight≥(30)KG/M | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_C-250x90x9x13_PB1 | [24 empty] | (34.6 kg/m)
|  | Template |  |  | H_SB_AR_S02_C-300x90x9x13_Stringer
[C-Light Steel]
6.2.7.1.3 | Load Family |  | SB-Q2 | H_SB_AR_S02_C (Light) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | - Material: ( KSD3502 ) - (30)KG/M>Weight | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_C-125x65x6x8_PB2 | [24 empty] | (13.4 kg/m)
| □ Steel Beam_Angle |  |  | ▶ Steel Beam_Angle_KSD
[L-Heavy Steel]
6.2.8.1.1 | Load Family |  | SB-Q2 | H_SB_AR_S02_L (Heavy) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | - Material: ( KSD3502 ) - Weight≥( 90 ) | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_L-250x250x35_PB1 | [24 empty] | (128 kg/m)
[L-Medium Steel]
6.2.8.1.2 | Load Family |  | SB-Q2 | H_SB_AR_S02_L (Medium) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | - Material: ( KSD3502 ) - (90)KG/M>Weight≥(30)KG/M | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_L-175x175x12_PB2 | [24 empty] | (31.8 kg/m)
[L-Light Steel]
6.2.8.1.3 | Load Family |  | SB-Q2 | H_SB_AR_S02_L (Light) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | - Material: ( KSD3502 ) - (30)KG/M>Weight | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_L-100x100x10_PB3 | [24 empty] | (14.9 kg/m)
| □ Steel Beam_Tee |  |  | ▶ Steel Beam_Tee_KSD
[CT-Heavy Steel]
6.2.9.1.1 | Load Family |  | SB-Q2 | H_SB_AR_S02_CT (Heavy) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | - Material: ( KSD3502 ) - Weight≥( 90 ) | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[CT-Medium Steel]
6.2.9.1.2 | Load Family |  | SB-Q2 | H_SB_AR_S02_CT (Medium) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | - Material: ( KSD3502 ) - (90)KG/M>Weight≥(30)KG/M | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_CT-170x250x9x14_PB2 | [24 empty] | (39.8 kg/m)
|  | Template |  |  | H_SB_AR_S02_CT-170x250x9x14_PLATFORM
[CT-Light Steel]
6.2.9.1.3 | Load Family |  | SB-Q2 | H_SB_AR_S02_CT (Light) | [25 empty] | KSD3502 | [5 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | - Material: ( KSD3502 ) - (30)KG/M>Weight | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | - Material: ( KSD3502 ) | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S02_CT-125x125x6x9_PB3 | [24 empty] | (12.8 kg/m)
6.3 | Steel Hori. Brace
[5 empty] | Extra Heavy Steel | 200
[5 empty] | Heavy Steel | 90
Medium Steel
[5 empty] | Light Steel | 30
[5 empty] | Extra Light Steel | 10
| □ Steel Hori. Brace_Angle |  |  | ▶ Steel Hori. Brace_Angle_KSD
[L-HB-Heavy Steel]
6.3.1.1.1 | Load Family |  | SB-Q2 | H_SB_AR_S03_L (Heavy) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S03_L-250x250x35_HBR1 | [24 empty] | (128 kg/m)
[L-HB-Medium Steel]
6.3.1.1.2 | Load Family |  | SB-Q2 | H_SB_AR_S03_L (Medium) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S03_L-175x175x12_HBR2 | [24 empty] | (31.8 kg/m)
[L-HB-Light Steel]
6.3.1.1.3 | Load Family |  | SB-Q2 | H_SB_AR_S03_L (Light) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 | 1.278 | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 | 1.528 | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 | 0.256 | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) | 41.132 | M2
[5 empty] | H_SB_AR_S03_L-100x100x7_HB13 | [24 empty] | (14.9 kg/m)
| □ Steel Hori. Brace_CHS (Circular Hollow Section) |  |  | ▶ Steel Hori. Brace_CHS_KSD
[CHS-HB-Heavy Steel]
6.3.2.1.1 | Load Family |  | SB-Q2 | H_SB_AR_S03_CHS (Heavy) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S03_CHS-558.8x9.5_HBR1 | [24 empty] | (129 kg/m)
[CHS-HB-Medium Steel]
6.3.2.1.2 | Load Family |  | SB-Q2 | H_SB_AR_S03_CHS (Medium) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S03_CHS-267.4x6.6_HBR2 | [24 empty] | (42.4 kg/m)
[CHS-HB-Light Steel]
6.3.2.1.3 | Load Family |  | SB-Q2 | H_SB_AR_S03_CHS (Light) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S03_CHS-165.2x4.5_HBR3 | [24 empty] | (17.8 kg/m)
| □ Steel Hori. Brace_Double Angle |  |  | ▶ Steel Hori. Brace_2Ls_KSD
[2Ls-HB-Heavy Steel]
6.3.3.1.1 | Load Family |  | SB-Q2 | H_SB_AR_S03_2Ls (Heavy) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S03_2Ls-200x200x15_HBR1 | [24 empty] | (90.7 kg/m)
[2Ls-HB-Medium Steel]
6.3.3.1.2 | Load Family |  | SB-Q2 | H_SB_AR_S03_2Ls (Medium) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S03_2Ls-100x100x13_HBR2 | [24 empty] | (38.2 kg/m)
[2Ls-HB-Light Steel]
6.3.3.1.3 | Load Family |  | SB-Q2 | H_SB_AR_S03_2Ls (Light) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S03_2Ls-75x75x6_HBR3 | [24 empty] | (13.7 kg/m)
6.4 | Steel Ver. Brace
[5 empty] | Extra Heavy Steel | 200
[5 empty] | Heavy Steel | 90
Medium Steel
[5 empty] | Light Steel | 30
[5 empty] | Extra Light Steel | 10
| □ Steel Ver. Brace_Angle |  |  | ▶ Steel Ver. Brace_Angle_KSD
[L-VB-Heavy Steel]
6.4.1.1.1 | Load Family |  | SB-Q2 | H_SB_AR_S04_L (Heavy) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S04_L-250x250x35_VBR1 | [24 empty] | (128 kg/m)
[L-VB-Medium Steel]
6.4.1.1.2 | Load Family |  | SB-Q2 | H_SB_AR_S04_L (Medium) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S04_L-175x175x12_VBR2 | [24 empty] | (31.8 kg/m)
[L-VB-Light Steel]
6.4.1.1.3 | Load Family |  | SB-Q2 | H_SB_AR_S04_L (Light) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S04_L-100x100x10_VBR3 | [24 empty] | (14.9 kg/m)
| □ Steel Ver. Brace_CHS (Circular Hollow Section) |  |  | ▶ Steel Ver. Brace_CHS_KSD
[CHS-VB-Heavy Steel]
6.4.2.1.1 | Load Family |  | SB-Q2 | H_SB_AR_S04_CHS (Heavy) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S04_CHS-558.8x9.5_VBR1 | [24 empty] | (129 kg/m)
[CHS-VB-Medium Steel]
6.4.2.1.2 | Load Family |  | SB-Q2 | H_SB_AR_S04_CHS (Medium) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S04_CHS-267.4x6.6_VBR2 | [24 empty] | (42.4 kg/m)
[CHS-VB-Light Steel]
6.4.2.1.3 | Load Family |  | SB-Q2 | H_SB_AR_S04_CHS (Light) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S04_CHS-165.2x4.5_VBR3 | [24 empty] | (17.8 kg/m)
| □ Steel Ver. Brace_Double Angle |  |  | ▶ Steel Ver. Brace_2Ls_KSD
[2Ls-VB-Heavy Steel]
6.4.3.1.1 | Load Family |  | SB-Q2 | H_SB_AR_S04_2Ls (Heavy) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Heavy Steel - Standard ¦ ¦ ¦ | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Heavy Steel ¦ ¦ ¦ | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S04_2Ls-200x200x15_VBR1 | [24 empty] | (90.7 kg/m)
[2Ls-VB-Medium Steel]
6.4.3.1.2 | Load Family |  | SB-Q2 | H_SB_AR_S04_2Ls (Medium) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Medium Steel - Standard ¦ ¦ ¦ | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Medium Steel ¦ ¦ ¦ | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Medium Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S04_2Ls-100x100x13_VBR2 | [24 empty] | (38.2 kg/m)
[2Ls-VB-Light Steel]
6.4.3.1.3 | Load Family |  | SB-Q2 | H_SB_AR_S04_2Ls (Light) | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Light Steel - Standard ¦ ¦ ¦ | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Light Steel ¦ ¦ ¦ | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Light Steel | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * (1+SE) / 1000 | = ( (L/1000) * W ) * (1+SE) / 1000 |  | TON
|  |  |  | 철골제작할증 | Plates - Gusset, Stiffener, ETC ¦ ¦ ¦ | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W ) * SE / 1000 | = ( (L/1000) * W ) * SE / 1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) * (1+PE) | = P * (L/1000) * (1+PE) |  | M2
[5 empty] | H_SB_AR_S04_2Ls-75x75x6_VBR3 | [24 empty] | (13.7 kg/m)
6.5 | Steel Purlin
| □ Steel Purlin_LC |  |  | ▶ Steel Purlin_LC_KSD
6.5.1.1.1 | Load Family |  | SB-Q2 | H_SB_AR_B03_LC | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Girth & Purlin ¦ ¦ ¦ | S01AA007-00001 Main Steel Structure Fabrication Work Shelter/Building Girth & Purlin | S01AA007-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Girth & Purlin | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 | 3.788 | TON
|  |  |  | 철골설치 | Girth & Purlin ¦ ¦ ¦ | S03AA007-00001 Main Steel Structure Erection Work Shelter/Building Girth & Purlin | S03AA007-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Girth & Purlin | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 | 3.788 | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) | = P * (L/1000) | 310.216 | M2
H_SB_AR_B03_LC-150x75x20x3.2_Purlin
H_SB_AR_B03_LC-150x75x20x3.2_Trim
6.6 | Steel Girth
| □ Steel Girth_LC |  |  | ▶ Steel Girth_LC_KSD
6.6.1.1.1 | Load Family |  | SB-Q2 | H_SB_AR_B04_LC | [31 empty] | 산출기준 >> [Steel Beam]
|  |  |  | 철골제작 | Girth & Purlin ¦ ¦ ¦ | S01AA007-00001 Main Steel Structure Fabrication Work Shelter/Building Girth & Purlin | S01AA007-00001 |  | TON | Main Steel Structure Fabrication Work | Shelter/Building | Girth & Purlin | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 철골설치 | Girth & Purlin ¦ ¦ ¦ | S03AA007-00001 Main Steel Structure Erection Work Shelter/Building Girth & Purlin | S03AA007-00001 |  | TON | Main Steel Structure Erection Work | Shelter/Building | Girth & Purlin | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = ( (L/1000) * W )/1000 | = ( (L/1000) * W )/1000 |  | TON
|  |  |  | 도장 | for Non-Fireproofed Steel Surface ¦ ¦ ¦ | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 |  | M2 | Steel Structure Paint Work | Shelter/Building | for Non-Fireproofed Steel Surface | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = P * (L/1000) | = P * (L/1000) |  | M2
H_SB_AR_B04_LC-200x75x25x4.0_Girth
B=> W
H=> D
B=> W
H=> D

## 7.Ceilings
[Family List] - Ceilings |  |  |  |  | 표준구성도로 가기
NO | Family Category | Building Tag | Q'ty Cal Type Tag | Standard Type | Family Type Name | Work Master Code /w Description | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Description | 입찰_ 물량산출식 | 실행_ 물량산출식 | Quantity |  | Remark (물량관련)
7 | Ceilings [CE]
7.1 | Basic Ceiling (System Family)
| □ Basic Ceiling |  |  | ▶ Simple Ceiling
7.1.1.1.1 | System Family |  |  | H_CE_AR_B09_Acrylic Emulsion Paint
[5 empty] | Ceiling Painting ¦ Acrylic Emulsion Paint ¦ ¦ | A04AM079-00001 Finishing Work Painting Work Ceiling Painting Acrylic Emulsion Paint | A04AM079-00001 |  | M2 | Finishing Work | Painting Work | Ceiling Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | _by Rooms | _by Rooms |  | M2
H_CE_AR_B09_Acrylic Emulsion Paint
| □ Compound Ceiling - normal |  |  | ▶ Compound Ceiling
7.1.2.1.1 | System Family |  | CE-Q1 | H_CE_AR_B09_Acoustic Ceiling_T Bar | [25 empty] | Suspended Ceiling / T Bar | [5 empty] | 산출기준 >> [ 천장 일반 산출 ]
[5 empty] | Acoustic Tiled Ceiling System ¦ T-Bar System ¦ ¦ | A04AS190-00002 Finishing Work Exterior/Interior Finish Work Acoustic Tiled Ceiling System T-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS190-00002 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Acoustic Tiled Ceiling System | T-Bar System | 0 | 0 | 0 | 0 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | 0 | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=( 600 )mm x (600 )mm | _by Rooms | _by Rooms |  | M2
H_CE_AR_B09_Acoustic Ceiling_T Bar_600x600x9T
7.1.2.1.2 | System Family |  | CE-Q1 | H_CE_AR_B09_Moisture Resistant Ceiling_M Bar | [25 empty] | Suspended Ceiling / M Bar | [5 empty] | 산출기준 >> [ 천장 일반 산출 ]
[5 empty] | Moisture Resistant Tiled Ceiling System ¦ M-Bar System ¦ ¦ | A04AS191-00001 Finishing Work Exterior/Interior Finish Work Moisture Resistant Tiled Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS191-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Moisture Resistant Tiled Ceiling System | M-Bar System | 0 | 0 | 0 | 0 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | 0 | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | Tile Size=( 600 )mm x (1200 )mm | _by Rooms | _by Rooms |  | M2
H_CE_AR_B09_Moisture Resistant Ceiling_M Bar_600x1200x9T

## 8.Doors
[Family List] - Doors |  |  |  |  | 표준구성도로 가기
NO | Family Category | Building Tag | Q'ty Cal Type Tag | Standard Type | Family Type Name | Work Master Code /w Description |  | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Description | 입찰_ 물량산출식 | 실행_ 물량산출식 | Quantity |  | Remark (물량관련)
8 | Doors [DR]
8.1 | Single Door
| □ Single Door - normal |  |  | ▶ Single Door_Steel
8.1.1.1.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Single Door_Steel |  | SD11 | # |  |  |  | Fire Protective Rating: N/A, Single Door |  | Fire Protective Rating: 0.5-hr, Single Door |  | Fire Protective Rating: 1-hr, Single Door |  | Fire Protective Rating: 1.5-hrs, Single Door |  | Fire Protective Rating: 2-hrs, Single Door |  | Fire Protective Rating: 3-hrs, Single Door | [15 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR099 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) | A04AR099
[5 empty] | H_DR_AR_B12_Single Door_Steel_W1000xH2100_0Hr | A04AR099-00001 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | 00001 | A04AR099-00001 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 1000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Single Door_Steel_W1000xH2100_0.5Hr | A04AR099-00003 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 0.5-hr, Single Door w/ Hardware & Accessories | 00003 | A04AR099-00003 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 0.5-hr, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.1.1.1.2 | System Family |  | DR-Q1 | H_DR_AR_B12_Single Door_Steel_Vision |  | SD12 | # |  |  |  | Fire Protective Rating: N/A, Single Door |  | Fire Protective Rating: 0.5-hr, Single Door |  | Fire Protective Rating: 1-hr, Single Door |  | Fire Protective Rating: 1.5-hrs, Single Door |  | Fire Protective Rating: 2-hrs, Single Door |  | Fire Protective Rating: 3-hrs, Single Door | [15 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR101 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR101
[5 empty] | H_DR_AR_B12_Single Door_Steel_Vision_W1000xH2100_0Hr | A04AR101-00001 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | 00001 | A04AR101-00001 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: N/A, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 1000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Single Door_Steel_Vision_W1000xH2100_1.0Hr | A04AR101-00005 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1-hr, Single Door w/ Hardware & Accessories | 00005 | A04AR101-00005 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: 1-hr, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.1.1.1.3 | System Family |  | DR-Q1 | H_DR_AR_B12_Single Door_Steel_Panic |  | SD13 | # |  |  |  | Fire Protective Rating: N/A, Single Door |  | Fire Protective Rating: 0.5-hr, Single Door |  | Fire Protective Rating: 1-hr, Single Door |  | Fire Protective Rating: 1.5-hrs, Single Door |  | Fire Protective Rating: 2-hrs, Single Door |  | Fire Protective Rating: 3-hrs, Single Door | [15 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR103 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | A04AR103
[5 empty] | H_DR_AR_B12_Single Door_Steel_Panic_W1000xH2100_0Hr | A04AR103-00001 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | 00001 | A04AR103-00001 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: N/A, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 1000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Single Door_Steel_Panic_W1000xH2100_1.5Hr | A04AR103-00007 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: 1.5-hrs, Single Door w/ Hardware & Accessories | 00007 | A04AR103-00007 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: 1.5-hrs, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.1.1.1.4 | System Family |  | DR-Q1 | H_DR_AR_B12_Single Door_Steel_Vision_Panic |  | SD14 | # |  |  |  | Fire Protective Rating: N/A, Single Door |  | Fire Protective Rating: 0.5-hr, Single Door |  | Fire Protective Rating: 1-hr, Single Door |  | Fire Protective Rating: 1.5-hrs, Single Door |  | Fire Protective Rating: 2-hrs, Single Door | [17 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR105 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR105
[5 empty] | H_DR_AR_B12_Single Door_Steel_Vision_Panic_W1000xH2100_0Hr | A04AR105-00001 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | 00001 | A04AR105-00001 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: N/A, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 1000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Single Door_Steel_Vision_Panic_W1000xH2100_2.0Hr | A04AR105-00009 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 2-hrs, Single Door w/ Hardware & Accessories | 00009 | A04AR105-00009 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: 2-hrs, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Single Door - normal |  |  | ▶ Single Door_Blast
8.1.1.2.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Single Door_Blast |  | SD21 | # |  |  |  | Fire Protective Rating: N/A, Single Door |  | Fire Protective Rating: 0.5-hr, Single Door |  | Fire Protective Rating: 1-hr, Single Door |  | Fire Protective Rating: 1.5-hrs, Single Door |  | Fire Protective Rating: 2-hrs, Single Door |  | Fire Protective Rating: 3-hrs, Single Door | [15 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR107 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) | A04AR107
[5 empty] | H_DR_AR_B12_Single Door_Blast_W1000xH2100_0Hr | A04AR107-00001 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | 00001 | A04AR107-00001 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | W x H=( 1000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Single Door_Blast_W1000xH2100_1.0Hr | A04AR107-00005 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Single Door w/ Hardware & Accessories | 00005 | A04AR107-00005 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1-hr, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.1.1.2.2 | System Family |  | DR-Q1 | H_DR_AR_B12_Single Door_Blast_Panic |  | SD22 | # |  |  |  | Fire Protective Rating: N/A, Single Door |  | Fire Protective Rating: 0.5-hr, Single Door |  | Fire Protective Rating: 1-hr, Single Door |  | Fire Protective Rating: 1.5-hrs, Single Door |  | Fire Protective Rating: 2-hrs, Single Door |  | Fire Protective Rating: 3-hrs, Single Door | [15 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR109 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR109
[5 empty] | H_DR_AR_B12_Single Door_Blast_Panic_W1000xH2100_0Hr | A04AR109-00001 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | 00001 | A04AR109-00001 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | Fire Protective Rating: N/A, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | W x H=( 1000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Single Door_Blast_Panic_W1000xH2100_1.5Hr | A04AR109-00007 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 1.5-hrs, Single Door w/ Hardware & Accessories | 00007 | A04AR109-00007 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | Fire Protective Rating: 1.5-hrs, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Single Door - normal |  |  | ▶ Single Door_Aluminum
8.1.1.3.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Single Door_AL |  | SD31 | # |  |  |  | Fire Protective Rating: N/A, Single Door |  | Fire Protective Rating: 0.5-hr, Single Door |  | Fire Protective Rating: 1-hr, Single Door |  | Fire Protective Rating: 1.5-hrs, Single Door | [19 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR111 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) | A04AR111
[5 empty] | H_DR_AR_B12_Single Door_AL_W1000xH2100_0Hr | A04AR111-00001 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | 00001 | A04AR111-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Door w/ Aluminum Frame (UoM: EA) | Fire Protective Rating: N/A, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 1000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Single Door_AL_W1000xH2100_0.5Hr | A04AR111-00003 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: 0.5-hr, Single Door w/ Hardware & Accessories | 00003 | A04AR111-00003 |  | EA | Finishing Work | Door & Window Work | Aluminum Door w/ Aluminum Frame (UoM: EA) | Fire Protective Rating: 0.5-hr, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.1.1.3.2 | System Family |  | DR-Q1 | H_DR_AR_B12_Single Door_AL_Vision |  | SD32 | # |  |  |  | Fire Protective Rating: N/A, Single Door |  | Fire Protective Rating: 0.5-hr, Single Door |  | Fire Protective Rating: 1-hr, Single Door |  | Fire Protective Rating: 1.5-hrs, Single Door | [19 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR113 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR113
[5 empty] | H_DR_AR_B12_Double Door_AL_Vision_W2000xH2100_0Hr | A04AR113-00001 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | 00001 | A04AR113-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: N/A, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 1000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Double Door_AL_Vision_W2000xH2100_1.0Hr | A04AR113-00005 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1-hr, Single Door w/ Hardware & Accessories | 00005 | A04AR113-00005 |  | EA | Finishing Work | Door & Window Work | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: 1-hr, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.1.1.3.3 | System Family |  | DR-Q1 | H_DR_AR_B12_Single Door_AL_Panic |  | SD33 | # |  |  |  | Fire Protective Rating: N/A, Single Door |  | Fire Protective Rating: 0.5-hr, Single Door |  | Fire Protective Rating: 1-hr, Single Door |  | Fire Protective Rating: 1.5-hrs, Single Door | [19 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR115 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | A04AR115
[5 empty] | H_DR_AR_B12_Single Door_AL_Panic_W1000xH2100_0Hr | A04AR115-00001 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | 00001 | A04AR115-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | Fire Protective Rating: N/A, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 1000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Single Door_AL_Panic_W1000xH2100_1.5Hr | A04AR115-00007 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) Fire Protective Rating: 1.5-hrs, Single Door w/ Hardware & Accessories | 00007 | A04AR115-00007 |  | EA | Finishing Work | Door & Window Work | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | Fire Protective Rating: 1.5-hrs, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.1.1.3.4 | System Family |  | DR-Q1 | H_DR_AR_B12_Single Door_AL_Vision_Panic |  | SD34 | # |  |  |  | Fire Protective Rating: N/A, Single Door |  | Fire Protective Rating: 0.5-hr, Single Door |  | Fire Protective Rating: 1-hr, Single Door |  | Fire Protective Rating: 1.5-hrs, Single Door | [19 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR117 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR117
[5 empty] | H_DR_AR_B12_Single Door_AL_Vision_Panic_W1000xH2100_0Hr | A04AR117-00001 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | 00001 | A04AR117-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: N/A, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 1000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Single Door_AL_Vision_Panic_W1000xH2100_1.5Hr | A04AR117-00007 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1.5-hrs, Single Door w/ Hardware & Accessories | 00007 | A04AR117-00007 |  | EA | Finishing Work | Door & Window Work | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: 1.5-hrs, Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Single Door - normal |  |  | ▶ Single Door_Glass
8.1.1.4.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Single Door_Glass |  | SD41 | # |  |  |  | Single Door | [25 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR119 Finishing Work Door & Window Work Glass Door w/ SST Frame (UoM: EA) | A04AR119
[5 empty] | H_DR_AR_B12_Single Door_Glass_W1000xH2100 | A04AR119-00001 Finishing Work Door & Window Work Glass Door w/ SST Frame (UoM: EA) Single Door w/ Hardware & Accessories | 00001 | A04AR119-00001 |  | EA | Finishing Work | Door & Window Work | Glass Door w/ SST Frame (UoM: EA) | Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 1000 )mm x (2100 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Single Door - normal |  |  | ▶ Single Door_SST
8.1.1.5.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Single Door_SST |  | SD51 | # |  |  |  | Single Door | [25 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR121 Finishing Work Door & Window Work Stainless Steel Door w/ SST Frame (UoM: EA) | A04AR121
[5 empty] | H_DR_AR_B12_Single Door_SST_W1000xH2100 | A04AR121-00001 Finishing Work Door & Window Work Stainless Steel Door w/ SST Frame (UoM: EA) Single Door w/ Hardware & Accessories | 00001 | A04AR121-00001 |  | EA | Finishing Work | Door & Window Work | Stainless Steel Door w/ SST Frame (UoM: EA) | Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 1000 )mm x (2100 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Single Door - normal |  |  | ▶ Single Door_Wood
8.1.1.6.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Single Door_Wood |  | SD61 | # |  |  |  | Single Door | [25 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR123 Finishing Work Door & Window Work Wood Door w/ Wood Frame (UoM: EA) | A04AR123
[5 empty] | H_DR_AR_B12_Single Door_Wood_W1000xH2100 | A04AR123-00001 Finishing Work Door & Window Work Wood Door w/ Wood Frame (UoM: EA) Single Door w/ Hardware & Accessories | 00001 | A04AR123-00001 |  | EA | Finishing Work | Door & Window Work | Wood Door w/ Wood Frame (UoM: EA) | Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 1000 )mm x (2100 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.1.1.6.2 | System Family |  | DR-Q1 | H_DR_AR_B12_Single Door_Wood_Vision |  | SD62 | # |  |  |  | Single Door | [25 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR125 Finishing Work Door & Window Work Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR125
[5 empty] | H_DR_AR_B12_Single Door_Wood_Vision_W1000xH2100 | A04AR125-00001 Finishing Work Door & Window Work Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: EA) Single Door w/ Hardware & Accessories | 00001 | A04AR125-00001 |  | EA | Finishing Work | Door & Window Work | Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: EA) | Single Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 1000 )mm x (2100 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Single Door - normal |  |  | ▶ Single Door_uPVC
8.1.1.7.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Single Door_uPVC |  | SD71 | # | [29 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR150 Finishing Work Door & Window Work uPVC Door w/ uPVC Frame (UoM: EA) | A04AR150
[5 empty] | H_DR_AR_B12_Single Door_uPVC_W1000xH2100 | A04AR150-00001 Finishing Work Door & Window Work uPVC Door w/ uPVC Frame (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR150-00001 |  | EA | Finishing Work | Door & Window Work | uPVC Door w/ uPVC Frame (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 1000 )mm x (2100 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.2 | Double Door
| □ Double Door - normal |  |  | ▶ Double Door_Steel
8.2.1.1.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_Steel |  | DD11 | # |  |  |  |  | Fire Protective Rating: N/A, Double Door |  | Fire Protective Rating: 0.5-hr, Double Door |  | Fire Protective Rating: 1-hr, Double Door |  | Fire Protective Rating: 1.5-hrs, Double Door |  | Fire Protective Rating: 2-hrs, Double Door |  | Fire Protective Rating: 3-hrs, Double Door | [14 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR099 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) | A04AR099
[5 empty] | H_DR_AR_B12_Double Door_Steel_W2200xH2280_No FR_SD1 | A04AR099-00002 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | 00002 | A04AR099-00002 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 3000 )mm x ( 3000 )mm | =Q | =Q |  | EA
[6 empty] | A04AR099-00006 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | 00006 | A04AR099-00006 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1-hr, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x ( 2100 )mm | =Q | =Q |  | EA
[6 empty] | A04AR099-00010 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 2-hrs, Double Door w/ Hardware & Accessories | 00010 | A04AR099-00010 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 2-hrs, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2400 )mm x ( 2800 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.2.1.1.2 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_Steel_Vision |  | DD12 | # |  |  |  |  | Fire Protective Rating: N/A, Double Door |  | Fire Protective Rating: 0.5-hr, Double Door |  | Fire Protective Rating: 1-hr, Double Door |  | Fire Protective Rating: 1.5-hrs, Double Door |  | Fire Protective Rating: 2-hrs, Double Door |  | Fire Protective Rating: 3-hrs, Double Door | [14 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR101 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR101
[5 empty] | H_DR_AR_B12_Double Door_Steel_Vision_W2000xH2100_0Hr | A04AR101-00002 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | 00002 | A04AR101-00002 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: N/A, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Double Door_Steel_Vision_W2000xH2100_1.0Hr | A04AR101-00006 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | 00006 | A04AR101-00006 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: 1-hr, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.2.1.1.3 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_Steel_Panic |  | DD13 | # |  |  |  |  | Fire Protective Rating: N/A, Double Door |  | Fire Protective Rating: 0.5-hr, Double Door |  | Fire Protective Rating: 1-hr, Double Door |  | Fire Protective Rating: 1.5-hrs, Double Door |  | Fire Protective Rating: 2-hrs, Double Door |  | Fire Protective Rating: 3-hrs, Double Door | [14 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR103 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | A04AR103
[5 empty] | H_DR_AR_B12_Double Door_Steel_Panic_W2000xH2100_0Hr | A04AR103-00002 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | 00002 | A04AR103-00002 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: N/A, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Double Door_Steel_Panic_W2000xH2100_2.0Hr | A04AR103-00010 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: 2-hrs, Double Door w/ Hardware & Accessories | 00010 | A04AR103-00010 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: 2-hrs, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.2.1.1.4 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_Steel_Vision_Panic |  | DD14 | # |  |  |  |  | Fire Protective Rating: N/A, Double Door |  | Fire Protective Rating: 0.5-hr, Double Door |  | Fire Protective Rating: 1-hr, Double Door |  | Fire Protective Rating: 1.5-hrs, Double Door |  | Fire Protective Rating: 2-hrs, Double Door | [16 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR105 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR105
[5 empty] | H_DR_AR_B12_Double Door_Steel_Vision_Panic_W2000xH2100_0Hr | A04AR105-00002 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | 00002 | A04AR105-00002 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: N/A, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Double Door_Steel_Vision_Panic_W2000xH2100_1.0Hr | A04AR105-00006 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | 00006 | A04AR105-00006 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: 1-hr, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Double Door - normal |  |  | ▶ Double Door_Blast
8.2.1.2.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_Blast |  | DD21 | # |  |  |  |  | Fire Protective Rating: N/A, Double Door |  | Fire Protective Rating: 0.5-hr, Double Door |  | Fire Protective Rating: 1-hr, Double Door |  | Fire Protective Rating: 1.5-hrs, Double Door |  | Fire Protective Rating: 2-hrs, Double Door |  | Fire Protective Rating: 3-hrs, Double Door | [14 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR107 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) | A04AR107
[5 empty] | H_DR_AR_B12_Double Door_Blast_W2000xH2100_0Hr | A04AR107-00002 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | 00002 | A04AR107-00002 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | W x H=( 2000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Double Door_Blast_W2000xH2100_1.0Hr | A04AR107-00006 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | 00006 | A04AR107-00006 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1-hr, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.2.1.2.2 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_Blast_Panic |  | DD22 | # |  |  |  |  | Fire Protective Rating: N/A, Double Door |  | Fire Protective Rating: 0.5-hr, Double Door |  | Fire Protective Rating: 1-hr, Double Door |  | Fire Protective Rating: 1.5-hrs, Double Door |  | Fire Protective Rating: 2-hrs, Double Door |  | Fire Protective Rating: 3-hrs, Double Door | [14 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR109 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR109
[5 empty] | H_DR_AR_B12_Double Door_Blast_Panic_W2000xH2100_0Hr | A04AR109-00002 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | 00002 | A04AR109-00002 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | Fire Protective Rating: N/A, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | W x H=( 2000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Double Door_Blast_Panic_W2000xH2100_1.0Hr | A04AR109-00006 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | 00006 | A04AR109-00006 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | Fire Protective Rating: 1-hr, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Double Door - normal |  |  | ▶ Double Door_Aluminum
8.2.1.3.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_AL |  | DD31 | # |  |  |  |  | Fire Protective Rating: N/A, Double Door |  | Fire Protective Rating: 0.5-hr, Double Door |  | Fire Protective Rating: 1-hr, Double Door |  | Fire Protective Rating: 1.5-hrs, Double Door | [18 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR111 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) | A04AR111
[5 empty] | H_DR_AR_B12_Double Door_AL_W2000xH2100_0Hr | A04AR111-00002 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | 00002 | A04AR111-00002 |  | EA | Finishing Work | Door & Window Work | Aluminum Door w/ Aluminum Frame (UoM: EA) | Fire Protective Rating: N/A, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Double Door_AL_W2000xH2100_1.0Hr | A04AR111-00006 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | 00006 | A04AR111-00006 |  | EA | Finishing Work | Door & Window Work | Aluminum Door w/ Aluminum Frame (UoM: EA) | Fire Protective Rating: 1-hr, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.2.1.3.2 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_AL_Vision |  | DD32 | # |  |  |  |  | Fire Protective Rating: N/A, Double Door |  | Fire Protective Rating: 0.5-hr, Double Door |  | Fire Protective Rating: 1-hr, Double Door |  | Fire Protective Rating: 1.5-hrs, Double Door | [18 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR113 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR113
[5 empty] | H_DR_AR_B12_Double Door_AL_Vision_W2000xH2100_0Hr | A04AR113-00002 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | 00002 | A04AR113-00002 |  | EA | Finishing Work | Door & Window Work | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: N/A, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Double Door_AL_Vision_W2000xH2100_1.0Hr | A04AR113-00006 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | 00006 | A04AR113-00006 |  | EA | Finishing Work | Door & Window Work | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: 1-hr, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.2.1.3.3 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_AL_Panic |  | DD33 | # |  |  |  |  | Fire Protective Rating: N/A, Double Door |  | Fire Protective Rating: 0.5-hr, Double Door |  | Fire Protective Rating: 1-hr, Double Door |  | Fire Protective Rating: 1.5-hrs, Double Door | [18 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR115 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | A04AR115
[5 empty] | H_DR_AR_B12_Double Door_AL_Panic_W2000xH2100_0Hr | A04AR115-00002 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | 00002 | A04AR115-00002 |  | EA | Finishing Work | Door & Window Work | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | Fire Protective Rating: N/A, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Double Door_AL_Panic_W2000xH2100_1.0Hr | A04AR115-00006 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | 00006 | A04AR115-00006 |  | EA | Finishing Work | Door & Window Work | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | Fire Protective Rating: 1-hr, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.2.1.3.4 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_AL_Vision_Panic |  | DD34 | # |  |  |  |  | Fire Protective Rating: N/A, Double Door |  | Fire Protective Rating: 0.5-hr, Double Door |  | Fire Protective Rating: 1-hr, Double Door |  | Fire Protective Rating: 1.5-hrs, Double Door | [18 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR117 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR117
[5 empty] | H_DR_AR_B12_Double Door_AL_Vision_Panic_W2000xH2100_0Hr | A04AR117-00002 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | 00002 | A04AR117-00002 |  | EA | Finishing Work | Door & Window Work | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: N/A, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (2100 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Double Door_AL_Vision_Panic_W2000xH2100_1.0Hr | A04AR117-00006 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | 00006 | A04AR117-00006 |  | EA | Finishing Work | Door & Window Work | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: 1-hr, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Double Door - normal |  |  | ▶ Double Door_Glass
8.2.1.4.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_Glass |  | DD41 | # |  |  |  |  | Double Door | [24 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR119 Finishing Work Door & Window Work Glass Door w/ SST Frame (UoM: EA) | A04AR119
[5 empty] | H_DR_AR_B12_Double Door_Glass_W2000xH2100 | A04AR119-00002 Finishing Work Door & Window Work Glass Door w/ SST Frame (UoM: EA) Double Door w/ Hardware & Accessories | 00002 | A04AR119-00002 |  | EA | Finishing Work | Door & Window Work | Glass Door w/ SST Frame (UoM: EA) | Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (2100 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Double Door - normal |  |  | ▶ Double Door_SST
8.2.1.5.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_SST |  | DD51 | # |  |  |  |  | Double Door | [24 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR121 Finishing Work Door & Window Work Stainless Steel Door w/ SST Frame (UoM: EA) | A04AR121
[5 empty] | H_DR_AR_B12_Double Door_SST_W2000xH2100 | A04AR121-00002 Finishing Work Door & Window Work Stainless Steel Door w/ SST Frame (UoM: EA) Double Door w/ Hardware & Accessories | 00002 | A04AR121-00002 |  | EA | Finishing Work | Door & Window Work | Stainless Steel Door w/ SST Frame (UoM: EA) | Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (2100 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Double Door - normal |  |  | ▶ Double Door_Wood
8.2.1.6.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_Wood |  | DD61 | # |  |  |  |  | Double Door | [24 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR123 Finishing Work Door & Window Work Wood Door w/ Wood Frame (UoM: EA) | A04AR123
[5 empty] | H_DR_AR_B12_Double Door_Wood_W2000xH2100 | A04AR123-00002 Finishing Work Door & Window Work Wood Door w/ Wood Frame (UoM: EA) Double Door w/ Hardware & Accessories | 00002 | A04AR123-00002 |  | EA | Finishing Work | Door & Window Work | Wood Door w/ Wood Frame (UoM: EA) | Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (2100 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.2.1.6.2 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_Wood_Vision |  | DD62 | # |  |  |  |  | Double Door | [24 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR125 Finishing Work Door & Window Work Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR125
[5 empty] | H_DR_AR_B12_Double Door_Wood_Vision_W2000xH2100 | A04AR125-00002 Finishing Work Door & Window Work Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: EA) Double Door w/ Hardware & Accessories | 00002 | A04AR125-00002 |  | EA | Finishing Work | Door & Window Work | Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: EA) | Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (2100 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.3 | Double Door + Transsom
| □ Double Door + Transsom - normal |  |  | ▶ Double Door_Steel_Transsom
8.3.1.1.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_Steel_Transsom |  | DDT11 | # |  |  |  |  | Fire Protective Rating: N/A, Double Door |  | Fire Protective Rating: 0.5-hr, Double Door |  | Fire Protective Rating: 1-hr, Double Door |  | Fire Protective Rating: 1.5-hrs, Double Door |  | Fire Protective Rating: 2-hrs, Double Door |  | Fire Protective Rating: 3-hrs, Double Door | [14 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR099 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) | A04AR099
[5 empty] | H_DR_AR_B12_Double Door_Steel_Transsom_W2000xH3000_0Hr | A04AR099-00002 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | 00002 | A04AR099-00002 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (3000 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Double Door_Steel_Transsom_W2000xH3000_1.0Hr | A04AR099-00006 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | 00006 | A04AR099-00006 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1-hr, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.3.1.1.2 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_Steel_Vision_Transsom |  | DDT12 | # |  |  |  |  | Fire Protective Rating: N/A, Double Door |  | Fire Protective Rating: 0.5-hr, Double Door |  | Fire Protective Rating: 1-hr, Double Door |  | Fire Protective Rating: 1.5-hrs, Double Door |  | Fire Protective Rating: 2-hrs, Double Door |  | Fire Protective Rating: 3-hrs, Double Door | [14 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR101 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR101
[5 empty] | H_DR_AR_B12_Double Door_Steel_Vision_Transsom_W2000xH3000_0Hr | A04AR101-00002 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | 00002 | A04AR101-00002 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: N/A, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (3000 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Double Door_Steel_Vision_Transsom_W2000xH3000_1.0Hr | A04AR101-00006 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | 00006 | A04AR101-00006 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: 1-hr, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.3.1.1.3 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_Steel_Panic_Transsom |  | DDT13 | # |  |  |  |  | Fire Protective Rating: N/A, Double Door |  | Fire Protective Rating: 0.5-hr, Double Door |  | Fire Protective Rating: 1-hr, Double Door |  | Fire Protective Rating: 1.5-hrs, Double Door |  | Fire Protective Rating: 2-hrs, Double Door |  | Fire Protective Rating: 3-hrs, Double Door | [14 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR103 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | A04AR103
[5 empty] | H_DR_AR_B12_Double Door_Steel_Panic_Transsom_W2000xH3000_0Hr | A04AR103-00002 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | 00002 | A04AR103-00002 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: N/A, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (3000 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Double Door_Steel_Panic_Transsom_W2000xH3000_1.0Hr | A04AR103-00006 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | 00006 | A04AR103-00006 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: 1-hr, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.3.1.1.4 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_Steel_Vision_Panic_Transsom |  | DDT14 | # |  |  |  |  | Fire Protective Rating: N/A, Double Door |  | Fire Protective Rating: 0.5-hr, Double Door |  | Fire Protective Rating: 1-hr, Double Door |  | Fire Protective Rating: 1.5-hrs, Double Door |  | Fire Protective Rating: 2-hrs, Double Door | [16 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR105 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR105
[5 empty] | H_DR_AR_B12_Double Door_Steel_Vision_Panic_Transsom_W2000xH3000_0Hr | A04AR105-00002 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | 00002 | A04AR105-00002 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: N/A, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (3000 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Double Door_Steel_Vision_Panic_Transsom_W2000xH3000_1.0Hr | A04AR105-00006 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | 00006 | A04AR105-00006 |  | EA | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: 1-hr, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Double Door + Transsom - normal |  |  | ▶ Double Door_Blast_Transsom
8.3.1.2.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_Blast_Transsom |  | DDT21 | # |  |  |  |  | Fire Protective Rating: N/A, Double Door |  | Fire Protective Rating: 0.5-hr, Double Door |  | Fire Protective Rating: 1-hr, Double Door |  | Fire Protective Rating: 1.5-hrs, Double Door |  | Fire Protective Rating: 2-hrs, Double Door |  | Fire Protective Rating: 3-hrs, Double Door | [14 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR107 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) | A04AR107
[5 empty] | H_DR_AR_B12_Double Door_Blast_Transsom_W2000xH3000_0Hr | A04AR107-00002 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | 00002 | A04AR107-00002 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | W x H=( 2000 )mm x (3000 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Double Door_Blast_Transsom_W2000xH3000_1.0Hr | A04AR107-00006 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | 00006 | A04AR107-00006 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1-hr, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.3.1.2.2 | System Family |  | DR-Q1 | H_DR_AR_B12_Double Door_Blast_Panic_Transsom |  | DDT22 | # |  |  |  |  | Fire Protective Rating: N/A, Double Door |  | Fire Protective Rating: 0.5-hr, Double Door |  | Fire Protective Rating: 1-hr, Double Door |  | Fire Protective Rating: 1.5-hrs, Double Door |  | Fire Protective Rating: 2-hrs, Double Door |  | Fire Protective Rating: 3-hrs, Double Door | [14 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR109 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR109
[5 empty] | H_DR_AR_B12_Double Door_Blast_Panic_Transsom_W2000xH3000_0Hr | A04AR109-00002 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | 00002 | A04AR109-00002 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | Fire Protective Rating: N/A, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | W x H=( 2000 )mm x (3000 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Double Door_Blast_Panic_Transsom_W2000xH3000_2.0Hr | A04AR109-00010 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 2-hrs, Double Door w/ Hardware & Accessories | 00010 | A04AR109-00010 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | Fire Protective Rating: 2-hrs, Double Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.4 | Etc.
| □ Etc. - normal |  |  | ▶ Shutter
[Roll up Steel]
8.4.1.1.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Roll up Door_Steel_Manual |  | BD11 | # |  |  |  |  | Fire Protective Rating: N/A, Manual Type |  | Fire Protective Rating: 0.5-hr, Manual Type |  | Fire Protective Rating: 1-hr, Manual Type |  | Fire Protective Rating: 1.5-hrs, Manual Type |  | Fire Protective Rating: 2-hrs, Manual Type | [16 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR127 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) | A04AR127
[5 empty] | H_DR_AR_B12_Roll up Door_Steel_Manual_W5000xH6000_0Hr | A04AR127-00002 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Manual Type w/ Hardware & Accessories | 00002 | A04AR127-00002 |  | EA | Finishing Work | Door & Window Work | Steel Roll Up Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Manual Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Roll up Door_Steel_Manual_W5000xH6000_1.0Hr | A04AR127-00006 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Manual Type w/ Hardware & Accessories | 00006 | A04AR127-00006 |  | EA | Finishing Work | Door & Window Work | Steel Roll Up Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1-hr, Manual Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.4.1.1.2 | System Family |  | DR-Q1 | H_DR_AR_B12_Roll up Door_Steel_Motor |  | BD12 | # |  |  |  | Fire Protective Rating: N/A, Motorized Type |  | Fire Protective Rating: 0.5-hr, Motorized Type |  | Fire Protective Rating: 1-hr, Motorized Type |  | Fire Protective Rating: 1.5-hrs, Motorized Type |  | Fire Protective Rating: 2-hrs, Motorized Type | [17 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR127 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) | A04AR127
[5 empty] | H_DR_AR_B12_Roll up Door_Steel_Motor_W5000xH6000_0Hr | A04AR127-00001 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Motorized Type w/ Hardware & Accessories | 00001 | A04AR127-00001 |  | EA | Finishing Work | Door & Window Work | Steel Roll Up Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Motorized Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Roll up Door_Steel_Motor_W5000xH6000_1.0Hr | A04AR127-00005 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Motorized Type w/ Hardware & Accessories | 00005 | A04AR127-00005 |  | EA | Finishing Work | Door & Window Work | Steel Roll Up Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1-hr, Motorized Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Etc. - normal |  |  | ▶ Shutter
[Roll up Blast]
8.4.1.1.3 | System Family |  | DR-Q1 | H_DR_AR_B12_Roll up Door_Blast_Manual |  | BD13 | # |  |  |  |  | Fire Protective Rating: N/A, Manual Type |  | Fire Protective Rating: 1-hr, Manual Type |  | Fire Protective Rating: 2-hrs, Manual Type | [20 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR129 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | A04AR129
[5 empty] | H_DR_AR_B12_Roll up Door_Blast_Manual_W5000xH6000_0Hr | A04AR129-00002 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Manual Type w/ Hardware & Accessories | 00002 | A04AR129-00002 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Manual Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Roll up Door_Blast_Manual_W5000xH6000_2.0Hr | A04AR129-00006 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 2-hrs, Manual Type w/ Hardware & Accessories | 00006 | A04AR129-00006 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 2-hrs, Manual Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.4.1.1.4 | System Family |  | DR-Q1 | H_DR_AR_B12_Roll up Door_Blast_Motor |  | BD14 | # |  |  |  | Fire Protective Rating: N/A, Motorized Type |  | Fire Protective Rating: 1-hr, Motorized Type |  | Fire Protective Rating: 2-hrs, Motorized Type | [21 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR129 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | A04AR129
[5 empty] | H_DR_AR_B12_Roll up Door_Blast_Motor_W5000xH6000_0Hr | A04AR129-00001 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Motorized Type w/ Hardware & Accessories | 00001 | A04AR129-00001 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Motorized Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[5 empty] | H_DR_AR_B12_Roll up Door_Blast_Motor_W5000xH6000_2.0Hr | A04AR129-00005 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 2-hrs, Motorized Type w/ Hardware & Accessories | 00005 | A04AR129-00005 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 2-hrs, Motorized Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  |  | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Etc. - normal |  |  | ▶ Shutter
[Roll up Aluminum]
8.4.1.1.5 | System Family |  | DR-Q1 | H_DR_AR_B12_Roll up Door_AL_Manual |  | BD15 | # |  |  |  |  | Fire Protective Rating: N/A, Manual Type | [24 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR131 Finishing Work Door & Window Work Aluminum Roll Up Door w/ Aluminum Frame (UoM: EA) | A04AR131
[5 empty] | H_DR_AR_B12_Roll up Door_AL_Manual_W5000xH6000 | A04AR131-00002 Finishing Work Door & Window Work Aluminum Roll Up Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: N/A, Manual Type w/ Hardware & Accessories | 00002 | A04AR131-00002 |  | EA | Finishing Work | Door & Window Work | Aluminum Roll Up Door w/ Aluminum Frame (UoM: EA) | Fire Protective Rating: N/A, Manual Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.4.1.1.6 | System Family |  | DR-Q1 | H_DR_AR_B12_Roll up Door_AL_Motor |  | BD16 | # |  |  |  | Fire Protective Rating: N/A, Motorized Type | [25 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR131 Finishing Work Door & Window Work Aluminum Roll Up Door w/ Aluminum Frame (UoM: EA) | A04AR131
[5 empty] | H_DR_AR_B12_Roll up Door_AL_Mortor_W5000xH6000 | A04AR131-00001 Finishing Work Door & Window Work Aluminum Roll Up Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: N/A, Motorized Type w/ Hardware & Accessories | 00001 | A04AR131-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Roll Up Door w/ Aluminum Frame (UoM: EA) | Fire Protective Rating: N/A, Motorized Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Etc. - normal |  |  | ▶ Sliding
[Sliding Door Steel]
8.4.1.2.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Sliding Door_Steel_Manual |  | BD21 | # |  |  |  |  | Fire Protective Rating: N/A, Manual Type |  | Fire Protective Rating: 0.5-hr, Manual Type |  | Fire Protective Rating: 1-hr, Manual Type |  | Fire Protective Rating: 1.5-hrs, Manual Type |  | Fire Protective Rating: 2-hrs, Manual Type | [16 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR133 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) | A04AR133
[5 empty] | H_DR_AR_B12_Sliding Door_Steel_Manual_W5000xH6000 | A04AR133-00002 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Manual Type w/ Hardware & Accessories | 00002 | A04AR133-00002 |  | EA | Finishing Work | Door & Window Work | Steel Sliding Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Manual Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.4.1.2.2 | System Family |  | DR-Q1 | H_DR_AR_B12_Sliding Door_Steel_Motor |  | BD22 | # |  |  |  | Fire Protective Rating: N/A, Motorized Type |  | Fire Protective Rating: 0.5-hr, Motorized Type |  | Fire Protective Rating: 1-hr, Motorized Type |  | Fire Protective Rating: 1.5-hrs, Motorized Type |  | Fire Protective Rating: 2-hrs, Motorized Type | [17 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR133 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) | A04AR133
[5 empty] | H_DR_AR_B12_Sliding Door_Steel_Mortor_W5000xH6000 | A04AR133-00001 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Motorized Type w/ Hardware & Accessories | 00001 | A04AR133-00001 |  | EA | Finishing Work | Door & Window Work | Steel Sliding Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Motorized Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Etc. - normal |  |  | ▶ Sliding
[Sliding Door Aluminum]
8.4.1.2.3 | System Family |  | DR-Q1 | H_DR_AR_B12_Sliding Door_AL_Manual |  | BD23 | # |  |  |  |  | Fire Protective Rating: N/A, Manual Type | [24 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR135 Finishing Work Door & Window Work Aluminum Sliding Door w/ Aluminum Frame (UoM: EA) | A04AR135
[5 empty] | H_DR_AR_B12_Sliding Door_AL_Manual_W5000xH6000 | A04AR135-00002 Finishing Work Door & Window Work Aluminum Sliding Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: N/A, Manual Type w/ Hardware & Accessories | 00002 | A04AR135-00002 |  | EA | Finishing Work | Door & Window Work | Aluminum Sliding Door w/ Aluminum Frame (UoM: EA) | Fire Protective Rating: N/A, Manual Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.4.1.2.4 | System Family |  | DR-Q1 | H_DR_AR_B12_Sliding Door_AL_Motor |  | BD24 | # |  |  |  | Fire Protective Rating: N/A, Motorized Type | [25 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR135 Finishing Work Door & Window Work Aluminum Sliding Door w/ Aluminum Frame (UoM: EA) | A04AR135
[5 empty] | H_DR_AR_B12_Sliding Door_AL_Mortor_W5000xH6000 | A04AR135-00001 Finishing Work Door & Window Work Aluminum Sliding Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: N/A, Motorized Type w/ Hardware & Accessories | 00001 | A04AR135-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Sliding Door w/ Aluminum Frame (UoM: EA) | Fire Protective Rating: N/A, Motorized Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Etc. - normal |  |  | ▶ Sliding
[Sliding Door Glass]
8.4.1.2.5 | System Family |  | DR-Q1 | H_DR_AR_B12_Sliding Door_Glass_Manual |  | BD25 | # | [29 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | 0
|  |  |  | WM 항목없음 | H_DR_AR_B12_Sliding Door_Glass_Manual_W1000xH2100 | [25 empty] | W x H=( 5000 )mm x (6000 )mm | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.4.1.2.6 | System Family |  | DR-Q1 | H_DR_AR_B12_Sliding Door_Glass_Motor |  | BD26 | # | [29 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | 0
|  |  |  | WM 항목없음 | H_DR_AR_B12_Sliding Door_Glass_Motor_W1000xH2100 | [25 empty] | W x H=( 5000 )mm x (6000 )mm | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Etc. - normal |  |  | ▶ Hanger
8.4.1.3.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Hanger Door_Steel |  | BD31 | # |  |  |  | Steel Hanger Door w/ Steel Frame (UoM: EA) | [25 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR137 Finishing Work Door & Window Work Steel Hanger Door w/ Steel Frame (UoM: EA) | A04AR137
[5 empty] | H_DR_AR_B12_Hanger Door_Steel_W5000xH6000 | A04AR137-00001 Finishing Work Door & Window Work Steel Hanger Door w/ Steel Frame (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR137-00001 |  | EA | Finishing Work | Door & Window Work | Steel Hanger Door w/ Steel Frame (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Etc. - normal |  |  | ▶ Swing
8.4.1.4.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Swing Door_Steel |  | BD41 | # |  |  |  | Steel Swing Door w/ Steel Frame (UoM: EA) | [25 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR139 Finishing Work Door & Window Work Steel Swing Door w/ Steel Frame (UoM: EA) | A04AR139
[5 empty] | H_DR_AR_B12_Swing Door_Steel_W5000xH6000 | A04AR139-00001 Finishing Work Door & Window Work Steel Swing Door w/ Steel Frame (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR139-00001 |  | EA | Finishing Work | Door & Window Work | Steel Swing Door w/ Steel Frame (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.4.1.4.2 | System Family |  | DR-Q1 | H_DR_AR_B12_Swing Door_AL |  | BD42 | # |  |  |  | Aluminum Swing Door w/ Aluminum Frame (UoM: EA) | [25 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR141 Finishing Work Door & Window Work Aluminum Swing Door w/ Aluminum Frame (UoM: EA) | A04AR141
[5 empty] | H_DR_AR_B12_Swing Door_AL_W5000xH6000 | A04AR141-00001 Finishing Work Door & Window Work Aluminum Swing Door w/ Aluminum Frame (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR141-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Swing Door w/ Aluminum Frame (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Etc. - normal |  |  | ▶ Revolving
8.4.1.5.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Revolving Door_Manual |  | BD51 | # |  |  |  | Revolving Door (UoM: EA) | Revolving Door (UoM: EA) | [24 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR142 Finishing Work Door & Window Work Revolving Door (UoM: EA) | A04AR142
[5 empty] | H_DR_AR_B12_Revolving Door_Manual_W5000xH6000 | A04AR142-00001 Finishing Work Door & Window Work Revolving Door (UoM: EA) Manual Revolving Door w/ Hardware & Accessories | 00001 | A04AR142-00001 |  | EA | Finishing Work | Door & Window Work | Revolving Door (UoM: EA) | Manual Revolving Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.4.1.5.2 | System Family |  | DR-Q1 | H_DR_AR_B12_Revolving Door_Auto |  | BD52 | # |  |  |  | Revolving Door (UoM: EA) | Revolving Door (UoM: EA) | [24 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR142 Finishing Work Door & Window Work Revolving Door (UoM: EA) | A04AR142
[5 empty] | H_DR_AR_B12_Revolving Door_Auto_W5000xH6000 | A04AR142-00002 Finishing Work Door & Window Work Revolving Door (UoM: EA) Auto Revolving Door w/ Hardware & Accessories | 00002 | A04AR142-00002 |  | EA | Finishing Work | Door & Window Work | Revolving Door (UoM: EA) | Auto Revolving Door | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Etc. - normal |  |  | ▶ Folding
[Folding Door Steel]
8.4.1.6.1 | System Family |  | DR-Q1 | H_DR_AR_B12_Folding Door_Steel_Manual |  | BD61 | # |  |  |  |  | Manual Type | [24 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR144 Finishing Work Door & Window Work Steel Folding(Accordion) Door w/ Steel Frame (UoM: EA) | A04AR144
[5 empty] | H_DR_AR_B12_Folding Door_Steel_Manual_W5000xH6000 | A04AR144-00002 Finishing Work Door & Window Work Steel Folding(Accordion) Door w/ Steel Frame (UoM: EA) Manual Type w/ Hardware & Accessories | 00002 | A04AR144-00002 |  | EA | Finishing Work | Door & Window Work | Steel Folding(Accordion) Door w/ Steel Frame (UoM: EA) | Manual Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.4.1.6.2 | System Family |  | DR-Q1 | H_DR_AR_B12_Folding Door_Steel_Motor |  | BD62 | # |  |  |  | Motorized Type | [25 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR144 Finishing Work Door & Window Work Steel Folding(Accordion) Door w/ Steel Frame (UoM: EA) | A04AR144
[5 empty] | H_DR_AR_B12_Folding Door_Steel_Mortor_W5000xH6000 | A04AR144-00001 Finishing Work Door & Window Work Steel Folding(Accordion) Door w/ Steel Frame (UoM: EA) Motorized Type w/ Hardware & Accessories | 00001 | A04AR144-00001 |  | EA | Finishing Work | Door & Window Work | Steel Folding(Accordion) Door w/ Steel Frame (UoM: EA) | Motorized Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Etc. - normal |  |  | ▶ Folding
[Folding Door Aluminum]
8.4.1.6.3 | System Family |  | DR-Q1 | H_DR_AR_B12_Folding Door_AL_Manual |  | BD63 | # |  |  |  |  | Manual Type | [24 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR146 Finishing Work Door & Window Work Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: EA) | A04AR146
[5 empty] | H_DR_AR_B12_Folding Door_AL_Manual_W5000xH6000 | A04AR146-00002 Finishing Work Door & Window Work Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: EA) Manual Type w/ Hardware & Accessories | 00002 | A04AR146-00002 |  | EA | Finishing Work | Door & Window Work | Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: EA) | Manual Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.4.1.6.4 | System Family |  | DR-Q1 | H_DR_AR_B12_Folding Door_AL_Motor |  | BD64 | # |  |  |  | Motorized Type | [25 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR146 Finishing Work Door & Window Work Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: EA) | A04AR146
[5 empty] | H_DR_AR_B12_Folding Door_AL_Mortor_W5000xH6000 | A04AR146-00001 Finishing Work Door & Window Work Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: EA) Motorized Type w/ Hardware & Accessories | 00001 | A04AR146-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: EA) | Motorized Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Etc. - normal |  |  | ▶ Folding
[Folding Door Etc.]
8.4.1.6.5 | System Family |  | DR-Q1 | H_DR_AR_B12_Folding Door_PVC_Manual |  | BD65 | # |  |  |  | Manual Type | [25 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR148 Finishing Work Door & Window Work PVC Folding(Accordion) Door w/ PVC Frame (UoM: EA) | A04AR148
[5 empty] | H_DR_AR_B12_Folding Door_PVC_Manual_W5000xH6000 | A04AR148-00001 Finishing Work Door & Window Work PVC Folding(Accordion) Door w/ PVC Frame (UoM: EA) Manual Type w/ Hardware & Accessories | 00001 | A04AR148-00001 |  | EA | Finishing Work | Door & Window Work | PVC Folding(Accordion) Door w/ PVC Frame (UoM: EA) | Manual Type | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 5000 )mm x (6000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
8.4.1.6.6 | System Family |  | DR-Q1 | H_DR_AR_B12_Folding Door_Glass_Manual |  | BD66 | # | [29 empty] | 산출기준 >> [ 도어 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | 0
|  |  |  | WM 항목없음 | H_DR_AR_B12_Folding Door_Glass_Manual_W5000xH6000 | [25 empty] | W x H=( 5000 )mm x (6000 )mm | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q

## 9.Windows
[Family List] - Windows |  |  |  |  | 표준구성도로 가기
NO | Family Category | Building Tag | Q'ty Cal Type Tag | Standard Type | Family Type Name | Work Master Code /w Description |  | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Description | 입찰_ 물량산출식 | 실행_ 물량산출식 | Quantity |  | Remark (물량관련)
9 | Windows [WD]
9.1 | Sliding Type Window
| □ Sliding Type |  |  | ▶ Steel Window (Sliding)
9.1.1.1.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Sliding_Steel Window |  | WN11, WN12 | # |  |  |  | Fire Protective Rating: N/A | Fire Protective Rating: 0.5-hr | Fire Protective Rating: 1-hr | [23 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR153 Finishing Work Door & Window Work Steel Window (UoM: EA) | A04AR153 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Sliding_Steel Window_SG_W2000xH1000 | A04AR153-00001 Finishing Work Door & Window Work Steel Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR153-00001 |  | EA | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[5 empty] | H_WD_AR_B11_Sliding_Steel Window_DG_W2000xH1000 | A04AR153-00001 Finishing Work Door & Window Work Steel Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR153-00001 |  | EA | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Sliding Type |  |  | ▶ Aluminum Window (Sliding)
9.1.1.2.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Sliding_AL Window |  | WN12, WN13 | # |  |  |  | Fire Protective Rating: N/A | Fire Protective Rating: 0.5-hr | Fire Protective Rating: 1-hr | [23 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR159 Finishing Work Door & Window Work Aluminum Window (UoM: EA) | A04AR159 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Sliding_AL Window_SG_W2000xH1000 | A04AR159-00001 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR159-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[5 empty] | H_WD_AR_B11_Sliding_AL Window_DG_W2000xH1000 | A04AR159-00001 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR159-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Sliding Type |  |  | ▶ uPVC Window (Sliding)
9.1.1.3.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Sliding_uPVC Window |  | WN15, WN16 | # |  |  |  | 0 | [25 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR161 Finishing Work Door & Window Work uPVC Window (UoM: EA) | A04AR161 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Sliding_uPVC Window_SG_W2000xH1000 | A04AR161-00001 Finishing Work Door & Window Work uPVC Window (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR161-00001 |  | EA | Finishing Work | Door & Window Work | uPVC Window (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[5 empty] | H_WD_AR_B11_Sliding_uPVC Window_DG_W2000xH1000 | A04AR161-00001 Finishing Work Door & Window Work uPVC Window (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR161-00001 |  | EA | Finishing Work | Door & Window Work | uPVC Window (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Sliding Type |  |  | ▶ Blast Resistant Window (Sliding)
9.1.1.4.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Sliding_Blast Window |  | WN17 | # |  |  |  | 0 | [25 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR155 Finishing Work Door & Window Work Blast Resistant Steel Window (UoM: EA) | A04AR155 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Sliding_Blast Window_W2000xH1000 | A04AR155-00001 Finishing Work Door & Window Work Blast Resistant Steel Window (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR155-00001 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Steel Window (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Sliding Type |  |  | ▶ Bullet-Proof Steel Window (Sliding)
9.1.1.5.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Sliding_Bullet-Proof Steel Window |  | WN18 | # |  |  |  | 0 | [25 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR157 Finishing Work Door & Window Work Bullet-Proof Steel Window (UoM: EA) | A04AR157 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Sliding_Bullet-Proof Steel Window_W2000xH1000 | A04AR157-00001 Finishing Work Door & Window Work Bullet-Proof Steel Window (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR157-00001 |  | EA | Finishing Work | Door & Window Work | Bullet-Proof Steel Window (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
9.2 | Awning Type Window
| □ Awning Type |  |  | ▶ Steel Window (Awning)
9.2.1.1.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Awning_Steel Window |  | WN21, WN22 | # |  |  |  | Fire Protective Rating: N/A | Fire Protective Rating: 0.5-hr | Fire Protective Rating: 1-hr | [23 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR153 Finishing Work Door & Window Work Steel Window (UoM: EA) | A04AR153 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Awining_ Steel Window_SG_W2000xH1000 | A04AR153-00001 Finishing Work Door & Window Work Steel Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR153-00001 |  | EA | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[5 empty] | H_WD_AR_B11_Awining_ Steel Window_DG_W2000xH1000 | A04AR153-00002 Finishing Work Door & Window Work Steel Window (UoM: EA) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | 00002 | A04AR153-00002 |  | EA | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 0.5-hr | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Awning Type |  |  | ▶ Aluminum Window (Awning)
9.2.1.2.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Awning_AL Window |  | WN23, WN24 | # |  |  |  | Fire Protective Rating: N/A | Fire Protective Rating: 0.5-hr | Fire Protective Rating: 1-hr | [23 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR159 Finishing Work Door & Window Work Aluminum Window (UoM: EA) | A04AR159 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Awining_ AL Window_SG_W2000xH1000 | A04AR159-00001 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR159-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[5 empty] | H_WD_AR_B11_Awining_ AL Window_DG_W2000xH1000 | A04AR159-00002 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | 00002 | A04AR159-00002 |  | EA | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: 0.5-hr | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Awning Type |  |  | ▶ uPVC Window (Awning)
9.2.1.3.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Awning_uPVC Window |  | WN25, WN26 | # |  |  |  | 0 | [25 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR161 Finishing Work Door & Window Work uPVC Window (UoM: EA) | A04AR161 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Awining_uPVC Window_SG_W2000xH1000 | A04AR161-00001 Finishing Work Door & Window Work uPVC Window (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR161-00001 |  | EA | Finishing Work | Door & Window Work | uPVC Window (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[5 empty] | H_WD_AR_B11_Awining_uPVC Window_DG_W2000xH1000 | A04AR161-00001 Finishing Work Door & Window Work uPVC Window (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR161-00001 |  | EA | Finishing Work | Door & Window Work | uPVC Window (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Awning Type |  |  | ▶ Blast Resistant Window (Awning)
9.2.1.4.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Awning_Blast Window |  | WN27 | # |  |  |  | 0 | [25 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR155 Finishing Work Door & Window Work Blast Resistant Steel Window (UoM: EA) | A04AR155 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Awining_Blast Window_W2000xH1000 | A04AR155-00001 Finishing Work Door & Window Work Blast Resistant Steel Window (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR155-00001 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Steel Window (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Awning Type |  |  | ▶ Bullet-Proof Steel Window (Awning)
9.2.1.5.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Awning_Bullet-Proof Steel Window |  | WN29 | # |  |  |  | 0 | [25 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR157 Finishing Work Door & Window Work Bullet-Proof Steel Window (UoM: EA) | A04AR157 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Awining_Bullet-Proof Steel Window_W2000xH1000 | A04AR157-00001 Finishing Work Door & Window Work Bullet-Proof Steel Window (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR157-00001 |  | EA | Finishing Work | Door & Window Work | Bullet-Proof Steel Window (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
9.3 | Fix Type Window
| □ Fix Type |  |  | ▶ Steel Window (Fix)
9.3.1.1.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Fix_Steel Window |  | WN31, WN32 | # |  |  |  | Fire Protective Rating: N/A | Fire Protective Rating: 0.5-hr | Fire Protective Rating: 1-hr | [23 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR153 Finishing Work Door & Window Work Steel Window (UoM: EA) | A04AR153 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Fix_Steel Window_SG_W2000xH1000 | A04AR153-00001 Finishing Work Door & Window Work Steel Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR153-00001 |  | EA | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[5 empty] | H_WD_AR_B11_Fix_Steel Window_DG_W2000xH1000 | A04AR153-00002 Finishing Work Door & Window Work Steel Window (UoM: EA) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | 00002 | A04AR153-00002 |  | EA | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 0.5-hr | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Fix Type |  |  | ▶ Aluminum Window (Fix)
9.3.1.2.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Fix_AL Window |  | WN33, WN34, WN34A | # |  |  |  | Fire Protective Rating: N/A | Fire Protective Rating: 0.5-hr | Fire Protective Rating: 1-hr | [23 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR159 Finishing Work Door & Window Work Aluminum Window (UoM: EA) | A04AR159 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Fix_AL Window_SG_W2000xH1000 | A04AR159-00001 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR159-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[5 empty] | H_WD_AR_B11_Fix_AL Window_DG_W2000xH1000 | A04AR159-00002 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | 00002 | A04AR159-00002 |  | EA | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: 0.5-hr | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[5 empty] | H_WD_AR_B11_Fix_AL Window_DG LowE_W2000xH1000 | A04AR159-00001 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR159-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Fix Type |  |  | ▶ uPVC Window (Fix)
9.3.1.3.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Fix_uPVC Window |  | WN35, WN36 | # |  |  |  | 0 | [25 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR161 Finishing Work Door & Window Work uPVC Window (UoM: EA) | A04AR161 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Fix_uPVC Window_SG_W2000xH1000 | A04AR161-00001 Finishing Work Door & Window Work uPVC Window (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR161-00001 |  | EA | Finishing Work | Door & Window Work | uPVC Window (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[5 empty] | H_WD_AR_B11_Fix_uPVC Window_DG_W2000xH1000 | A04AR161-00001 Finishing Work Door & Window Work uPVC Window (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR161-00001 |  | EA | Finishing Work | Door & Window Work | uPVC Window (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Fix Type |  |  | ▶ Blast Resistant Window (Fix)
| System Family |  | WD-Q1 | H_WD_AR_B11_Fix_Blast Window |  | WN37 | # |  |  |  | 0 | [25 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR155 Finishing Work Door & Window Work Blast Resistant Steel Window (UoM: EA) | A04AR155 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Fix_Blast Window_W2000xH1000 | A04AR155-00001 Finishing Work Door & Window Work Blast Resistant Steel Window (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR155-00001 |  | EA | Finishing Work | Door & Window Work | Blast Resistant Steel Window (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Fix Type |  |  | ▶ Bullet-Proof Steel Window (Fix)
9.3.1.5.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Fix_Bullet-Proof Steel Window |  | WN39 | # |  |  |  | 0 | [25 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR157 Finishing Work Door & Window Work Bullet-Proof Steel Window (UoM: EA) | A04AR157 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Fix_Bullet-Proof Steel Window_W2000xH1000 | A04AR157-00001 Finishing Work Door & Window Work Bullet-Proof Steel Window (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR157-00001 |  | EA | Finishing Work | Door & Window Work | Bullet-Proof Steel Window (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
9.4 | Combination Type Window
| □ Fix + Awning |  |  | ▶ Steel Window (Fix + Awning)
9.4.1.1.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Fix_Awning_Steel Window |  | WN41, WN42 | # |  |  |  | Fire Protective Rating: N/A | Fire Protective Rating: 0.5-hr | Fire Protective Rating: 1-hr | [23 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR153 Finishing Work Door & Window Work Steel Window (UoM: EA) | A04AR153 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Fix_Awning_Steel Window_SG_W2000xH1000 | A04AR153-00001 Finishing Work Door & Window Work Steel Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR153-00001 |  | EA | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[5 empty] | H_WD_AR_B11_Fix_Awning_Steel Window_DG_W2000xH1000 | A04AR153-00002 Finishing Work Door & Window Work Steel Window (UoM: EA) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | 00002 | A04AR153-00002 |  | EA | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 0.5-hr | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Fix + Awning |  |  | ▶ Aluminum Window (Fix + Awning)
9.4.1.2.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Fix_Awning_AL Window |  | WN43, WN44, WN44A | # |  |  |  | Fire Protective Rating: N/A | Fire Protective Rating: 0.5-hr | Fire Protective Rating: 1-hr | [23 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR159 Finishing Work Door & Window Work Aluminum Window (UoM: EA) | A04AR159 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Fix_Awning_AL Window_SG_W2000xH1000 | A04AR159-00001 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR159-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[5 empty] | H_WD_AR_B11_Fix_Awning_AL Window_DG_W2000xH1000 | A04AR159-00002 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | 00002 | A04AR159-00002 |  | EA | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: 0.5-hr | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[5 empty] | H_WD_AR_B11_Fix_Awning_AL Window_DG LowE_W2000xH1000 | A04AR159-00001 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR159-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ Fix + Awning |  |  | ▶ uPVC Window (Fix + Awning)
9.4.1.3.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Fix_Awning_uPVC Window |  | WN45, WN46 | # |  |  |  | 0 | [25 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR161 Finishing Work Door & Window Work uPVC Window (UoM: EA) | A04AR161 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Fix_Awning_uPVC Window_SG_W2000xH1000 | A04AR161-00001 Finishing Work Door & Window Work uPVC Window (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR161-00001 |  | EA | Finishing Work | Door & Window Work | uPVC Window (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[5 empty] | H_WD_AR_B11_Fix_Awning_uPVC Window_DG_W2000xH1000 | A04AR161-00001 Finishing Work Door & Window Work uPVC Window (UoM: EA) w/ Hardware & Accessories | 00001 | A04AR161-00001 |  | EA | Finishing Work | Door & Window Work | uPVC Window (UoM: EA) | 0 | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
9.5 | Skylight
| □ Skylight - normal |  |  | ▶ Skylight
9.5.1.1.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Skylight |  | WN71, WN72 | # | [29 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR162 Finishing Work Door & Window Work Skylight (UoM: M2) | A04AR162 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Skylight_FRP_W2000xH1000 | A04AR162-00001 Finishing Work Door & Window Work Skylight (UoM: M2) FRP(Fiberglass Reinforced Plastics) Skylight | 00001 | A04AR162-00001 |  | M2 | Finishing Work | Door & Window Work | Skylight (UoM: M2) | FRP(Fiberglass Reinforced Plastics) Skylight | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | = (H/1000) * (W/1000) | = (H/1000) * (W/1000) |  | M2
[5 empty] | H_WD_AR_B11_Skylight_Acrylic_W2000xH1000 | A04AR162-00002 Finishing Work Door & Window Work Skylight (UoM: M2) Acrylic Skylight w/ Ventilation | 00002 | A04AR162-00002 |  | M2 | Finishing Work | Door & Window Work | Skylight (UoM: M2) | Acrylic Skylight w/ Ventilation | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | = (H/1000) * (W/1000) | = (H/1000) * (W/1000) |  | M2
[32 empty] | = (H/1000) * (W/1000) | = (H/1000) * (W/1000)
[32 empty] | = (H/1000) * (W/1000) | = (H/1000) * (W/1000)
[32 empty] | = (H/1000) * (W/1000) | = (H/1000) * (W/1000)
9.6 | MISC Window
| □ MISC |  |  | ▶ Casement_Aluminum Window
9.6.1.1.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Casement_AL Window |  | WN81 | # |  |  |  | Fire Protective Rating: N/A | Fire Protective Rating: 0.5-hr | Fire Protective Rating: 1-hr | [23 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR159 Finishing Work Door & Window Work Aluminum Window (UoM: EA) | A04AR159 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Casement_AL Window_DG_W2000xH1000 | A04AR159-00001 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR159-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ MISC |  |  | ▶ Hung_Aluminum Window
9.6.1.2.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Hung_AL Window |  | WN91, WN91A, WN95 | # |  |  |  | Fire Protective Rating: N/A | Fire Protective Rating: 0.5-hr | Fire Protective Rating: 1-hr | [23 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR159 Finishing Work Door & Window Work Aluminum Window (UoM: EA) | A04AR159 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Hung_AL Window_Single_DG_W2000xH1000 | A04AR159-00001 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR159-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[5 empty] | H_WD_AR_B11_Hung_AL Window_Single_DG_Low E_W2000xH1000 | A04AR159-00001 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR159-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[5 empty] | H_WD_AR_B11_Hung_AL Window_Double_DG_W2000xH1000 | A04AR159-00001 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR159-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ MISC |  |  | ▶ Tilt_Aluminum Window
9.6.1.3.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Tilt_AL Window |  | WN101 | # |  |  |  | Fire Protective Rating: N/A | Fire Protective Rating: 0.5-hr | Fire Protective Rating: 1-hr | [23 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR159 Finishing Work Door & Window Work Aluminum Window (UoM: EA) | A04AR159 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Tilt_AL Window_DG_W2000xH1000 | A04AR159-00001 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR159-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
| □ MISC |  |  | ▶ Center Pivotilt_Aluminum Window
9.6.1.4.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Center Pivot_AL Window |  | WN111 | # |  |  |  | Fire Protective Rating: N/A | Fire Protective Rating: 0.5-hr | Fire Protective Rating: 1-hr | [23 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR159 Finishing Work Door & Window Work Aluminum Window (UoM: EA) | A04AR159 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_WD_AR_B11_Center Pivot_AL Window_DG_W2000xH1000 | A04AR159-00001 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | 00001 | A04AR159-00001 |  | EA | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q |  | EA
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
[32 empty] | =Q | =Q
9.7 | Louver
| □ Louver - normal |  |  | ▶ Louver
9.7.1.1.1 | System Family |  | WD-Q1 | H_WD_AR_B11_Louver |  | LV11, LV12 | # |  |  |  | Aluminum | Steel | [24 empty] | 산출기준 >> [ 윈도우 일반 산출 ]
[5 empty] | Work Group Code → Actual Family Type Name ↓ | A04AR164 Finishing Work Door & Window Work Louver (UoM: EA) | A04AR164 | [23 empty] | WM는 DG/SG 구분 없음 WM는 Type 구분 없음
[5 empty] | H_DR_AR_B12_Double Door_Steel_W2200xH2280_No FR_SD1 | A04AR164-00001 Finishing Work Door & Window Work Louver (UoM: EA) Aluminum w/ Hardware & Accessories | 00001 | A04AR164-00001 |  | EA | Finishing Work | Door & Window Work | Louver (UoM: EA) | Aluminum | 0 | 0 | 0 | 0 | w/ Hardware & Accessories | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | W x H=( 2000 )mm x (1000 )mm | =Q | =Q | 2 | EA
[31 empty] | W x H=( 600 )mm x (800 )mm | =Q | =Q
[32 empty] | =Q | =Q

## 10.Stairs
[Family List] - Stairs |  |  |  |  | 표준구성도로 가기
NO | Family Category | Building Tag | Q'ty Cal Type Tag | Standard Type | Family Type Name | Work Master Code /w Description | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Description | 입찰_ 물량산출식 | 실행_ 물량산출식 | Quantity |  | Remark (물량관련)
10 | Stairs [SR]
10.1 | Assembled Stair (System Family)
| □ Assembled Stair - normal |  |  | ▶ Assembled Stair
10.1.1.1.1 | System Family |  | SR-Q2 | H_SR_AR_S09_Steel Stair | [31 empty] | 산출기준 >> [Steel Stair]
[5 empty] | Steel Stairs | S02AA019-00003 Miscellaneous Steel Fabrication Work Shelter/Building Steel Stairs Galvanized Steel W/Painting | S02AA019-00003 |  | M | Miscellaneous Steel Fabrication Work | Shelter/Building | Steel Stairs | Galvanized Steel W/Painting | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | = S | = S |  | M
[5 empty] | Steel Stairs | S04AA019-00001 Miscellaneous Steel Erection Work Shelter/Building Steel Stairs | S04AA019-00001 |  | M | Miscellaneous Steel Erection Work | Shelter/Building | Steel Stairs | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 |  | = S | = S |  | M
H_SR_AR_S09_Steel Stair_W1000
10.2 | Precast Stair (System Family)
| □ Precast Stair - normal |  |  | ▶ Precast Stair
10.2.1.1.1 | System Family |  | SR-Q1 | H_SR_AR_B08_Concrete Stair_Outdoor | [31 empty] | 산출기준 >> [Concrete Stair]
|  |  |  | 구체 | Structural Concrete 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | F'c (Cylinder Strength) = 24MPa | = ((A+C)*(T/1000)+S*((T+0.17)/1000))*W*Q | = ((A+C)*(T/1000)+S*((T+0.17)/1000))*W*Q |  | M3
|  |  |  | 철근 | Rebar Work 400MPa<Fy≤470MPa | A03AD037-00002 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 400MPa<Fy≤470MPa | A03AD037-00002 |  | TON | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 400MPa<Fy≤470MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ASTM A615 GRADE 60 (Fy=420MPa) | = ((A+C)*(T/1000)+S*((T+0.17)/1000))*W*Q*RE | = ((A+C)*(T/1000)+S*((T+0.17)/1000))*W*Q*RE |  | TON
|  |  |  | 거푸집 | Form Work (1 time in use) | A03AF036-00001 Concrete Work Superstructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF036-00001 |  | M2 | Concrete Work | Superstructure Work | Form Work (1 time in use) | Flat Form | 0 | 0 | 0 | 0 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | =(A+S+C+H)*W*Q | =(A+S+C+H)*W*Q |  | M2
H_SR_AR_B08_Concrete Stair_Out_S2
H_SR_AR_B08_Concrete Stair_S1
H_SR_AR_B08_Concrete Stair_Out_S3
H_SR_AR_B08_Concrete Stair_Out_S4

## 11.Railings
[Family List] - Railings |  |  |  |  | 표준구성도로 가기
NO | Family Category | Building Tag | Q'ty Cal Type Tag | Standard Type | Family Type Name | Work Master Code /w Description | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Description | 입찰_ 물량산출식 | 실행_ 물량산출식 | Quantity |  | Remark (물량관련)
11 | Railings [RL]
11.1 | Railing (System Family)
| □ Railing - normal |  |  | ▶ Steel Handrail
11.1.1.1.1 | System Family |  | RL-Q1 | H_RL_AR_S10_Steel Handrail | [31 empty] | 산출기준 >> [Handrail]
[5 empty] | Steel Handrails | S02AA020-00002 Miscellaneous Steel Fabrication Work Shelter/Building Steel Handrails W/Painting | S02AA020-00002 |  | M | Miscellaneous Steel Fabrication Work | Shelter/Building | Steel Handrails | W/Painting | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | Material: ( KS D 3566, ASTM A53 grade B ) H=(1100)mm | = L/1000 | = L/1000 |  | M
[5 empty] | Steel Handrails | S04AA020-00001 Miscellaneous Steel Erection Work Shelter/Building Steel Handrails | S04AA020-00001 |  | M | Miscellaneous Steel Erection Work | Shelter/Building | Steel Handrails | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | H=( )mm | 0 | Material: ( KS D 3566, ASTM A53 grade B ) H=(1100)mm | = L/1000 | = L/1000 |  | M
H_RL_AR_S10_Steel Handrail_H1100
|  | Template |  |  | H_RL_AR_S10_Steel Handrail_H1100_PLATFORM
|  | Template |  |  | H_RL_AR_S10_Steel Handrail_H1100_LADDER
|  | Template |  |  | H_RL_AR_S10_Steel Handrail_H1100_STAIR
11.1.1.1.2 | System Family |  | RL-Q1 | H_RL_AR_S11_Steel Removable Handrail | [31 empty] | 산출기준 >> [Handrail]
[5 empty] | Steel Handrails - Removable | S02AA021-00002 Miscellaneous Steel Fabrication Work Shelter/Building Steel Handrails - Removable W/Painting | S02AA021-00002 |  | M | Miscellaneous Steel Fabrication Work | Shelter/Building | Steel Handrails - Removable | W/Painting | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | Material: ( KS D 3566, ASTM A53 grade B ) H=(1100)mm | = L/1000 | = L/1000 |  | M
[5 empty] | Steel Handrails - Removable | S04AA021-00001 Miscellaneous Steel Erection Work Shelter/Building Steel Handrails - Removable | S04AA021-00001 |  | M | Miscellaneous Steel Erection Work | Shelter/Building | Steel Handrails - Removable | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | H=( )mm | 0 | Material: ( KS D 3566, ASTM A53 grade B ) H=(1100)mm | = L/1000 | = L/1000 |  | M
H_RL_AR_S11_Steel Removable Handrail_H1100

## 12.Generic
[Family List] - Generic Model |  |  |  |  | 표준구성도로 가기
NO | Family Category | Building Tag | Q'ty Cal Type Tag | Standard Type | Family Type Name | Work Master Code /w Description | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Description | 입찰_ 물량산출식 | 실행_ 물량산출식 | Quantity |  | Remark (물량관련)
12 | Generic Model [GM]
12.1 | Ladder
| □ Ladder - normal |  |  | ▶ Caged Ladder
12.1.1.1.1 | System Family |  | GM-Q1A | H_GM_AR_S08_Caged Ladder | [31 empty] | 산출기준 >> [Caged Ladder]
[5 empty] | Steel Ladder w/ Cage | S02AA041-00001 Miscellaneous Steel Fabrication Work Shelter/Building Steel Ladder w/ Cage W/Painting | S02AA041-00001 |  | M | Miscellaneous Steel Fabrication Work | Shelter/Building | Steel Ladder w/ Cage | W/Painting | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | = L/1000 | = L/1000 |  | M
[5 empty] | Steel Ladder w/ Cage | S04AA041-00001 Miscellaneous Steel Erection Work Shelter/Building Steel Ladder w/ Cage | S04AA041-00001 |  | M | Miscellaneous Steel Erection Work | Shelter/Building | Steel Ladder w/ Cage | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | = L/1000 | = L/1000 |  | M
[5 empty] | Structural Concrete 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = PW * PL * PT | = PW * PL * PT |  | M3 | 래더 패드
H_GM_AR_S08_Caged Ladder_Bracket Set 150
|  | Template |  |  | H_GM_AR_S08_Caged Ladder_Staggered
|  | Template |  |  | H_GM_AR_S08_Caged Ladder_Access Platform
| □ Ladder - normal |  |  | ▶ Non Caged Ladder
12.1.1.2.1 | System Family |  | GM-Q1B | H_GM_AR_S08_Non Caged Ladder | [31 empty] | 산출기준 >> [Non-Caged Ladder]
[5 empty] | Steel Ladder w/o Cage | S02AA044-00001 Miscellaneous Steel Fabrication Work Shelter/Building Steel Ladder w/o Cage W/Painting | S02AA044-00001 |  | M | Miscellaneous Steel Fabrication Work | Shelter/Building | Steel Ladder w/o Cage | W/Painting | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | = L/1000 | = L/1000 |  | M
[5 empty] | Steel Ladder w/o Cage | S04AA044-00001 Miscellaneous Steel Erection Work Shelter/Building Steel Ladder w/o Cage | S04AA044-00001 |  | M | Miscellaneous Steel Erection Work | Shelter/Building | Steel Ladder w/o Cage | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | = L/1000 | = L/1000 |  | M
[5 empty] | Structural Concrete 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032-00022 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = PW * PL * PT | = PW * PL * PT |  | M3 | 래더 패드
H_GM_AR_S08_Non Caged Ladder_Bracket Set 150_H1250
12.2 | Bollard
| □ Bollard - normal |  |  | ▶ Steel Bollard
12.2.1.1.1 | System Family |  | GM-Q4 | H_GM_AR_B07_Steel Bollard | [31 empty] | 산출기준 >> [MISC : EA base]
[5 empty] | Steel Bollard | A04AV219-00002 Finishing Work Misc. Work Steel Bollard Removable Type w/ Paint, Concrete Fill | A04AV219-00002 |  | EA | Finishing Work | Misc. Work | Steel Bollard | Removable Type | 0 | 0 | 0 | 0 | w/ Paint, Concrete Fill | 0 | 0 | 0 | DIA=( )mm / H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | DIA=( 150 )mm / H=( 1000 )mm | = Q | = Q | 4 | EA
|  | Template |  |  | H_GM_AR_B07_Steel Bollard_D150
12.3 | Rain Drainage
| □ Roof Drain - normal |  |  | ▶ Roof Drain
12.3.1.1.1 | System Family |  | GM-Q4 | H_GM_AR_B07_Roof Drain | [31 empty] | 산출기준 >> [MISC : EA base]
[5 empty] | Roof Drain (for Building) | A04AV205-00010 Finishing Work Misc. Work Roof Drain (for Building) Stainless Steel Type DIA=150mm | A04AV205-00010 |  | EA | Finishing Work | Misc. Work | Roof Drain (for Building) | Stainless Steel Type | 0 | 0 | 0 | 0 |  | 0 | DIA=150mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = Q | = Q |  | EA
H_GM_AR_B07_Roof Drain_D150
| □ Downspout & Splash Block |  |  | ▶ Downspout
12.3.2.1.1 | System Family |  | GM-Q2 | H_GM_AR_B07_Steel Downspout | [31 empty] | 산출기준 >> [Downspout & Splash Block]
[5 empty] | Downspout | A04AV207-00010 Finishing Work Misc. Work Downspout Stainless Steel Type w/ Fixing Accessories DIA=150mm | A04AV207-00010 |  | M | Finishing Work | Misc. Work | Downspout | Stainless Steel Type | 0 | 0 | 0 | 0 | w/ Fixing Accessories | 0 | DIA=150mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = L/1000 | = L/1000 |  | M
H_GM_AR_B07_Steel Downspout_D150
| □ Downspout & Splash Block |  |  | ▶ Splash Block
12.3.2.2.1 | System Family |  | GM-Q2 | H_GM_AR_B07_Splash Block | [31 empty] | 산출기준 >> [Downspout & Splash Block]
[5 empty] | Splash Block | A04AV209-00001 Finishing Work Misc. Work Splash Block Precast Concrete Block Type | A04AV209-00001 |  | EA | Finishing Work | Misc. Work | Splash Block | Precast Concrete Block Type | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = Q | = Q |  | EA
H_GM_AR_B07_Splash Block_200x300
12.4 | Grout
| □ Grout - normal |  |  | ▶ Grouting
12.4.1.1.1 | System Family |  | GM-Q3 | H_GM_AR_B07_Grouting | [31 empty] | 산출기준 >> [Grouting]
[5 empty] | Non-Shrink Grouting | S03AA030-00001 Main Steel Structure Erection Work Shelter/Building Non-Shrink Grouting | S03AA030-00001 |  | M3 | Main Steel Structure Erection Work | Shelter/Building | Non-Shrink Grouting | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | THK=( )mm | 0 | 0 |  | =V | =V |  | M3
H_GM_AR_B07_Grouting_T50
12.5 | MISC
| □ MISC - normal |  |  | ▶ Room Signage
12.5.1.1.1 | System Family |  | GM-Q4 | H_GM_AR_B07_Room Signage | [31 empty] | 산출기준 >> [MISC : EA base]
[5 empty] | Room Signage | A04AV221-00001 Finishing Work Misc. Work Room Signage | A04AV221-00001 |  | SET | Finishing Work | Misc. Work | Room Signage | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | = Q | = Q |  | SET
H_GM_AR_B07_Room Signage

## 13.Manual_Input
MISC (직접산출-모델객체 없음) |  |  |  |  | 표준구성도로 가기
NO | Family Category | Building Tag | Q'ty Cal Type Tag | Standard Type | Family Type Name | Work Master Code /w Description | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Description | 입찰_ 물량산출식 | 실행_ 물량산출식 | Quantity |  | Remark (물량관련)
13 | MISC
13.1 | Ladder
| □ Ladder |  |  | ▶ Caged Ladder
13.1.1.1.1 |  |  | 직접산출 | H_MI_AR_S08_Caged Ladder
[5 empty] | H_MI_AR_S08_Caged Ladder_Bracket Set 150 | S02AA041-00002 Miscellaneous Steel Fabrication Work Shelter/Building Steel Ladder w/ Cage Galvanized Steel | S02AA041-00002 |  | M | Miscellaneous Steel Fabrication Work | Shelter/Building | Steel Ladder w/ Cage | Galvanized Steel | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabrication | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | M
[5 empty] | H_MI_AR_S08_Caged Ladder_Bracket Set 150 | S04AA041-00001 Miscellaneous Steel Erection Work Shelter/Building Steel Ladder w/ Cage | S04AA041-00001 |  | M | Miscellaneous Steel Erection Work | Shelter/Building | Steel Ladder w/ Cage | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Erection | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | M
| □ Ladder |  |  | ▶ Non Caged Ladder
13.1.1.2.1 |  |  | 직접산출 | H_MI_AR_S08_Non Caged Ladder
[5 empty] | H_MI_AR_S08_Non Caged Ladder_Bracket Set 150_H1250 | S02AA044-00002 Miscellaneous Steel Fabrication Work Shelter/Building Steel Ladder w/o Cage Galvanized Steel | S02AA044-00002 |  | M | Miscellaneous Steel Fabrication Work | Shelter/Building | Steel Ladder w/o Cage | Galvanized Steel | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabrication | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | M
[5 empty] | H_MI_AR_S08_Non Caged Ladder_Bracket Set 150_H1250 | S04AA044-00001 Miscellaneous Steel Erection Work Shelter/Building Steel Ladder w/o Cage | S04AA044-00001 |  | M | Miscellaneous Steel Erection Work | Shelter/Building | Steel Ladder w/o Cage | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Erection | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | M
13.2 | Bollard
| □ Bollard |  |  | ▶ Steel Bollard
13.2.1.1.1 |  |  | 직접산출 | H_MI_AR_B07_Steel Bollard
[5 empty] | H_MI_AR_B07_Steel Bollard_Fix_D150 | A04AV219-00001 Finishing Work Misc. Work Steel Bollard Fixed Type w/ Paint, Concrete Fill | A04AV219-00001 |  | EA | Finishing Work | Misc. Work | Steel Bollard | Fixed Type | 0 | 0 | 0 | 0 | w/ Paint, Concrete Fill | 0 | 0 | 0 | DIA=( )mm / H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | DIA=( 150 )mm / H=( 1000 )mm |  | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Steel Bollard_Removable_D150 | A04AV219-00002 Finishing Work Misc. Work Steel Bollard Removable Type w/ Paint, Concrete Fill | A04AV219-00002 |  | EA | Finishing Work | Misc. Work | Steel Bollard | Removable Type | 0 | 0 | 0 | 0 | w/ Paint, Concrete Fill | 0 | 0 | 0 | DIA=( )mm / H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | DIA=( 150 )mm / H=( 1000 )mm | =2 | 물량 직접 산출 입력 | 0 | EA
13.3 | Rain Drainage
| □ Rain Drainage |  |  | ▶ Roof Drain
13.3.1.1.1 |  |  | 직접산출 | H_MI_AR_B07_Roof Drain
[5 empty] | H_MI_AR_B07_Roof Drain_D100 | A04AV205-00001 Finishing Work Misc. Work Roof Drain (for Building) Cast Iron Type DIA=100mm | A04AV205-00001 |  | EA | Finishing Work | Misc. Work | Roof Drain (for Building) | Cast Iron Type | 0 | 0 | 0 | 0 |  | 0 | DIA=100mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
| □ Rain Drainage |  |  | ▶ Downspout
13.3.1.2.1 |  |  | 직접산출 | H_MI_AR_B07_Steel Downspout
[5 empty] | H_MI_AR_B07_Steel Downspout_D150 | A04AV207-00002 Finishing Work Misc. Work Downspout Galvanized Steel Type w/ Fixing Accessories DIA=150mm | A04AV207-00002 |  | M | Finishing Work | Misc. Work | Downspout | Galvanized Steel Type | 0 | 0 | 0 | 0 | w/ Fixing Accessories | 0 | DIA=150mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | M
| □ Rain Drainage |  |  | ▶ Gutter
13.3.1.3.1 |  |  | 직접산출 | H_MI_AR_B07_Steel Eave Gutter
[5 empty] | H_MI_AR_B07_Steel Eave Gutter_200x200 | A04AV207-00002 Finishing Work Misc. Work Downspout Galvanized Steel Type w/ Fixing Accessories DIA=150mm | A04AV207-00002 |  | M | Finishing Work | Misc. Work | Downspout | Galvanized Steel Type | 0 | 0 | 0 | 0 | w/ Fixing Accessories | 0 | DIA=150mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | M
| □ Rain Drainage |  |  | ▶ Splash Block
13.3.1.4.1 |  |  | 직접산출 | H_MI_AR_B07_Splash Block
[5 empty] | H_MI_AR_B07_Splash Block_200x300 | A04AV209-00001 Finishing Work Misc. Work Splash Block Precast Concrete Block Type | A04AV209-00001 |  | EA | Finishing Work | Misc. Work | Splash Block | Precast Concrete Block Type | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
13.4 | Grout
| □ Grout |  |  | ▶ Grouting
13.4.1.1.1 |  |  | 직접산출 | H_MI_AR_B07_Grouting
[5 empty] | H_MI_AR_B07_Grouting_T50 | S03AA030-00001 Main Steel Structure Erection Work Shelter/Building Non-Shrink Grouting | S03AA030-00001 |  | M3 | Main Steel Structure Erection Work | Shelter/Building | Non-Shrink Grouting | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | THK=( )mm | 0 | 0 |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | M3
13.5 | Anchor Bolt
| □ Anchor Bolt |  |  | ▶ Anchor Bolt - Substructure
13.5.1.1.1 |  |  | 직접산출 | H_MI_AR_B07_Anchor Bolt_Substructure
[5 empty] | H_MI_AR_B07_Anchor Bolt_Substructure_M12 | A03AD329-00001 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M12 | A03AD329-00001 |  | EA | Concrete Work | Substructure Work | Anchor Bolt (Purchase & Installation) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Anchor Bolt_Substructure_M16 | A03AD329-00002 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M16 | A03AD329-00002 |  | EA | Concrete Work | Substructure Work | Anchor Bolt (Purchase & Installation) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Anchor Bolt_Substructure_M20 | A03AD329-00003 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M20 | A03AD329-00003 |  | EA | Concrete Work | Substructure Work | Anchor Bolt (Purchase & Installation) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Anchor Bolt_Substructure_Chemical_M10 | A03AD030-00001 Concrete Work Substructure Work Chemical Anchor Bolt Including injected Chemical material M10 | A03AD030-00001 |  | EA | Concrete Work | Substructure Work | Chemical Anchor Bolt | 0 | 0 | 0 | 0 | 0 | Including injected Chemical material | 0 | M10 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Anchor Bolt_Substructure_Chemical_M12 | A03AD030-00002 Concrete Work Substructure Work Chemical Anchor Bolt Including injected Chemical material M12 | A03AD030-00002 |  | EA | Concrete Work | Substructure Work | Chemical Anchor Bolt | 0 | 0 | 0 | 0 | 0 | Including injected Chemical material | 0 | M12 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Anchor Bolt_Substructure_Chemical_M16 | A03AD030-00003 Concrete Work Substructure Work Chemical Anchor Bolt Including injected Chemical material M16 | A03AD030-00003 |  | EA | Concrete Work | Substructure Work | Chemical Anchor Bolt | 0 | 0 | 0 | 0 | 0 | Including injected Chemical material | 0 | M16 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Anchor Bolt_Substructure_Expansion_M10 | A03AD031-00001 Concrete Work Substructure Work Expansion Anchor Bolt M10 | A03AD031-00001 |  | EA | Concrete Work | Substructure Work | Expansion Anchor Bolt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M10 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Anchor Bolt_Substructure_Expansion_M12 | A03AD031-00002 Concrete Work Substructure Work Expansion Anchor Bolt M12 | A03AD031-00002 |  | EA | Concrete Work | Substructure Work | Expansion Anchor Bolt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M12 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Anchor Bolt_Substructure_Expansion_M16 | A03AD031-00003 Concrete Work Substructure Work Expansion Anchor Bolt M16 | A03AD031-00003 |  | EA | Concrete Work | Substructure Work | Expansion Anchor Bolt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M16 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
| □ Anchor Bolt |  |  | ▶ Anchor Bolt - Equipment Foundation
13.5.1.2.1 |  |  | 직접산출 | H_MI_AR_B07_Anchor Bolt_Equipment Foundation
[5 empty] | H_MI_AR_B07_Anchor Bolt_Equipment Foundation_M12 | A03AG329-00001 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M12 | A03AG329-00001 |  | EA | Concrete Work | Equipment Foundation Work | Anchor Bolt (Purchase & Installation) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Anchor Bolt_Equipment Foundation_M16 | A03AG329-00002 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M16 | A03AG329-00002 |  | EA | Concrete Work | Equipment Foundation Work | Anchor Bolt (Purchase & Installation) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Anchor Bolt_Equipment Foundation_M20 | A03AG329-00003 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M20 | A03AG329-00003 |  | EA | Concrete Work | Equipment Foundation Work | Anchor Bolt (Purchase & Installation) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
| □ Anchor Bolt |  |  | ▶ Anchor Bolt - Mass Concrete
13.5.1.3.1 |  |  | 직접산출 | H_MI_AR_B07_Anchor Bolt_Mass Concrete
[31 empty] | 물량 직접 산출 입력 | 물량 직접 산출 입력
[5 empty] | H_MI_AR_B07_Anchor Bolt_Mass Concrete_M12 | A03AE329-00001 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M12 | A03AE329-00001 |  | EA | Concrete Work | Mass Concrete Work | Anchor Bolt (Purchase & Installation) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Anchor Bolt_Mass Concrete_M16 | A03AE329-00002 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M16 | A03AE329-00002 |  | EA | Concrete Work | Mass Concrete Work | Anchor Bolt (Purchase & Installation) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Anchor Bolt_Mass Concrete_M20 | A03AE329-00003 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M20 | A03AE329-00003 |  | EA | Concrete Work | Mass Concrete Work | Anchor Bolt (Purchase & Installation) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
13.6 | Embedded Steel
| □ Embedded Steel |  |  | ▶ Embedded Steel
13.6.1.1.1 |  |  | 직접산출 | H_MI_AR_B07_Embedded Steel
[5 empty] | H_MI_AR_B07_Embedded Steel_Galva. | A03AG049-00001 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) Hot-Dip Galvanized Steel Galv.: ASTM A123 | A03AG049-00001 |  | TON | Concrete Work | Equipment Foundation Work | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | Hot-Dip Galvanized Steel | 0 | 0 | 0 | 0 | Galv.: ASTM A123 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Hot-Dip Galvanized Steel | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | TON
[5 empty] | H_MI_AR_B07_Embedded Steel_SUS 304 | A03AG049-00003 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) SUS SUS 304 | A03AG049-00003 |  | TON | Concrete Work | Equipment Foundation Work | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | SUS | 0 | 0 | 0 | 0 | SUS 304 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | SUS 304 | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | TON
[5 empty] | H_MI_AR_B07_Embedded Steel_SUS 316L | A03AG049-00004 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) SUS SUS 316L | A03AG049-00004 |  | TON | Concrete Work | Equipment Foundation Work | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | SUS | 0 | 0 | 0 | 0 | SUS 316L | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | SUS 316L | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | TON
13.7 | Room, Toilt, Shower
| □ Room, Toilt, Shower |  |  | ▶ Signage
13.7.1.1.1 |  |  | 직접산출 | H_MI_AR_B07_Signage
[5 empty] | H_MI_AR_B07_Signage_Room | A04AV221-00001 Finishing Work Misc. Work Room Signage | A04AV221-00001 |  | SET | Finishing Work | Misc. Work | Room Signage | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | SET
[5 empty] | H_MI_AR_B07_Signage_Building | A04AV220-00001 Finishing Work Misc. Work Building Signage | A04AV220-00001 |  | SET | Finishing Work | Misc. Work | Building Signage | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | SET
| □ Room, Toilt, Shower |  |  | ▶ Toilet Accessories
13.7.1.2.1 |  |  | 직접산출 | H_MI_AR_B07_Toilet Accessories
[5 empty] | H_MI_AR_B07_Toilet Accessories_Mirror_W750xH800 | A04AV225-00001 Finishing Work Misc. Work Mirror w/ Shelf Stainless Steel, Surface Mounted Type | A04AV225-00001 |  | EA | Finishing Work | Misc. Work | Mirror w/ Shelf | Stainless Steel, Surface Mounted Type | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Toilet Accessories_Soap Dish | A04AV227-00001 Finishing Work Misc. Work Soap Dish Stainless Steel, Surface Mounted Type | A04AV227-00001 |  | EA | Finishing Work | Misc. Work | Soap Dish | Stainless Steel, Surface Mounted Type | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Toilet Accessories_Towel Bar | A04AV228-00001 Finishing Work Misc. Work Towel Bar Stainless Steel, Surface Mounted Type | A04AV228-00001 |  | EA | Finishing Work | Misc. Work | Towel Bar | Stainless Steel, Surface Mounted Type | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Toilet Accessories_Paper Tower Dispenser | A04AV231-00001 Finishing Work Misc. Work Paper Tower Dispenser Stainless Steel, Surface Mounted Type | A04AV231-00001 |  | EA | Finishing Work | Misc. Work | Paper Tower Dispenser | Stainless Steel, Surface Mounted Type | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Toilet Accessories_Urinal Partition | A04AV240-00001 Finishing Work Misc. Work Urinal Partition | A04AV240-00001 |  | EA | Finishing Work | Misc. Work | Urinal Partition | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Toilet Accessories_Marble Washstand | A04AV244-00001 Finishing Work Misc. Work Marble Washstand w/ Mortar Bond Coat or Adhesive | A04AV244-00001 |  | M | Finishing Work | Misc. Work | Marble Washstand | 0 | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | THK=( )mm / W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | M
| □ Room, Toilt, Shower |  |  | ▶ Septic Tank
13.7.1.3.1 |  |  | 직접산출 | H_MI_AR_B07_Septic Tank
[6 empty] | A04AV241-00001 Finishing Work Misc. Work Septic Tank FRP Type Including Excatvation, Installation, Backfilling and Any Other Works to Complete the Work 10 People≤Capa.<50 People | A04AV241-00001
[5 empty] | H_MI_AR_B07_Septic Tank_FRP | A04AV241-00001 Finishing Work Misc. Work Septic Tank FRP Type Including Excatvation, Installation, Backfilling and Any Other Works to Complete the Work 10 People≤Capa.<50 People | A04AV241-00001 |  | EA | Finishing Work | Misc. Work | Septic Tank | FRP Type | 0 | 0 | 0 | 0 | Including Excatvation, Installation, Backfilling and Any Other Works to Complete the Work | 0 | 10 People≤Capa.<50 People | 0 |  | 0 | 0 | 0 | 0 | 0 | Capa.=( )People |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
13.8 | Furniture Installation
| □ Furniture Installation |  |  | ▶ Furniture Installation
13.8.1.1.1 |  |  | 직접산출 | H_MI_AR_B07_Furniture Installation
[5 empty] | H_MI_AR_B07_Furniture Installation_Desk | A04BA260-00001 Finishing Work Furniture Installation Desk | A04BA260-00001 |  | EA | Finishing Work | Furniture Installation | Desk | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | EA
[5 empty] | H_MI_AR_B07_Furniture Installation_Washing Unit | A04BA291-00001 Finishing Work Furniture Installation Washing Unit | A04BA291-00001 |  | LOT | Finishing Work | Furniture Installation | Washing Unit | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 물량 직접 산출 입력 | 물량 직접 산출 입력 |  | LOT
13.9 | Ext Wall Finish
| □ EXT Wal Finish |  |  | ▶ Paint
13.8.1.1.1 |  |  | 직접산출 | H_MI_AR_B07_Furniture Installation
[5 empty] | H_WA_AR_B02_Ext Wall_RC_Emulsion Paint_T200_W1 | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | =223.6 | 223.6 | M2
Water Collection Box 추가 요망

## WM-AR
[8 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
[7 empty] | 1048576 | 2: Work Master
As of 2022-02-11
[8 empty] | Work Master Code | Discipline | Category(Large) |  | Category(Middle) |  | Category(Small) |  | Attributes Specifications | [15 empty] | BOQ Specifications | [8 empty] | UoM |  | Work Group Code | Work Master Code
single door |  | double door |  | Work Group Code /w Description | Work Master Code /w Description |  |  |  |  | Code | Description | Code | Description | Code | Description | Code | L04 | Code | L05 | Code | L06 | Code | L07 | Code | L08 | Code | L09 | Code | L10 | Code | L11 | B01 | B02 | B03 | B04 | B05 | B06 | B07 | B08 | B09 | UoM1 | UoM2
|  |  |  | A01ZZ001 Earth Work - Excavation | A01ZZ001-00010 Earth Work - Excavation Soil, Manual Manual Excavation Above GWL | A01ZZ001 | 00010 | A01ZZ001-00010 | AR | A01 | Earth Work | ZZ | - | 001 | Excavation | 01 | Soil, Manual |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 07 | Manual Excavation Above GWL |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ001 | A01ZZ001-00010
|  |  |  | A01ZZ001 Earth Work - Excavation | A01ZZ001-00011 Earth Work - Excavation Soil, Manual Manual Excavation Below GWL | A01ZZ001 | 00011 | A01ZZ001-00011 | AR | A01 | Earth Work | ZZ | - | 001 | Excavation | 01 | Soil, Manual |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 08 | Manual Excavation Below GWL |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ001 | A01ZZ001-00011
|  |  |  | A01ZZ001 Earth Work - Excavation | A01ZZ001-00012 Earth Work - Excavation Soil, Mech. Manual Excavation Above GWL | A01ZZ001 | 00012 | A01ZZ001-00012 | AR | A01 | Earth Work | ZZ | - | 001 | Excavation | 02 | Soil, Mech. |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 07 | Manual Excavation Above GWL |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ001 | A01ZZ001-00012
|  |  |  | A01ZZ001 Earth Work - Excavation | A01ZZ001-00013 Earth Work - Excavation Soil, Mech. Manual Excavation Below GWL | A01ZZ001 | 00013 | A01ZZ001-00013 | AR | A01 | Earth Work | ZZ | - | 001 | Excavation | 02 | Soil, Mech. |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 08 | Manual Excavation Below GWL |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ001 | A01ZZ001-00013
|  |  |  | A01ZZ317 Earth Work - Rock Excavation | A01ZZ317-00001 Earth Work - Rock Excavation Weathered Rock w/ Ripping | A01ZZ317 | 00001 | A01ZZ317-00001 | AR | A01 | Earth Work | ZZ | - | 317 | Rock Excavation | 03 | Weathered Rock |  | 0 |  | 0 |  | 0 |  | 0 | 59 | w/ Ripping |  | 0 |  |  | RQD Value=( )% |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ317 | A01ZZ317-00001
|  |  |  | A01ZZ317 Earth Work - Rock Excavation | A01ZZ317-00002 Earth Work - Rock Excavation Soft Rock w/ Ripping | A01ZZ317 | 00002 | A01ZZ317-00002 | AR | A01 | Earth Work | ZZ | - | 317 | Rock Excavation | 04 | Soft Rock |  | 0 |  | 0 |  | 0 |  | 0 | 59 | w/ Ripping |  | 0 |  |  | RQD Value=( )% |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ317 | A01ZZ317-00002
|  |  |  | A01ZZ317 Earth Work - Rock Excavation | A01ZZ317-00003 Earth Work - Rock Excavation Weathered Rock w/ Breaking | A01ZZ317 | 00003 | A01ZZ317-00003 | AR | A01 | Earth Work | ZZ | - | 317 | Rock Excavation | 03 | Weathered Rock |  | 0 |  | 0 |  | 0 |  | 0 | 60 | w/ Breaking |  | 0 |  |  | RQD Value=( )% |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ317 | A01ZZ317-00003
|  |  |  | A01ZZ317 Earth Work - Rock Excavation | A01ZZ317-00004 Earth Work - Rock Excavation Soft Rock w/ Breaking | A01ZZ317 | 00004 | A01ZZ317-00004 | AR | A01 | Earth Work | ZZ | - | 317 | Rock Excavation | 04 | Soft Rock |  | 0 |  | 0 |  | 0 |  | 0 | 60 | w/ Breaking |  | 0 |  |  | RQD Value=( )% |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ317 | A01ZZ317-00004
|  |  |  | A01ZZ317 Earth Work - Rock Excavation | A01ZZ317-00005 Earth Work - Rock Excavation Soft Rock w/ Blasting | A01ZZ317 | 00005 | A01ZZ317-00005 | AR | A01 | Earth Work | ZZ | - | 317 | Rock Excavation | 04 | Soft Rock |  | 0 |  | 0 |  | 0 |  | 0 | 61 | w/ Blasting |  | 0 |  |  | RQD Value=( )% |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ317 | A01ZZ317-00005
|  |  |  | A01ZZ317 Earth Work - Rock Excavation | A01ZZ317-00006 Earth Work - Rock Excavation Hard Rock w/ Blasting | A01ZZ317 | 00006 | A01ZZ317-00006 | AR | A01 | Earth Work | ZZ | - | 317 | Rock Excavation | 05 | Hard Rock |  | 0 |  | 0 |  | 0 |  | 0 | 61 | w/ Blasting |  | 0 |  |  | RQD Value=( )% |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ317 | A01ZZ317-00006
|  |  |  | A01ZZ003 Earth Work - Backfill | A01ZZ003-00001 Earth Work - Backfill Re-use, Soil | A01ZZ003 | 00001 | A01ZZ003-00001 | AR | A01 | Earth Work | ZZ | - | 003 | Backfill | 06 | Re-use, Soil |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | M3 | M3 | A01ZZ003 | A01ZZ003-00001
|  |  |  | A01ZZ003 Earth Work - Backfill | A01ZZ003-00002 Earth Work - Backfill Borrow Soil (Borrow Pit provided by Client, Free of Charge) | A01ZZ003 | 00002 | A01ZZ003-00002 | AR | A01 | Earth Work | ZZ | - | 003 | Backfill | 07 | Borrow Soil (Borrow Pit provided by Client, Free of Charge) |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | Borrow Pit Distance=Appx. ( )km | 0 | Compaction=( )% | 0 | 0 |  | M3 | M3 | A01ZZ003 | A01ZZ003-00002
|  |  |  | A01ZZ003 Earth Work - Backfill | A01ZZ003-00003 Earth Work - Backfill Purchased, Soil | A01ZZ003 | 00003 | A01ZZ003-00003 | AR | A01 | Earth Work | ZZ | - | 003 | Backfill | 08 | Purchased, Soil |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | Compaction=( )% | 0 | 0 |  | M3 | M3 | A01ZZ003 | A01ZZ003-00003
|  |  |  | A01ZZ004 Earth Work - Disposal | A01ZZ004-00001 Earth Work - Disposal Soil | A01ZZ004 | 00001 | A01ZZ004-00001 | AR | A01 | Earth Work | ZZ | - | 004 | Disposal | 09 | Soil |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ004 | A01ZZ004-00001
|  |  |  | A01ZZ004 Earth Work - Disposal | A01ZZ004-00002 Earth Work - Disposal Weathered Rock | A01ZZ004 | 00002 | A01ZZ004-00002 | AR | A01 | Earth Work | ZZ | - | 004 | Disposal | 03 | Weathered Rock |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ004 | A01ZZ004-00002
|  |  |  | A01ZZ004 Earth Work - Disposal | A01ZZ004-00003 Earth Work - Disposal Soft Rock | A01ZZ004 | 00003 | A01ZZ004-00003 | AR | A01 | Earth Work | ZZ | - | 004 | Disposal | 04 | Soft Rock |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ004 | A01ZZ004-00003
|  |  |  | A01ZZ004 Earth Work - Disposal | A01ZZ004-00004 Earth Work - Disposal Hard Rock | A01ZZ004 | 00004 | A01ZZ004-00004 | AR | A01 | Earth Work | ZZ | - | 004 | Disposal | 05 | Hard Rock |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ004 | A01ZZ004-00004
|  |  |  | A01ZZ004 Earth Work - Disposal | A01ZZ004-00005 Earth Work - Disposal Contaminated Soil | A01ZZ004 | 00005 | A01ZZ004-00005 | AR | A01 | Earth Work | ZZ | - | 004 | Disposal | 10 | Contaminated Soil |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | Disposal Distance=Appx. ( )km from Site | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ004 | A01ZZ004-00005
|  |  |  | A01ZZ005 Earth Work - Base Course | A01ZZ005-00001 Earth Work - Base Course THK≤150mm | A01ZZ005 | 00001 | A01ZZ005-00001 | AR | A01 | Earth Work | ZZ | - | 005 | Base Course |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 01 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | M2 | M2 | A01ZZ005 | A01ZZ005-00001
|  |  |  | A01ZZ005 Earth Work - Base Course | A01ZZ005-00002 Earth Work - Base Course 150mm<THK≤250mm | A01ZZ005 | 00002 | A01ZZ005-00002 | AR | A01 | Earth Work | ZZ | - | 005 | Base Course |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 06 | 150mm<THK≤250mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | M2 | M2 | A01ZZ005 | A01ZZ005-00002
|  |  |  | A01ZZ005 Earth Work - Base Course | A01ZZ005-00003 Earth Work - Base Course 250mm<THK≤350mm | A01ZZ005 | 00003 | A01ZZ005-00003 | AR | A01 | Earth Work | ZZ | - | 005 | Base Course |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 07 | 250mm<THK≤350mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | M2 | M2 | A01ZZ005 | A01ZZ005-00003
|  |  |  | A01ZZ005 Earth Work - Base Course | A01ZZ005-00004 Earth Work - Base Course 350mm<THK | A01ZZ005 | 00004 | A01ZZ005-00004 | AR | A01 | Earth Work | ZZ | - | 005 | Base Course |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 08 | 350mm<THK | 0 | THK=( )mm | 0 | 0 | CBR=( )% | 0 | 0 | 0 |  | M2 | M2 | A01ZZ005 | A01ZZ005-00004
|  |  |  | A01ZZ006 Earth Work - Subbase Course | A01ZZ006-00001 Earth Work - Subbase Course Including Compaction of Sub-Grade THK≤150mm | A01ZZ006 | 00001 | A01ZZ006-00001 | AR | A01 | Earth Work | ZZ | - | 006 | Subbase Course |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 01 | Including Compaction of Sub-Grade |  | 0 | 01 | THK≤150mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | M2 | M2 | A01ZZ006 | A01ZZ006-00001
|  |  |  | A01ZZ006 Earth Work - Subbase Course | A01ZZ006-00002 Earth Work - Subbase Course Including Compaction of Sub-Grade 150mm<THK≤250mm | A01ZZ006 | 00002 | A01ZZ006-00002 | AR | A01 | Earth Work | ZZ | - | 006 | Subbase Course |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 01 | Including Compaction of Sub-Grade |  | 0 | 06 | 150mm<THK≤250mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | M2 | M2 | A01ZZ006 | A01ZZ006-00002
|  |  |  | A01ZZ006 Earth Work - Subbase Course | A01ZZ006-00003 Earth Work - Subbase Course Including Compaction of Sub-Grade 250mm<THK≤350mm | A01ZZ006 | 00003 | A01ZZ006-00003 | AR | A01 | Earth Work | ZZ | - | 006 | Subbase Course |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 01 | Including Compaction of Sub-Grade |  | 0 | 07 | 250mm<THK≤350mm | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | M2 | M2 | A01ZZ006 | A01ZZ006-00003
|  |  |  | A01ZZ006 Earth Work - Subbase Course | A01ZZ006-00004 Earth Work - Subbase Course Including Compaction of Sub-Grade 350mm<THK | A01ZZ006 | 00004 | A01ZZ006-00004 | AR | A01 | Earth Work | ZZ | - | 006 | Subbase Course |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 01 | Including Compaction of Sub-Grade |  | 0 | 08 | 350mm<THK | 0 | THK=( )mm | 0 | 0 | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase | 0 | 0 |  | M2 | M2 | A01ZZ006 | A01ZZ006-00004
|  |  |  | A01ZZ007 Earth Work - Fill Material (only for Module Base Frame) | A01ZZ007-00001 Earth Work - Fill Material (only for Module Base Frame) | A01ZZ007 | 00001 | A01ZZ007-00001 | AR | A01 | Earth Work | ZZ | - | 007 | Fill Material (only for Module Base Frame) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ007 | A01ZZ007-00001
|  |  |  | A01ZZ008 Earth Work - Gravel | A01ZZ008-00002 Earth Work - Gravel DIA ≤ 25mm | A01ZZ008 | 00002 | A01ZZ008-00002 | AR | A01 | Earth Work | ZZ | - | 008 | Gravel |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 87 | DIA ≤ 25mm | 0 | DIA=( )mm~( )mm or Max DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ008 | A01ZZ008-00002
|  |  |  | A01ZZ008 Earth Work - Gravel | A01ZZ008-00003 Earth Work - Gravel 25mm < DIA ≤ 100mm | A01ZZ008 | 00003 | A01ZZ008-00003 | AR | A01 | Earth Work | ZZ | - | 008 | Gravel |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 88 | 25mm < DIA ≤ 100mm | 0 | DIA=( )mm~( )mm or Max DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ008 | A01ZZ008-00003
|  |  |  | A01ZZ009 Earth Work - Crushed Stone | A01ZZ009-00002 Earth Work - Crushed Stone DIA ≤ 25mm | A01ZZ009 | 00002 | A01ZZ009-00002 | AR | A01 | Earth Work | ZZ | - | 009 | Crushed Stone |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 87 | DIA ≤ 25mm | 0 | DIA=( )mm~( )mm or Max DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ009 | A01ZZ009-00002
|  |  |  | A01ZZ009 Earth Work - Crushed Stone | A01ZZ009-00003 Earth Work - Crushed Stone 25mm < DIA ≤ 100mm | A01ZZ009 | 00003 | A01ZZ009-00003 | AR | A01 | Earth Work | ZZ | - | 009 | Crushed Stone |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 88 | 25mm < DIA ≤ 100mm | 0 | DIA=( )mm~( )mm or Max DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ009 | A01ZZ009-00003
|  |  |  | A01ZZ010 Earth Work - Clean Sand for Cable Trench or UG Pipe | A01ZZ010-00001 Earth Work - Clean Sand for Cable Trench or UG Pipe | A01ZZ010 | 00001 | A01ZZ010-00001 | AR | A01 | Earth Work | ZZ | - | 010 | Clean Sand for Cable Trench or UG Pipe |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A01ZZ010 | A01ZZ010-00001
|  |  |  | A01ZZ011 Earth Work - Anti Termite Treatment | A01ZZ011-00001 Earth Work - Anti Termite Treatment | A01ZZ011 | 00001 | A01ZZ011-00001 | AR | A01 | Earth Work | ZZ | - | 011 | Anti Termite Treatment |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A01ZZ011 | A01ZZ011-00001
|  |  |  | A01ZZ012 Earth Work - PE Sheet (Vapor Barrier) | A01ZZ012-00002 Earth Work - PE Sheet (Vapor Barrier) THK ≤ 0.25mm (or 0.01 inch) | A01ZZ012 | 00002 | A01ZZ012-00002 | AR | A01 | Earth Work | ZZ | - | 012 | PE Sheet (Vapor Barrier) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 89 | THK ≤ 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A01ZZ012 | A01ZZ012-00002
|  |  |  | A01ZZ012 Earth Work - PE Sheet (Vapor Barrier) | A01ZZ012-00003 Earth Work - PE Sheet (Vapor Barrier) THK > 0.25mm (or 0.01 inch) | A01ZZ012 | 00003 | A01ZZ012-00003 | AR | A01 | Earth Work | ZZ | - | 012 | PE Sheet (Vapor Barrier) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 90 | THK > 0.25mm (or 0.01 inch) | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A01ZZ012 | A01ZZ012-00003
|  |  |  | A01ZZ013 Earth Work - Sheet Pile | A01ZZ013-00001 Earth Work - Sheet Pile To Comply with ASTM A 328, Including Dewatering | A01ZZ013 | 00001 | A01ZZ013-00001 | AR | A01 | Earth Work | ZZ | - | 013 | Sheet Pile |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 02 | To Comply with ASTM A 328, Including Dewatering |  | 0 |  | 0 | 0 | H=( )m | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A01ZZ013 | A01ZZ013-00001
|  |  |  | A01ZZ095 Earth Work - Geotextile | A01ZZ095-00001 Earth Work - Geotextile w/ Fixing Accessories | A01ZZ095 | 00001 | A01ZZ095-00001 | AR | A01 | Earth Work | ZZ | - | 095 | Geotextile |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A01ZZ095 | A01ZZ095-00001
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00007 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Direct Driving Including Pile Connection and Joint Welding Work 250 ≤ DIA <300 | A02AA014 | 00007 | A02AA014-00007 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 91 | 250 ≤ DIA <300 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00007
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00008 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Direct Driving Including Pile Connection and Joint Welding Work 300 ≤ DIA <350 | A02AA014 | 00008 | A02AA014-00008 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 92 | 300 ≤ DIA <350 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00008
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00009 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Direct Driving Including Pile Connection and Joint Welding Work 350 ≤ DIA <400 | A02AA014 | 00009 | A02AA014-00009 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 93 | 350 ≤ DIA <400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00009
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00010 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Direct Driving Including Pile Connection and Joint Welding Work 400 ≤ DIA <450 | A02AA014 | 00010 | A02AA014-00010 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 94 | 400 ≤ DIA <450 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00010
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00011 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Jacking Including Pile Connection and Joint Welding Work 250 ≤ DIA <300 | A02AA014 | 00011 | A02AA014-00011 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 91 | 250 ≤ DIA <300 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00011
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00012 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Jacking Including Pile Connection and Joint Welding Work 300 ≤ DIA <350 | A02AA014 | 00012 | A02AA014-00012 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 92 | 300 ≤ DIA <350 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00012
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00013 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Jacking Including Pile Connection and Joint Welding Work 350 ≤ DIA <400 | A02AA014 | 00013 | A02AA014-00013 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 93 | 350 ≤ DIA <400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00013
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Jacking Including Pile Connection and Joint Welding Work 400 ≤ DIA <450 | A02AA014 | 00014 | A02AA014-00014 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 94 | 400 ≤ DIA <450 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00014
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00015 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Augering without Casing Including Pile Connection and Joint Welding Work 250 ≤ DIA <300 | A02AA014 | 00015 | A02AA014-00015 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 91 | 250 ≤ DIA <300 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00015
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00016 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Augering without Casing Including Pile Connection and Joint Welding Work 300 ≤ DIA <350 | A02AA014 | 00016 | A02AA014-00016 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 92 | 300 ≤ DIA <350 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00016
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00017 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Augering without Casing Including Pile Connection and Joint Welding Work 350 ≤ DIA <400 | A02AA014 | 00017 | A02AA014-00017 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 93 | 350 ≤ DIA <400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00017
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00018 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Augering without Casing Including Pile Connection and Joint Welding Work 400 ≤ DIA <450 | A02AA014 | 00018 | A02AA014-00018 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 94 | 400 ≤ DIA <450 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00018
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00019 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Augering with Casing Including Pile Connection and Joint Welding Work 250 ≤ DIA <300 | A02AA014 | 00019 | A02AA014-00019 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 91 | 250 ≤ DIA <300 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00019
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00020 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Augering with Casing Including Pile Connection and Joint Welding Work 300 ≤ DIA <350 | A02AA014 | 00020 | A02AA014-00020 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 92 | 300 ≤ DIA <350 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00020
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00021 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Augering with Casing Including Pile Connection and Joint Welding Work 350 ≤ DIA <400 | A02AA014 | 00021 | A02AA014-00021 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 93 | 350 ≤ DIA <400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00021
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00022 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Augering with Casing Including Pile Connection and Joint Welding Work 400 ≤ DIA <450 | A02AA014 | 00022 | A02AA014-00022 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 94 | 400 ≤ DIA <450 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00022
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00023 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 250 ≤ DIA <300 | A02AA014 | 00023 | A02AA014-00023 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 91 | 250 ≤ DIA <300 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00023
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00024 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 300 ≤ DIA <350 | A02AA014 | 00024 | A02AA014-00024 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 92 | 300 ≤ DIA <350 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00024
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00025 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 350 ≤ DIA <400 | A02AA014 | 00025 | A02AA014-00025 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 93 | 350 ≤ DIA <400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00025
|  |  |  | A02AA014 Pile Work Piling Work Reinforced Concrete Pile (Round Type) | A02AA014-00026 Pile Work Piling Work Reinforced Concrete Pile (Round Type) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 400 ≤ DIA <450 | A02AA014 | 00026 | A02AA014-00026 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 94 | 400 ≤ DIA <450 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA014 | A02AA014-00026
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00004 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Direct Driving Including Pile Connection and Joint Welding Work SIZE <200 | A02AA015 | 00004 | A02AA015-00004 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 95 | SIZE <200 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00004
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00005 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Direct Driving Including Pile Connection and Joint Welding Work 200 ≤ SIZE <250 | A02AA015 | 00005 | A02AA015-00005 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 96 | 200 ≤ SIZE <250 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00005
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00006 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Direct Driving Including Pile Connection and Joint Welding Work 250 ≤ SIZE <300 | A02AA015 | 00006 | A02AA015-00006 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 97 | 250 ≤ SIZE <300 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00006
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00007 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Direct Driving Including Pile Connection and Joint Welding Work 300 ≤ SIZE <350 | A02AA015 | 00007 | A02AA015-00007 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 98 | 300 ≤ SIZE <350 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00007
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00008 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Direct Driving Including Pile Connection and Joint Welding Work 350 ≤ SIZE <400 | A02AA015 | 00008 | A02AA015-00008 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 99 | 350 ≤ SIZE <400 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00008
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00009 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Direct Driving Including Pile Connection and Joint Welding Work 400 ≤ SIZE <450 | A02AA015 | 00009 | A02AA015-00009 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AA | 400 ≤ SIZE <450 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00009
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00010 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Jacking Including Pile Connection and Joint Welding Work SIZE <200 | A02AA015 | 00010 | A02AA015-00010 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 95 | SIZE <200 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00010
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00011 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Jacking Including Pile Connection and Joint Welding Work 200 ≤ SIZE <250 | A02AA015 | 00011 | A02AA015-00011 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 96 | 200 ≤ SIZE <250 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00011
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00012 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Jacking Including Pile Connection and Joint Welding Work 250 ≤ SIZE <300 | A02AA015 | 00012 | A02AA015-00012 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 97 | 250 ≤ SIZE <300 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00012
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00013 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Jacking Including Pile Connection and Joint Welding Work 300 ≤ SIZE <350 | A02AA015 | 00013 | A02AA015-00013 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 98 | 300 ≤ SIZE <350 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00013
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00014 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Jacking Including Pile Connection and Joint Welding Work 350 ≤ SIZE <400 | A02AA015 | 00014 | A02AA015-00014 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 99 | 350 ≤ SIZE <400 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00014
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Jacking Including Pile Connection and Joint Welding Work 400 ≤ SIZE <450 | A02AA015 | 00015 | A02AA015-00015 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AA | 400 ≤ SIZE <450 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00015
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00016 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Augering without Casing Including Pile Connection and Joint Welding Work SIZE <200 | A02AA015 | 00016 | A02AA015-00016 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 95 | SIZE <200 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00016
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00017 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Augering without Casing Including Pile Connection and Joint Welding Work 200 ≤ SIZE <250 | A02AA015 | 00017 | A02AA015-00017 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 96 | 200 ≤ SIZE <250 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00017
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00018 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Augering without Casing Including Pile Connection and Joint Welding Work 250 ≤ SIZE <300 | A02AA015 | 00018 | A02AA015-00018 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 97 | 250 ≤ SIZE <300 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00018
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00019 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Augering without Casing Including Pile Connection and Joint Welding Work 300 ≤ SIZE <350 | A02AA015 | 00019 | A02AA015-00019 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 98 | 300 ≤ SIZE <350 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00019
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00020 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Augering without Casing Including Pile Connection and Joint Welding Work 350 ≤ SIZE <400 | A02AA015 | 00020 | A02AA015-00020 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 99 | 350 ≤ SIZE <400 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00020
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00021 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Augering without Casing Including Pile Connection and Joint Welding Work 400 ≤ SIZE <450 | A02AA015 | 00021 | A02AA015-00021 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AA | 400 ≤ SIZE <450 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00021
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00022 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Augering with Casing Including Pile Connection and Joint Welding Work SIZE <200 | A02AA015 | 00022 | A02AA015-00022 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 95 | SIZE <200 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00022
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00023 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Augering with Casing Including Pile Connection and Joint Welding Work 200 ≤ SIZE <250 | A02AA015 | 00023 | A02AA015-00023 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 96 | 200 ≤ SIZE <250 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00023
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00024 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Augering with Casing Including Pile Connection and Joint Welding Work 250 ≤ SIZE <300 | A02AA015 | 00024 | A02AA015-00024 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 97 | 250 ≤ SIZE <300 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00024
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00025 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Augering with Casing Including Pile Connection and Joint Welding Work 300 ≤ SIZE <350 | A02AA015 | 00025 | A02AA015-00025 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 98 | 300 ≤ SIZE <350 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00025
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00026 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Augering with Casing Including Pile Connection and Joint Welding Work 350 ≤ SIZE <400 | A02AA015 | 00026 | A02AA015-00026 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 99 | 350 ≤ SIZE <400 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00026
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00027 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Augering with Casing Including Pile Connection and Joint Welding Work 400 ≤ SIZE <450 | A02AA015 | 00027 | A02AA015-00027 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AA | 400 ≤ SIZE <450 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00027
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00028 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work SIZE <200 | A02AA015 | 00028 | A02AA015-00028 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 95 | SIZE <200 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00028
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00029 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 200 ≤ SIZE <250 | A02AA015 | 00029 | A02AA015-00029 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 96 | 200 ≤ SIZE <250 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00029
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00030 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 250 ≤ SIZE <300 | A02AA015 | 00030 | A02AA015-00030 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 97 | 250 ≤ SIZE <300 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00030
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00031 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 300 ≤ SIZE <350 | A02AA015 | 00031 | A02AA015-00031 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 98 | 300 ≤ SIZE <350 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00031
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00032 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 350 ≤ SIZE <400 | A02AA015 | 00032 | A02AA015-00032 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 99 | 350 ≤ SIZE <400 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00032
|  |  |  | A02AA015 Pile Work Piling Work Reinforced Concrete Pile (Square Type) | A02AA015-00033 Pile Work Piling Work Reinforced Concrete Pile (Square Type) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 400 ≤ SIZE <450 | A02AA015 | 00033 | A02AA015-00033 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AA | 400 ≤ SIZE <450 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA015 | A02AA015-00033
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00007 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work DIA<400 | A02AA016 | 00007 | A02AA016-00007 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00007
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00008 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA016 | 00008 | A02AA016-00008 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00008
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00009 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA016 | 00009 | A02AA016-00009 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00009
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00010 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA016 | 00010 | A02AA016-00010 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00010
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00011 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA016 | 00011 | A02AA016-00011 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00011
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00012 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA016 | 00012 | A02AA016-00012 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00012
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00013 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA016 | 00013 | A02AA016-00013 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00013
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00014 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA016 | 00014 | A02AA016-00014 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00014
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00015 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Jacking Including Pile Connection and Joint Welding Work DIA<400 | A02AA016 | 00015 | A02AA016-00015 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00015
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Jacking Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA016 | 00016 | A02AA016-00016 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00016
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00017 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Jacking Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA016 | 00017 | A02AA016-00017 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00017
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00018 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Jacking Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA016 | 00018 | A02AA016-00018 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00018
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00019 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Jacking Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA016 | 00019 | A02AA016-00019 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00019
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00020 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Jacking Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA016 | 00020 | A02AA016-00020 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00020
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00021 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Jacking Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA016 | 00021 | A02AA016-00021 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00021
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00022 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Jacking Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA016 | 00022 | A02AA016-00022 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00022
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00023 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work DIA<400 | A02AA016 | 00023 | A02AA016-00023 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00023
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00024 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA016 | 00024 | A02AA016-00024 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00024
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00025 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA016 | 00025 | A02AA016-00025 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00025
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00026 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA016 | 00026 | A02AA016-00026 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00026
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00027 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA016 | 00027 | A02AA016-00027 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00027
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00028 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA016 | 00028 | A02AA016-00028 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00028
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00029 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA016 | 00029 | A02AA016-00029 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00029
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00030 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA016 | 00030 | A02AA016-00030 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00030
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00031 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Augering with Casing Including Pile Connection and Joint Welding Work DIA<400 | A02AA016 | 00031 | A02AA016-00031 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00031
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00032 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Augering with Casing Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA016 | 00032 | A02AA016-00032 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00032
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00033 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Augering with Casing Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA016 | 00033 | A02AA016-00033 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00033
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00034 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Augering with Casing Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA016 | 00034 | A02AA016-00034 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00034
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00035 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Augering with Casing Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA016 | 00035 | A02AA016-00035 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00035
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00036 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Augering with Casing Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA016 | 00036 | A02AA016-00036 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00036
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00037 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Augering with Casing Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA016 | 00037 | A02AA016-00037 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00037
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00038 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Augering with Casing Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA016 | 00038 | A02AA016-00038 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00038
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00039 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work DIA<400 | A02AA016 | 00039 | A02AA016-00039 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00039
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00040 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA016 | 00040 | A02AA016-00040 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00040
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00041 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA016 | 00041 | A02AA016-00041 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00041
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00042 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA016 | 00042 | A02AA016-00042 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00042
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00043 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA016 | 00043 | A02AA016-00043 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00043
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00044 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA016 | 00044 | A02AA016-00044 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00044
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00045 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA016 | 00045 | A02AA016-00045 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00045
|  |  |  | A02AA016 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) | A02AA016-00046 Pile Work Piling Work Pretensioned Concrete Pile (Type-A) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA016 | 00046 | A02AA016-00046 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA016 | A02AA016-00046
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00007 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Direct Driving Including Pile Connection and Joint Welding Work DIA<400 | A02AA017 | 00007 | A02AA017-00007 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00007
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00008 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Direct Driving Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA017 | 00008 | A02AA017-00008 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00008
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00009 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Direct Driving Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA017 | 00009 | A02AA017-00009 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00009
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00010 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Direct Driving Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA017 | 00010 | A02AA017-00010 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00010
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00011 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Direct Driving Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA017 | 00011 | A02AA017-00011 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00011
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00012 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Direct Driving Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA017 | 00012 | A02AA017-00012 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00012
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00013 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Direct Driving Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA017 | 00013 | A02AA017-00013 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00013
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00014 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Direct Driving Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA017 | 00014 | A02AA017-00014 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00014
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00015 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Jacking Including Pile Connection and Joint Welding Work DIA<400 | A02AA017 | 00015 | A02AA017-00015 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00015
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00016 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Jacking Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA017 | 00016 | A02AA017-00016 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00016
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Jacking Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA017 | 00017 | A02AA017-00017 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00017
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00018 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Jacking Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA017 | 00018 | A02AA017-00018 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00018
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00019 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Jacking Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA017 | 00019 | A02AA017-00019 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00019
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00020 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Jacking Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA017 | 00020 | A02AA017-00020 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00020
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00021 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Jacking Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA017 | 00021 | A02AA017-00021 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00021
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00022 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Jacking Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA017 | 00022 | A02AA017-00022 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00022
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00023 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Augering without Casing Including Pile Connection and Joint Welding Work DIA<400 | A02AA017 | 00023 | A02AA017-00023 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00023
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00024 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Augering without Casing Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA017 | 00024 | A02AA017-00024 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00024
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00025 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Augering without Casing Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA017 | 00025 | A02AA017-00025 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00025
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00026 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Augering without Casing Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA017 | 00026 | A02AA017-00026 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00026
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00027 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Augering without Casing Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA017 | 00027 | A02AA017-00027 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00027
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00028 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Augering without Casing Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA017 | 00028 | A02AA017-00028 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00028
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00029 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Augering without Casing Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA017 | 00029 | A02AA017-00029 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00029
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00030 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Augering without Casing Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA017 | 00030 | A02AA017-00030 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00030
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00031 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Augering with Casing Including Pile Connection and Joint Welding Work DIA<400 | A02AA017 | 00031 | A02AA017-00031 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00031
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00032 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Augering with Casing Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA017 | 00032 | A02AA017-00032 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00032
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00033 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Augering with Casing Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA017 | 00033 | A02AA017-00033 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00033
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00034 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Augering with Casing Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA017 | 00034 | A02AA017-00034 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00034
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00035 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Augering with Casing Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA017 | 00035 | A02AA017-00035 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00035
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00036 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Augering with Casing Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA017 | 00036 | A02AA017-00036 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00036
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00037 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Augering with Casing Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA017 | 00037 | A02AA017-00037 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00037
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00038 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Augering with Casing Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA017 | 00038 | A02AA017-00038 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00038
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00039 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work DIA<400 | A02AA017 | 00039 | A02AA017-00039 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00039
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00040 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA017 | 00040 | A02AA017-00040 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00040
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00041 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA017 | 00041 | A02AA017-00041 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00041
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00042 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA017 | 00042 | A02AA017-00042 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00042
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00043 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA017 | 00043 | A02AA017-00043 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00043
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00044 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA017 | 00044 | A02AA017-00044 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00044
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00045 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA017 | 00045 | A02AA017-00045 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00045
|  |  |  | A02AA017 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) | A02AA017-00046 Pile Work Piling Work Pretensioned Concrete Pile (Type-B) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA017 | 00046 | A02AA017-00046 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA017 | A02AA017-00046
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00007 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work DIA<400 | A02AA018 | 00007 | A02AA018-00007 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00007
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00008 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA018 | 00008 | A02AA018-00008 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00008
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00009 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA018 | 00009 | A02AA018-00009 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00009
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00010 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA018 | 00010 | A02AA018-00010 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00010
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00011 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA018 | 00011 | A02AA018-00011 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00011
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00012 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA018 | 00012 | A02AA018-00012 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00012
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00013 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA018 | 00013 | A02AA018-00013 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00013
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00014 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Direct Driving Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA018 | 00014 | A02AA018-00014 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00014
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00015 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Jacking Including Pile Connection and Joint Welding Work DIA<400 | A02AA018 | 00015 | A02AA018-00015 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00015
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00016 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Jacking Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA018 | 00016 | A02AA018-00016 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00016
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00017 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Jacking Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA018 | 00017 | A02AA018-00017 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00017
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Jacking Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA018 | 00018 | A02AA018-00018 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00018
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Jacking Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA018 | 00019 | A02AA018-00019 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00019
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00020 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Jacking Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA018 | 00020 | A02AA018-00020 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00020
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00021 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Jacking Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA018 | 00021 | A02AA018-00021 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00021
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00022 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Jacking Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA018 | 00022 | A02AA018-00022 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00022
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00023 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work DIA<400 | A02AA018 | 00023 | A02AA018-00023 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00023
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00024 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA018 | 00024 | A02AA018-00024 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00024
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00025 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA018 | 00025 | A02AA018-00025 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00025
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00026 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA018 | 00026 | A02AA018-00026 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00026
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00027 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA018 | 00027 | A02AA018-00027 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00027
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00028 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA018 | 00028 | A02AA018-00028 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00028
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00029 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA018 | 00029 | A02AA018-00029 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00029
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00030 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering without Casing Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA018 | 00030 | A02AA018-00030 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00030
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00031 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering with Casing Including Pile Connection and Joint Welding Work DIA<400 | A02AA018 | 00031 | A02AA018-00031 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00031
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00032 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering with Casing Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA018 | 00032 | A02AA018-00032 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00032
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00033 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering with Casing Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA018 | 00033 | A02AA018-00033 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00033
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00034 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering with Casing Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA018 | 00034 | A02AA018-00034 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00034
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00035 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering with Casing Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA018 | 00035 | A02AA018-00035 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00035
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00036 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering with Casing Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA018 | 00036 | A02AA018-00036 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00036
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00037 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering with Casing Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA018 | 00037 | A02AA018-00037 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00037
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00038 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Augering with Casing Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA018 | 00038 | A02AA018-00038 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00038
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00039 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work DIA<400 | A02AA018 | 00039 | A02AA018-00039 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00039
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00040 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA018 | 00040 | A02AA018-00040 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00040
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00041 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA018 | 00041 | A02AA018-00041 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00041
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00042 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA018 | 00042 | A02AA018-00042 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00042
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00043 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA018 | 00043 | A02AA018-00043 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00043
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00044 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA018 | 00044 | A02AA018-00044 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00044
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00045 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA018 | 00045 | A02AA018-00045 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00045
|  |  |  | A02AA018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) | A02AA018-00046 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-A) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA018 | 00046 | A02AA018-00046 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA018 | A02AA018-00046
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00007 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Direct Driving Including Pile Connection and Joint Welding Work DIA<400 | A02AA019 | 00007 | A02AA019-00007 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00007
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00008 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Direct Driving Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA019 | 00008 | A02AA019-00008 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00008
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00009 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Direct Driving Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA019 | 00009 | A02AA019-00009 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00009
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00010 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Direct Driving Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA019 | 00010 | A02AA019-00010 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00010
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00011 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Direct Driving Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA019 | 00011 | A02AA019-00011 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00011
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00012 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Direct Driving Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA019 | 00012 | A02AA019-00012 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00012
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00013 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Direct Driving Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA019 | 00013 | A02AA019-00013 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00013
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00014 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Direct Driving Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA019 | 00014 | A02AA019-00014 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00014
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00015 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Jacking Including Pile Connection and Joint Welding Work DIA<400 | A02AA019 | 00015 | A02AA019-00015 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00015
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00016 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Jacking Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA019 | 00016 | A02AA019-00016 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00016
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00017 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Jacking Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA019 | 00017 | A02AA019-00017 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00017
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00018 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Jacking Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA019 | 00018 | A02AA019-00018 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00018
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Jacking Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA019 | 00019 | A02AA019-00019 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00019
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00020 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Jacking Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA019 | 00020 | A02AA019-00020 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00020
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00021 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Jacking Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA019 | 00021 | A02AA019-00021 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00021
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00022 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Jacking Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA019 | 00022 | A02AA019-00022 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 13 | Jacking |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00022
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00023 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Augering without Casing Including Pile Connection and Joint Welding Work DIA<400 | A02AA019 | 00023 | A02AA019-00023 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00023
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00024 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Augering without Casing Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA019 | 00024 | A02AA019-00024 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00024
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00025 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Augering without Casing Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA019 | 00025 | A02AA019-00025 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00025
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00026 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Augering without Casing Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA019 | 00026 | A02AA019-00026 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00026
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00027 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Augering without Casing Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA019 | 00027 | A02AA019-00027 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00027
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00028 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Augering without Casing Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA019 | 00028 | A02AA019-00028 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00028
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00029 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Augering without Casing Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA019 | 00029 | A02AA019-00029 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00029
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00030 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Augering without Casing Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA019 | 00030 | A02AA019-00030 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FL | Augering without Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00030
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00031 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Augering with Casing Including Pile Connection and Joint Welding Work DIA<400 | A02AA019 | 00031 | A02AA019-00031 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00031
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00032 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Augering with Casing Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA019 | 00032 | A02AA019-00032 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00032
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00033 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Augering with Casing Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA019 | 00033 | A02AA019-00033 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00033
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00034 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Augering with Casing Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA019 | 00034 | A02AA019-00034 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00034
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00035 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Augering with Casing Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA019 | 00035 | A02AA019-00035 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00035
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00036 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Augering with Casing Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA019 | 00036 | A02AA019-00036 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00036
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00037 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Augering with Casing Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA019 | 00037 | A02AA019-00037 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00037
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00038 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Augering with Casing Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA019 | 00038 | A02AA019-00038 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FM | Augering with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00038
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00039 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work DIA<400 | A02AA019 | 00039 | A02AA019-00039 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00039
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00040 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA019 | 00040 | A02AA019-00040 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00040
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00041 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA019 | 00041 | A02AA019-00041 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00041
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00042 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA019 | 00042 | A02AA019-00042 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00042
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00043 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA019 | 00043 | A02AA019-00043 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00043
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00044 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA019 | 00044 | A02AA019-00044 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00044
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00045 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA019 | 00045 | A02AA019-00045 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00045
|  |  |  | A02AA019 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) | A02AA019-00046 Pile Work Piling Work Pretensioned High-strength Concrete Pile (Type-B) Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA019 | 00046 | A02AA019-00046 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA019 | A02AA019-00046
|  |  |  | A02AA020 Pile Work Piling Work Steel Pipe Pile Work | A02AA020-00002 Pile Work Piling Work Steel Pipe Pile Work Direct Driving Including Pile Connection and Joint Welding Work DIA<400 | A02AA020 | 00002 | A02AA020-00002 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA020 | A02AA020-00002
|  |  |  | A02AA020 Pile Work Piling Work Steel Pipe Pile Work | A02AA020-00003 Pile Work Piling Work Steel Pipe Pile Work Direct Driving Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA020 | 00003 | A02AA020-00003 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA020 | A02AA020-00003
|  |  |  | A02AA020 Pile Work Piling Work Steel Pipe Pile Work | A02AA020-00004 Pile Work Piling Work Steel Pipe Pile Work Direct Driving Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA020 | 00004 | A02AA020-00004 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA020 | A02AA020-00004
|  |  |  | A02AA020 Pile Work Piling Work Steel Pipe Pile Work | A02AA020-00005 Pile Work Piling Work Steel Pipe Pile Work Direct Driving Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA020 | 00005 | A02AA020-00005 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA020 | A02AA020-00005
|  |  |  | A02AA020 Pile Work Piling Work Steel Pipe Pile Work | A02AA020-00006 Pile Work Piling Work Steel Pipe Pile Work Direct Driving Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA020 | 00006 | A02AA020-00006 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA020 | A02AA020-00006
|  |  |  | A02AA020 Pile Work Piling Work Steel Pipe Pile Work | A02AA020-00007 Pile Work Piling Work Steel Pipe Pile Work Direct Driving Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA020 | 00007 | A02AA020-00007 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA020 | A02AA020-00007
|  |  |  | A02AA020 Pile Work Piling Work Steel Pipe Pile Work | A02AA020-00008 Pile Work Piling Work Steel Pipe Pile Work Direct Driving Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA020 | 00008 | A02AA020-00008 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA020 | A02AA020-00008
|  |  |  | A02AA020 Pile Work Piling Work Steel Pipe Pile Work | A02AA020-00009 Pile Work Piling Work Steel Pipe Pile Work Direct Driving Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA020 | 00009 | A02AA020-00009 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA020 | A02AA020-00009
|  |  |  | A02AA020 Pile Work Piling Work Steel Pipe Pile Work | A02AA020-00010 Pile Work Piling Work Steel Pipe Pile Work Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work DIA<400 | A02AA020 | 00010 | A02AA020-00010 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA020 | A02AA020-00010
|  |  |  | A02AA020 Pile Work Piling Work Steel Pipe Pile Work | A02AA020-00011 Pile Work Piling Work Steel Pipe Pile Work Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA020 | 00011 | A02AA020-00011 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA020 | A02AA020-00011
|  |  |  | A02AA020 Pile Work Piling Work Steel Pipe Pile Work | A02AA020-00012 Pile Work Piling Work Steel Pipe Pile Work Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA020 | 00012 | A02AA020-00012 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA020 | A02AA020-00012
|  |  |  | A02AA020 Pile Work Piling Work Steel Pipe Pile Work | A02AA020-00013 Pile Work Piling Work Steel Pipe Pile Work Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA020 | 00013 | A02AA020-00013 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA020 | A02AA020-00013
|  |  |  | A02AA020 Pile Work Piling Work Steel Pipe Pile Work | A02AA020-00014 Pile Work Piling Work Steel Pipe Pile Work Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA020 | 00014 | A02AA020-00014 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA020 | A02AA020-00014
|  |  |  | A02AA020 Pile Work Piling Work Steel Pipe Pile Work | A02AA020-00015 Pile Work Piling Work Steel Pipe Pile Work Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA020 | 00015 | A02AA020-00015 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA020 | A02AA020-00015
|  |  |  | A02AA020 Pile Work Piling Work Steel Pipe Pile Work | A02AA020-00016 Pile Work Piling Work Steel Pipe Pile Work Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA020 | 00016 | A02AA020-00016 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA020 | A02AA020-00016
|  |  |  | A02AA020 Pile Work Piling Work Steel Pipe Pile Work | A02AA020-00017 Pile Work Piling Work Steel Pipe Pile Work Percussion Rotary Drilling with Casing Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA020 | 00017 | A02AA020-00017 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | FN | Percussion Rotary Drilling with Casing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA020 | A02AA020-00017
|  |  |  | A02AA021 Pile Work Piling Work H-Pile Work | A02AA021-00002 Pile Work Piling Work H-Pile Work Direct Driving Including Pile Connection and Joint Welding Work SIZE <200 | A02AA021 | 00002 | A02AA021-00002 | AR | A02 | Pile Work | AA | Piling Work | 021 | H-Pile Work | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 95 | SIZE <200 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA021 | A02AA021-00002
|  |  |  | A02AA021 Pile Work Piling Work H-Pile Work | A02AA021-00003 Pile Work Piling Work H-Pile Work Direct Driving Including Pile Connection and Joint Welding Work 200 ≤ SIZE <250 | A02AA021 | 00003 | A02AA021-00003 | AR | A02 | Pile Work | AA | Piling Work | 021 | H-Pile Work | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 96 | 200 ≤ SIZE <250 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA021 | A02AA021-00003
|  |  |  | A02AA021 Pile Work Piling Work H-Pile Work | A02AA021-00004 Pile Work Piling Work H-Pile Work Direct Driving Including Pile Connection and Joint Welding Work 250 ≤ SIZE <300 | A02AA021 | 00004 | A02AA021-00004 | AR | A02 | Pile Work | AA | Piling Work | 021 | H-Pile Work | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 97 | 250 ≤ SIZE <300 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA021 | A02AA021-00004
|  |  |  | A02AA021 Pile Work Piling Work H-Pile Work | A02AA021-00005 Pile Work Piling Work H-Pile Work Direct Driving Including Pile Connection and Joint Welding Work 300 ≤ SIZE <350 | A02AA021 | 00005 | A02AA021-00005 | AR | A02 | Pile Work | AA | Piling Work | 021 | H-Pile Work | 11 | Direct Driving |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 98 | 300 ≤ SIZE <350 | 0 | Size=( )mm x ( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA021 | A02AA021-00005
|  |  |  | A02AA022 Pile Work Piling Work Micro Pile Work | A02AA022-00002 Pile Work Piling Work Micro Pile Work Boring and Pressure Grouting Including Pile Connection and Joint Welding Work DIA<150 | A02AA022 | 00002 | A02AA022-00002 | AR | A02 | Pile Work | AA | Piling Work | 022 | Micro Pile Work | FP | Boring and Pressure Grouting |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AK | DIA<150 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA022 | A02AA022-00002
|  |  |  | A02AA022 Pile Work Piling Work Micro Pile Work | A02AA022-00003 Pile Work Piling Work Micro Pile Work Boring and Pressure Grouting Including Pile Connection and Joint Welding Work 150 ≤ DIA <200 | A02AA022 | 00003 | A02AA022-00003 | AR | A02 | Pile Work | AA | Piling Work | 022 | Micro Pile Work | FP | Boring and Pressure Grouting |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AL | 150 ≤ DIA <200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA022 | A02AA022-00003
|  |  |  | A02AA022 Pile Work Piling Work Micro Pile Work | A02AA022-00004 Pile Work Piling Work Micro Pile Work Boring and Post Grouting Including Pile Connection and Joint Welding Work 200 ≤ DIA <250 | A02AA022 | 00004 | A02AA022-00004 | AR | A02 | Pile Work | AA | Piling Work | 022 | Micro Pile Work | FQ | Boring and Post Grouting |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AM | 200 ≤ DIA <250 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA022 | A02AA022-00004
|  |  |  | A02AA022 Pile Work Piling Work Micro Pile Work | A02AA022-00005 Pile Work Piling Work Micro Pile Work Boring and Post Grouting Including Pile Connection and Joint Welding Work 250 ≤ DIA <300 | A02AA022 | 00005 | A02AA022-00005 | AR | A02 | Pile Work | AA | Piling Work | 022 | Micro Pile Work | FQ | Boring and Post Grouting |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | 91 | 250 ≤ DIA <300 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA022 | A02AA022-00005
|  |  |  | A02AA022 Pile Work Piling Work Micro Pile Work | A02AA022-00006 Pile Work Piling Work Micro Pile Work Boring and Post Grouting Including Pile Connection and Joint Welding Work 300 ≤ DIA | A02AA022 | 00006 | A02AA022-00006 | AR | A02 | Pile Work | AA | Piling Work | 022 | Micro Pile Work | FQ | Boring and Post Grouting |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AN | 300 ≤ DIA | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA022 | A02AA022-00006
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00008 Pile Work Piling Work Cast-In-Place Pile Work R.C.D Method Including Pile Connection and Joint Welding Work DIA<400 | A02AA023 | 00008 | A02AA023-00008 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 18 | R.C.D Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00008
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00009 Pile Work Piling Work Cast-In-Place Pile Work R.C.D Method Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA023 | 00009 | A02AA023-00009 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 18 | R.C.D Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00009
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00010 Pile Work Piling Work Cast-In-Place Pile Work R.C.D Method Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA023 | 00010 | A02AA023-00010 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 18 | R.C.D Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00010
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00011 Pile Work Piling Work Cast-In-Place Pile Work R.C.D Method Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA023 | 00011 | A02AA023-00011 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 18 | R.C.D Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00011
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00012 Pile Work Piling Work Cast-In-Place Pile Work R.C.D Method Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA023 | 00012 | A02AA023-00012 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 18 | R.C.D Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00012
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00013 Pile Work Piling Work Cast-In-Place Pile Work R.C.D Method Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA023 | 00013 | A02AA023-00013 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 18 | R.C.D Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00013
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00014 Pile Work Piling Work Cast-In-Place Pile Work R.C.D Method Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA023 | 00014 | A02AA023-00014 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 18 | R.C.D Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00014
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00015 Pile Work Piling Work Cast-In-Place Pile Work R.C.D Method Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA023 | 00015 | A02AA023-00015 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 18 | R.C.D Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00015
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00016 Pile Work Piling Work Cast-In-Place Pile Work R.C.D Method Including Pile Connection and Joint Welding Work 1200 ≤ DIA <1500 | A02AA023 | 00016 | A02AA023-00016 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 18 | R.C.D Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AP | 1200 ≤ DIA <1500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00016
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00017 Pile Work Piling Work Cast-In-Place Pile Work R.C.D Method Including Pile Connection and Joint Welding Work 1500 ≤ DIA <1800 | A02AA023 | 00017 | A02AA023-00017 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 18 | R.C.D Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AQ | 1500 ≤ DIA <1800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00017
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00018 Pile Work Piling Work Cast-In-Place Pile Work R.C.D Method Including Pile Connection and Joint Welding Work 1800 ≤ DIA <2000 | A02AA023 | 00018 | A02AA023-00018 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 18 | R.C.D Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AR | 1800 ≤ DIA <2000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00018
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00019 Pile Work Piling Work Cast-In-Place Pile Work R.C.D Method Including Pile Connection and Joint Welding Work 2000 ≤ DIA | A02AA023 | 00019 | A02AA023-00019 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 18 | R.C.D Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AS | 2000 ≤ DIA | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00019
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00020 Pile Work Piling Work Cast-In-Place Pile Work Beneto Method Including Pile Connection and Joint Welding Work DIA<400 | A02AA023 | 00020 | A02AA023-00020 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 19 | Beneto Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00020
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00021 Pile Work Piling Work Cast-In-Place Pile Work Beneto Method Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA023 | 00021 | A02AA023-00021 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 19 | Beneto Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00021
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00022 Pile Work Piling Work Cast-In-Place Pile Work Beneto Method Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA023 | 00022 | A02AA023-00022 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 19 | Beneto Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00022
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00023 Pile Work Piling Work Cast-In-Place Pile Work Beneto Method Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA023 | 00023 | A02AA023-00023 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 19 | Beneto Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00023
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00024 Pile Work Piling Work Cast-In-Place Pile Work Beneto Method Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA023 | 00024 | A02AA023-00024 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 19 | Beneto Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00024
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00025 Pile Work Piling Work Cast-In-Place Pile Work Beneto Method Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA023 | 00025 | A02AA023-00025 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 19 | Beneto Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00025
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00026 Pile Work Piling Work Cast-In-Place Pile Work Beneto Method Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA023 | 00026 | A02AA023-00026 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 19 | Beneto Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00026
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00027 Pile Work Piling Work Cast-In-Place Pile Work Beneto Method Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA023 | 00027 | A02AA023-00027 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 19 | Beneto Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00027
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00028 Pile Work Piling Work Cast-In-Place Pile Work Beneto Method Including Pile Connection and Joint Welding Work 1200 ≤ DIA <1500 | A02AA023 | 00028 | A02AA023-00028 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 19 | Beneto Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AP | 1200 ≤ DIA <1500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00028
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00029 Pile Work Piling Work Cast-In-Place Pile Work Beneto Method Including Pile Connection and Joint Welding Work 1500 ≤ DIA <1800 | A02AA023 | 00029 | A02AA023-00029 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 19 | Beneto Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AQ | 1500 ≤ DIA <1800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00029
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00030 Pile Work Piling Work Cast-In-Place Pile Work Beneto Method Including Pile Connection and Joint Welding Work 1800 ≤ DIA <2000 | A02AA023 | 00030 | A02AA023-00030 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 19 | Beneto Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AR | 1800 ≤ DIA <2000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00030
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00031 Pile Work Piling Work Cast-In-Place Pile Work Beneto Method Including Pile Connection and Joint Welding Work 2000 ≤ DIA | A02AA023 | 00031 | A02AA023-00031 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 19 | Beneto Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AS | 2000 ≤ DIA | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00031
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00032 Pile Work Piling Work Cast-In-Place Pile Work Earth Drill Method Including Pile Connection and Joint Welding Work DIA<400 | A02AA023 | 00032 | A02AA023-00032 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 20 | Earth Drill Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00032
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00033 Pile Work Piling Work Cast-In-Place Pile Work Earth Drill Method Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA023 | 00033 | A02AA023-00033 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 20 | Earth Drill Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00033
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00034 Pile Work Piling Work Cast-In-Place Pile Work Earth Drill Method Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA023 | 00034 | A02AA023-00034 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 20 | Earth Drill Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00034
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00035 Pile Work Piling Work Cast-In-Place Pile Work Earth Drill Method Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA023 | 00035 | A02AA023-00035 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 20 | Earth Drill Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00035
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00036 Pile Work Piling Work Cast-In-Place Pile Work Earth Drill Method Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA023 | 00036 | A02AA023-00036 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 20 | Earth Drill Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00036
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00037 Pile Work Piling Work Cast-In-Place Pile Work Earth Drill Method Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA023 | 00037 | A02AA023-00037 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 20 | Earth Drill Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00037
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00038 Pile Work Piling Work Cast-In-Place Pile Work Earth Drill Method Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA023 | 00038 | A02AA023-00038 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 20 | Earth Drill Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00038
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00039 Pile Work Piling Work Cast-In-Place Pile Work Earth Drill Method Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA023 | 00039 | A02AA023-00039 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 20 | Earth Drill Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00039
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00040 Pile Work Piling Work Cast-In-Place Pile Work Earth Drill Method Including Pile Connection and Joint Welding Work 1200 ≤ DIA <1500 | A02AA023 | 00040 | A02AA023-00040 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 20 | Earth Drill Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AP | 1200 ≤ DIA <1500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00040
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00041 Pile Work Piling Work Cast-In-Place Pile Work Earth Drill Method Including Pile Connection and Joint Welding Work 1500 ≤ DIA <1800 | A02AA023 | 00041 | A02AA023-00041 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 20 | Earth Drill Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AQ | 1500 ≤ DIA <1800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00041
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00042 Pile Work Piling Work Cast-In-Place Pile Work Earth Drill Method Including Pile Connection and Joint Welding Work 1800 ≤ DIA <2000 | A02AA023 | 00042 | A02AA023-00042 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 20 | Earth Drill Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AR | 1800 ≤ DIA <2000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00042
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00043 Pile Work Piling Work Cast-In-Place Pile Work Earth Drill Method Including Pile Connection and Joint Welding Work 2000 ≤ DIA | A02AA023 | 00043 | A02AA023-00043 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 20 | Earth Drill Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AS | 2000 ≤ DIA | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00043
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00044 Pile Work Piling Work Cast-In-Place Pile Work Continious Flight Auger Method Including Pile Connection and Joint Welding Work DIA<400 | A02AA023 | 00044 | A02AA023-00044 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | FR | Continious Flight Auger Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00044
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00045 Pile Work Piling Work Cast-In-Place Pile Work Continious Flight Auger Method Including Pile Connection and Joint Welding Work 400 ≤ DIA <500 | A02AA023 | 00045 | A02AA023-00045 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | FR | Continious Flight Auger Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00045
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00046 Pile Work Piling Work Cast-In-Place Pile Work Continious Flight Auger Method Including Pile Connection and Joint Welding Work 500 ≤ DIA <600 | A02AA023 | 00046 | A02AA023-00046 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | FR | Continious Flight Auger Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00046
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00047 Pile Work Piling Work Cast-In-Place Pile Work Continious Flight Auger Method Including Pile Connection and Joint Welding Work 600 ≤ DIA <700 | A02AA023 | 00047 | A02AA023-00047 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | FR | Continious Flight Auger Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00047
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00048 Pile Work Piling Work Cast-In-Place Pile Work Continious Flight Auger Method Including Pile Connection and Joint Welding Work 700 ≤ DIA <800 | A02AA023 | 00048 | A02AA023-00048 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | FR | Continious Flight Auger Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00048
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00049 Pile Work Piling Work Cast-In-Place Pile Work Continious Flight Auger Method Including Pile Connection and Joint Welding Work 800 ≤ DIA <900 | A02AA023 | 00049 | A02AA023-00049 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | FR | Continious Flight Auger Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00049
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00050 Pile Work Piling Work Cast-In-Place Pile Work Continious Flight Auger Method Including Pile Connection and Joint Welding Work 900 ≤ DIA <1000 | A02AA023 | 00050 | A02AA023-00050 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | FR | Continious Flight Auger Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00050
|  |  |  | A02AA023 Pile Work Piling Work Cast-In-Place Pile Work | A02AA023-00051 Pile Work Piling Work Cast-In-Place Pile Work Continious Flight Auger Method Including Pile Connection and Joint Welding Work 1000 ≤ DIA <1200 | A02AA023 | 00051 | A02AA023-00051 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | FR | Continious Flight Auger Method |  | 0 |  | 0 |  | 0 |  | 0 | 03 | Including Pile Connection and Joint Welding Work |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | Pile Length per Hole=( )M | 0 | 0 | 0 | 0 | 0 |  | M | M | A02AA023 | A02AA023-00051
|  |  |  | A02AB014 Pile Work Pile Head Treatment Reinforced Concrete Pile (Round Type) | A02AB014-00002 Pile Work Pile Head Treatment Reinforced Concrete Pile (Round Type) 250 ≤ DIA <300 | A02AB014 | 00002 | A02AB014-00002 | AR | A02 | Pile Work | AB | Pile Head Treatment | 014 | Reinforced Concrete Pile (Round Type) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 91 | 250 ≤ DIA <300 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB014 | A02AB014-00002
|  |  |  | A02AB014 Pile Work Pile Head Treatment Reinforced Concrete Pile (Round Type) | A02AB014-00003 Pile Work Pile Head Treatment Reinforced Concrete Pile (Round Type) 300 ≤ DIA <350 | A02AB014 | 00003 | A02AB014-00003 | AR | A02 | Pile Work | AB | Pile Head Treatment | 014 | Reinforced Concrete Pile (Round Type) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 92 | 300 ≤ DIA <350 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB014 | A02AB014-00003
|  |  |  | A02AB014 Pile Work Pile Head Treatment Reinforced Concrete Pile (Round Type) | A02AB014-00004 Pile Work Pile Head Treatment Reinforced Concrete Pile (Round Type) 350 ≤ DIA <400 | A02AB014 | 00004 | A02AB014-00004 | AR | A02 | Pile Work | AB | Pile Head Treatment | 014 | Reinforced Concrete Pile (Round Type) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 93 | 350 ≤ DIA <400 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB014 | A02AB014-00004
|  |  |  | A02AB014 Pile Work Pile Head Treatment Reinforced Concrete Pile (Round Type) | A02AB014-00005 Pile Work Pile Head Treatment Reinforced Concrete Pile (Round Type) 400 ≤ DIA <450 | A02AB014 | 00005 | A02AB014-00005 | AR | A02 | Pile Work | AB | Pile Head Treatment | 014 | Reinforced Concrete Pile (Round Type) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 94 | 400 ≤ DIA <450 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB014 | A02AB014-00005
|  |  |  | A02AB015 Pile Work Pile Head Treatment Reinforced Concrete Pile (Square Type) | A02AB015-00002 Pile Work Pile Head Treatment Reinforced Concrete Pile (Square Type) SIZE <200 | A02AB015 | 00002 | A02AB015-00002 | AR | A02 | Pile Work | AB | Pile Head Treatment | 015 | Reinforced Concrete Pile (Square Type) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 95 | SIZE <200 | 0 | Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB015 | A02AB015-00002
|  |  |  | A02AB015 Pile Work Pile Head Treatment Reinforced Concrete Pile (Square Type) | A02AB015-00003 Pile Work Pile Head Treatment Reinforced Concrete Pile (Square Type) 200 ≤ SIZE <250 | A02AB015 | 00003 | A02AB015-00003 | AR | A02 | Pile Work | AB | Pile Head Treatment | 015 | Reinforced Concrete Pile (Square Type) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 96 | 200 ≤ SIZE <250 | 0 | Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB015 | A02AB015-00003
|  |  |  | A02AB015 Pile Work Pile Head Treatment Reinforced Concrete Pile (Square Type) | A02AB015-00004 Pile Work Pile Head Treatment Reinforced Concrete Pile (Square Type) 250 ≤ SIZE <300 | A02AB015 | 00004 | A02AB015-00004 | AR | A02 | Pile Work | AB | Pile Head Treatment | 015 | Reinforced Concrete Pile (Square Type) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 97 | 250 ≤ SIZE <300 | 0 | Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB015 | A02AB015-00004
|  |  |  | A02AB015 Pile Work Pile Head Treatment Reinforced Concrete Pile (Square Type) | A02AB015-00005 Pile Work Pile Head Treatment Reinforced Concrete Pile (Square Type) 300 ≤ SIZE <350 | A02AB015 | 00005 | A02AB015-00005 | AR | A02 | Pile Work | AB | Pile Head Treatment | 015 | Reinforced Concrete Pile (Square Type) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 98 | 300 ≤ SIZE <350 | 0 | Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB015 | A02AB015-00005
|  |  |  | A02AB015 Pile Work Pile Head Treatment Reinforced Concrete Pile (Square Type) | A02AB015-00006 Pile Work Pile Head Treatment Reinforced Concrete Pile (Square Type) 350 ≤ SIZE <400 | A02AB015 | 00006 | A02AB015-00006 | AR | A02 | Pile Work | AB | Pile Head Treatment | 015 | Reinforced Concrete Pile (Square Type) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 99 | 350 ≤ SIZE <400 | 0 | Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB015 | A02AB015-00006
|  |  |  | A02AB015 Pile Work Pile Head Treatment Reinforced Concrete Pile (Square Type) | A02AB015-00007 Pile Work Pile Head Treatment Reinforced Concrete Pile (Square Type) 400 ≤ SIZE <450 | A02AB015 | 00007 | A02AB015-00007 | AR | A02 | Pile Work | AB | Pile Head Treatment | 015 | Reinforced Concrete Pile (Square Type) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | AA | 400 ≤ SIZE <450 | 0 | Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB015 | A02AB015-00007
|  |  |  | A02AB016 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-A) | A02AB016-00002 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-A) DIA<400 | A02AB016 | 00002 | A02AB016-00002 | AR | A02 | Pile Work | AB | Pile Head Treatment | 016 | Pretensioned Concrete Pile (Type-A) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB016 | A02AB016-00002
|  |  |  | A02AB016 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-A) | A02AB016-00003 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-A) 400 ≤ DIA <500 | A02AB016 | 00003 | A02AB016-00003 | AR | A02 | Pile Work | AB | Pile Head Treatment | 016 | Pretensioned Concrete Pile (Type-A) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB016 | A02AB016-00003
|  |  |  | A02AB016 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-A) | A02AB016-00004 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-A) 500 ≤ DIA <600 | A02AB016 | 00004 | A02AB016-00004 | AR | A02 | Pile Work | AB | Pile Head Treatment | 016 | Pretensioned Concrete Pile (Type-A) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB016 | A02AB016-00004
|  |  |  | A02AB016 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-A) | A02AB016-00005 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-A) 600 ≤ DIA <700 | A02AB016 | 00005 | A02AB016-00005 | AR | A02 | Pile Work | AB | Pile Head Treatment | 016 | Pretensioned Concrete Pile (Type-A) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB016 | A02AB016-00005
|  |  |  | A02AB016 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-A) | A02AB016-00006 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-A) 700 ≤ DIA <800 | A02AB016 | 00006 | A02AB016-00006 | AR | A02 | Pile Work | AB | Pile Head Treatment | 016 | Pretensioned Concrete Pile (Type-A) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB016 | A02AB016-00006
|  |  |  | A02AB016 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-A) | A02AB016-00007 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-A) 800 ≤ DIA <900 | A02AB016 | 00007 | A02AB016-00007 | AR | A02 | Pile Work | AB | Pile Head Treatment | 016 | Pretensioned Concrete Pile (Type-A) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB016 | A02AB016-00007
|  |  |  | A02AB016 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-A) | A02AB016-00008 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-A) 900 ≤ DIA <1000 | A02AB016 | 00008 | A02AB016-00008 | AR | A02 | Pile Work | AB | Pile Head Treatment | 016 | Pretensioned Concrete Pile (Type-A) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB016 | A02AB016-00008
|  |  |  | A02AB016 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-A) | A02AB016-00009 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-A) 1000 ≤ DIA <1200 | A02AB016 | 00009 | A02AB016-00009 | AR | A02 | Pile Work | AB | Pile Head Treatment | 016 | Pretensioned Concrete Pile (Type-A) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB016 | A02AB016-00009
|  |  |  | A02AB017 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-B) | A02AB017-00002 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-B) DIA<400 | A02AB017 | 00002 | A02AB017-00002 | AR | A02 | Pile Work | AB | Pile Head Treatment | 017 | Pretensioned Concrete Pile (Type-B) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB017 | A02AB017-00002
|  |  |  | A02AB017 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-B) | A02AB017-00003 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-B) 400 ≤ DIA <500 | A02AB017 | 00003 | A02AB017-00003 | AR | A02 | Pile Work | AB | Pile Head Treatment | 017 | Pretensioned Concrete Pile (Type-B) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB017 | A02AB017-00003
|  |  |  | A02AB017 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-B) | A02AB017-00004 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-B) 500 ≤ DIA <600 | A02AB017 | 00004 | A02AB017-00004 | AR | A02 | Pile Work | AB | Pile Head Treatment | 017 | Pretensioned Concrete Pile (Type-B) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB017 | A02AB017-00004
|  |  |  | A02AB017 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-B) | A02AB017-00005 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-B) 600 ≤ DIA <700 | A02AB017 | 00005 | A02AB017-00005 | AR | A02 | Pile Work | AB | Pile Head Treatment | 017 | Pretensioned Concrete Pile (Type-B) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB017 | A02AB017-00005
|  |  |  | A02AB017 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-B) | A02AB017-00006 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-B) 700 ≤ DIA <800 | A02AB017 | 00006 | A02AB017-00006 | AR | A02 | Pile Work | AB | Pile Head Treatment | 017 | Pretensioned Concrete Pile (Type-B) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB017 | A02AB017-00006
|  |  |  | A02AB017 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-B) | A02AB017-00007 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-B) 800 ≤ DIA <900 | A02AB017 | 00007 | A02AB017-00007 | AR | A02 | Pile Work | AB | Pile Head Treatment | 017 | Pretensioned Concrete Pile (Type-B) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB017 | A02AB017-00007
|  |  |  | A02AB017 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-B) | A02AB017-00008 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-B) 900 ≤ DIA <1000 | A02AB017 | 00008 | A02AB017-00008 | AR | A02 | Pile Work | AB | Pile Head Treatment | 017 | Pretensioned Concrete Pile (Type-B) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB017 | A02AB017-00008
|  |  |  | A02AB017 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-B) | A02AB017-00009 Pile Work Pile Head Treatment Pretensioned Concrete Pile (Type-B) 1000 ≤ DIA <1200 | A02AB017 | 00009 | A02AB017-00009 | AR | A02 | Pile Work | AB | Pile Head Treatment | 017 | Pretensioned Concrete Pile (Type-B) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB017 | A02AB017-00009
|  |  |  | A02AB018 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) | A02AB018-00002 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) DIA<400 | A02AB018 | 00002 | A02AB018-00002 | AR | A02 | Pile Work | AB | Pile Head Treatment | 018 | Pretensioned High-strength Concrete Pile (Type-A) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB018 | A02AB018-00002
|  |  |  | A02AB018 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) | A02AB018-00003 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) 400 ≤ DIA <500 | A02AB018 | 00003 | A02AB018-00003 | AR | A02 | Pile Work | AB | Pile Head Treatment | 018 | Pretensioned High-strength Concrete Pile (Type-A) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB018 | A02AB018-00003
|  |  |  | A02AB018 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) | A02AB018-00004 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) 500 ≤ DIA <600 | A02AB018 | 00004 | A02AB018-00004 | AR | A02 | Pile Work | AB | Pile Head Treatment | 018 | Pretensioned High-strength Concrete Pile (Type-A) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB018 | A02AB018-00004
|  |  |  | A02AB018 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) | A02AB018-00005 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) 600 ≤ DIA <700 | A02AB018 | 00005 | A02AB018-00005 | AR | A02 | Pile Work | AB | Pile Head Treatment | 018 | Pretensioned High-strength Concrete Pile (Type-A) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB018 | A02AB018-00005
|  |  |  | A02AB018 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) | A02AB018-00006 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) 700 ≤ DIA <800 | A02AB018 | 00006 | A02AB018-00006 | AR | A02 | Pile Work | AB | Pile Head Treatment | 018 | Pretensioned High-strength Concrete Pile (Type-A) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB018 | A02AB018-00006
|  |  |  | A02AB018 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) | A02AB018-00007 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) 800 ≤ DIA <900 | A02AB018 | 00007 | A02AB018-00007 | AR | A02 | Pile Work | AB | Pile Head Treatment | 018 | Pretensioned High-strength Concrete Pile (Type-A) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB018 | A02AB018-00007
|  |  |  | A02AB018 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) | A02AB018-00008 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) 900 ≤ DIA <1000 | A02AB018 | 00008 | A02AB018-00008 | AR | A02 | Pile Work | AB | Pile Head Treatment | 018 | Pretensioned High-strength Concrete Pile (Type-A) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB018 | A02AB018-00008
|  |  |  | A02AB018 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) | A02AB018-00009 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-A) 1000 ≤ DIA <1200 | A02AB018 | 00009 | A02AB018-00009 | AR | A02 | Pile Work | AB | Pile Head Treatment | 018 | Pretensioned High-strength Concrete Pile (Type-A) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB018 | A02AB018-00009
|  |  |  | A02AB019 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-B) | A02AB019-00002 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-B) DIA<400 | A02AB019 | 00002 | A02AB019-00002 | AR | A02 | Pile Work | AB | Pile Head Treatment | 019 | Pretensioned High-strength Concrete Pile (Type-B) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB019 | A02AB019-00002
|  |  |  | A02AB019 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-B) | A02AB019-00003 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-B) 400 ≤ DIA <500 | A02AB019 | 00003 | A02AB019-00003 | AR | A02 | Pile Work | AB | Pile Head Treatment | 019 | Pretensioned High-strength Concrete Pile (Type-B) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB019 | A02AB019-00003
|  |  |  | A02AB019 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-B) | A02AB019-00004 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-B) 500 ≤ DIA <600 | A02AB019 | 00004 | A02AB019-00004 | AR | A02 | Pile Work | AB | Pile Head Treatment | 019 | Pretensioned High-strength Concrete Pile (Type-B) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB019 | A02AB019-00004
|  |  |  | A02AB019 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-B) | A02AB019-00005 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-B) 600 ≤ DIA <700 | A02AB019 | 00005 | A02AB019-00005 | AR | A02 | Pile Work | AB | Pile Head Treatment | 019 | Pretensioned High-strength Concrete Pile (Type-B) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB019 | A02AB019-00005
|  |  |  | A02AB019 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-B) | A02AB019-00006 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-B) 700 ≤ DIA <800 | A02AB019 | 00006 | A02AB019-00006 | AR | A02 | Pile Work | AB | Pile Head Treatment | 019 | Pretensioned High-strength Concrete Pile (Type-B) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB019 | A02AB019-00006
|  |  |  | A02AB019 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-B) | A02AB019-00007 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-B) 800 ≤ DIA <900 | A02AB019 | 00007 | A02AB019-00007 | AR | A02 | Pile Work | AB | Pile Head Treatment | 019 | Pretensioned High-strength Concrete Pile (Type-B) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB019 | A02AB019-00007
|  |  |  | A02AB019 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-B) | A02AB019-00008 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-B) 900 ≤ DIA <1000 | A02AB019 | 00008 | A02AB019-00008 | AR | A02 | Pile Work | AB | Pile Head Treatment | 019 | Pretensioned High-strength Concrete Pile (Type-B) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB019 | A02AB019-00008
|  |  |  | A02AB019 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-B) | A02AB019-00009 Pile Work Pile Head Treatment Pretensioned High-strength Concrete Pile (Type-B) 1000 ≤ DIA <1200 | A02AB019 | 00009 | A02AB019-00009 | AR | A02 | Pile Work | AB | Pile Head Treatment | 019 | Pretensioned High-strength Concrete Pile (Type-B) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB019 | A02AB019-00009
|  |  |  | A02AB020 Pile Work Pile Head Treatment Steel Pipe Pile Work | A02AB020-00002 Pile Work Pile Head Treatment Steel Pipe Pile Work DIA<400 | A02AB020 | 00002 | A02AB020-00002 | AR | A02 | Pile Work | AB | Pile Head Treatment | 020 | Steel Pipe Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AB | DIA<400 | 0 | D=( )mm / THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB020 | A02AB020-00002
|  |  |  | A02AB020 Pile Work Pile Head Treatment Steel Pipe Pile Work | A02AB020-00003 Pile Work Pile Head Treatment Steel Pipe Pile Work 400 ≤ DIA <500 | A02AB020 | 00003 | A02AB020-00003 | AR | A02 | Pile Work | AB | Pile Head Treatment | 020 | Steel Pipe Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AC | 400 ≤ DIA <500 | 0 | D=( )mm / THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB020 | A02AB020-00003
|  |  |  | A02AB020 Pile Work Pile Head Treatment Steel Pipe Pile Work | A02AB020-00004 Pile Work Pile Head Treatment Steel Pipe Pile Work 500 ≤ DIA <600 | A02AB020 | 00004 | A02AB020-00004 | AR | A02 | Pile Work | AB | Pile Head Treatment | 020 | Steel Pipe Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AD | 500 ≤ DIA <600 | 0 | D=( )mm / THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB020 | A02AB020-00004
|  |  |  | A02AB020 Pile Work Pile Head Treatment Steel Pipe Pile Work | A02AB020-00005 Pile Work Pile Head Treatment Steel Pipe Pile Work 600 ≤ DIA <700 | A02AB020 | 00005 | A02AB020-00005 | AR | A02 | Pile Work | AB | Pile Head Treatment | 020 | Steel Pipe Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AE | 600 ≤ DIA <700 | 0 | D=( )mm / THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB020 | A02AB020-00005
|  |  |  | A02AB020 Pile Work Pile Head Treatment Steel Pipe Pile Work | A02AB020-00006 Pile Work Pile Head Treatment Steel Pipe Pile Work 700 ≤ DIA <800 | A02AB020 | 00006 | A02AB020-00006 | AR | A02 | Pile Work | AB | Pile Head Treatment | 020 | Steel Pipe Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AF | 700 ≤ DIA <800 | 0 | D=( )mm / THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB020 | A02AB020-00006
|  |  |  | A02AB020 Pile Work Pile Head Treatment Steel Pipe Pile Work | A02AB020-00007 Pile Work Pile Head Treatment Steel Pipe Pile Work 800 ≤ DIA <900 | A02AB020 | 00007 | A02AB020-00007 | AR | A02 | Pile Work | AB | Pile Head Treatment | 020 | Steel Pipe Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AG | 800 ≤ DIA <900 | 0 | D=( )mm / THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB020 | A02AB020-00007
|  |  |  | A02AB020 Pile Work Pile Head Treatment Steel Pipe Pile Work | A02AB020-00008 Pile Work Pile Head Treatment Steel Pipe Pile Work 900 ≤ DIA <1000 | A02AB020 | 00008 | A02AB020-00008 | AR | A02 | Pile Work | AB | Pile Head Treatment | 020 | Steel Pipe Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AH | 900 ≤ DIA <1000 | 0 | D=( )mm / THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB020 | A02AB020-00008
|  |  |  | A02AB020 Pile Work Pile Head Treatment Steel Pipe Pile Work | A02AB020-00009 Pile Work Pile Head Treatment Steel Pipe Pile Work 1000 ≤ DIA <1200 | A02AB020 | 00009 | A02AB020-00009 | AR | A02 | Pile Work | AB | Pile Head Treatment | 020 | Steel Pipe Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | D=( )mm / THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB020 | A02AB020-00009
|  |  |  | A02AB021 Pile Work Pile Head Treatment H-Pile Work | A02AB021-00002 Pile Work Pile Head Treatment H-Pile Work SIZE <200 | A02AB021 | 00002 | A02AB021-00002 | AR | A02 | Pile Work | AB | Pile Head Treatment | 021 | H-Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 95 | SIZE <200 | 0 | Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB021 | A02AB021-00002
|  |  |  | A02AB021 Pile Work Pile Head Treatment H-Pile Work | A02AB021-00003 Pile Work Pile Head Treatment H-Pile Work 200 ≤ SIZE <250 | A02AB021 | 00003 | A02AB021-00003 | AR | A02 | Pile Work | AB | Pile Head Treatment | 021 | H-Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 96 | 200 ≤ SIZE <250 | 0 | Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB021 | A02AB021-00003
|  |  |  | A02AB021 Pile Work Pile Head Treatment H-Pile Work | A02AB021-00004 Pile Work Pile Head Treatment H-Pile Work 250 ≤ SIZE <300 | A02AB021 | 00004 | A02AB021-00004 | AR | A02 | Pile Work | AB | Pile Head Treatment | 021 | H-Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 97 | 250 ≤ SIZE <300 | 0 | Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB021 | A02AB021-00004
|  |  |  | A02AB021 Pile Work Pile Head Treatment H-Pile Work | A02AB021-00005 Pile Work Pile Head Treatment H-Pile Work 300 ≤ SIZE <350 | A02AB021 | 00005 | A02AB021-00005 | AR | A02 | Pile Work | AB | Pile Head Treatment | 021 | H-Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 98 | 300 ≤ SIZE <350 | 0 | Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB021 | A02AB021-00005
|  |  |  | A02AB022 Pile Work Pile Head Treatment Micro Pile Work | A02AB022-00002 Pile Work Pile Head Treatment Micro Pile Work DIA<150 | A02AB022 | 00002 | A02AB022-00002 | AR | A02 | Pile Work | AB | Pile Head Treatment | 022 | Micro Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AK | DIA<150 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB022 | A02AB022-00002
|  |  |  | A02AB022 Pile Work Pile Head Treatment Micro Pile Work | A02AB022-00003 Pile Work Pile Head Treatment Micro Pile Work 150 ≤ DIA <200 | A02AB022 | 00003 | A02AB022-00003 | AR | A02 | Pile Work | AB | Pile Head Treatment | 022 | Micro Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AL | 150 ≤ DIA <200 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB022 | A02AB022-00003
|  |  |  | A02AB022 Pile Work Pile Head Treatment Micro Pile Work | A02AB022-00004 Pile Work Pile Head Treatment Micro Pile Work 200 ≤ DIA <250 | A02AB022 | 00004 | A02AB022-00004 | AR | A02 | Pile Work | AB | Pile Head Treatment | 022 | Micro Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AM | 200 ≤ DIA <250 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB022 | A02AB022-00004
|  |  |  | A02AB022 Pile Work Pile Head Treatment Micro Pile Work | A02AB022-00005 Pile Work Pile Head Treatment Micro Pile Work 250 ≤ DIA <300 | A02AB022 | 00005 | A02AB022-00005 | AR | A02 | Pile Work | AB | Pile Head Treatment | 022 | Micro Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 91 | 250 ≤ DIA <300 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB022 | A02AB022-00005
|  |  |  | A02AB022 Pile Work Pile Head Treatment Micro Pile Work | A02AB022-00006 Pile Work Pile Head Treatment Micro Pile Work 300 ≤ DIA | A02AB022 | 00006 | A02AB022-00006 | AR | A02 | Pile Work | AB | Pile Head Treatment | 022 | Micro Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AN | 300 ≤ DIA | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB022 | A02AB022-00006
|  |  |  | A02AB023 Pile Work Pile Head Treatment Cast-In-Place Pile Work | A02AB023-00002 Pile Work Pile Head Treatment Cast-In-Place Pile Work DIA<400 | A02AB023 | 00002 | A02AB023-00002 | AR | A02 | Pile Work | AB | Pile Head Treatment | 023 | Cast-In-Place Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AB | DIA<400 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB023 | A02AB023-00002
|  |  |  | A02AB023 Pile Work Pile Head Treatment Cast-In-Place Pile Work | A02AB023-00003 Pile Work Pile Head Treatment Cast-In-Place Pile Work 400 ≤ DIA <500 | A02AB023 | 00003 | A02AB023-00003 | AR | A02 | Pile Work | AB | Pile Head Treatment | 023 | Cast-In-Place Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AC | 400 ≤ DIA <500 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB023 | A02AB023-00003
|  |  |  | A02AB023 Pile Work Pile Head Treatment Cast-In-Place Pile Work | A02AB023-00004 Pile Work Pile Head Treatment Cast-In-Place Pile Work 500 ≤ DIA <600 | A02AB023 | 00004 | A02AB023-00004 | AR | A02 | Pile Work | AB | Pile Head Treatment | 023 | Cast-In-Place Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AD | 500 ≤ DIA <600 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB023 | A02AB023-00004
|  |  |  | A02AB023 Pile Work Pile Head Treatment Cast-In-Place Pile Work | A02AB023-00005 Pile Work Pile Head Treatment Cast-In-Place Pile Work 600 ≤ DIA <700 | A02AB023 | 00005 | A02AB023-00005 | AR | A02 | Pile Work | AB | Pile Head Treatment | 023 | Cast-In-Place Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AE | 600 ≤ DIA <700 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB023 | A02AB023-00005
|  |  |  | A02AB023 Pile Work Pile Head Treatment Cast-In-Place Pile Work | A02AB023-00006 Pile Work Pile Head Treatment Cast-In-Place Pile Work 700 ≤ DIA <800 | A02AB023 | 00006 | A02AB023-00006 | AR | A02 | Pile Work | AB | Pile Head Treatment | 023 | Cast-In-Place Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AF | 700 ≤ DIA <800 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB023 | A02AB023-00006
|  |  |  | A02AB023 Pile Work Pile Head Treatment Cast-In-Place Pile Work | A02AB023-00007 Pile Work Pile Head Treatment Cast-In-Place Pile Work 800 ≤ DIA <900 | A02AB023 | 00007 | A02AB023-00007 | AR | A02 | Pile Work | AB | Pile Head Treatment | 023 | Cast-In-Place Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AG | 800 ≤ DIA <900 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB023 | A02AB023-00007
|  |  |  | A02AB023 Pile Work Pile Head Treatment Cast-In-Place Pile Work | A02AB023-00008 Pile Work Pile Head Treatment Cast-In-Place Pile Work 900 ≤ DIA <1000 | A02AB023 | 00008 | A02AB023-00008 | AR | A02 | Pile Work | AB | Pile Head Treatment | 023 | Cast-In-Place Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AH | 900 ≤ DIA <1000 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB023 | A02AB023-00008
|  |  |  | A02AB023 Pile Work Pile Head Treatment Cast-In-Place Pile Work | A02AB023-00009 Pile Work Pile Head Treatment Cast-In-Place Pile Work 1000 ≤ DIA <1200 | A02AB023 | 00009 | A02AB023-00009 | AR | A02 | Pile Work | AB | Pile Head Treatment | 023 | Cast-In-Place Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AJ | 1000 ≤ DIA <1200 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB023 | A02AB023-00009
|  |  |  | A02AB023 Pile Work Pile Head Treatment Cast-In-Place Pile Work | A02AB023-00010 Pile Work Pile Head Treatment Cast-In-Place Pile Work 1200 ≤ DIA <1500 | A02AB023 | 00010 | A02AB023-00010 | AR | A02 | Pile Work | AB | Pile Head Treatment | 023 | Cast-In-Place Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AP | 1200 ≤ DIA <1500 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB023 | A02AB023-00010
|  |  |  | A02AB023 Pile Work Pile Head Treatment Cast-In-Place Pile Work | A02AB023-00011 Pile Work Pile Head Treatment Cast-In-Place Pile Work 1500 ≤ DIA <1800 | A02AB023 | 00011 | A02AB023-00011 | AR | A02 | Pile Work | AB | Pile Head Treatment | 023 | Cast-In-Place Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AQ | 1500 ≤ DIA <1800 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB023 | A02AB023-00011
|  |  |  | A02AB023 Pile Work Pile Head Treatment Cast-In-Place Pile Work | A02AB023-00012 Pile Work Pile Head Treatment Cast-In-Place Pile Work 1800 ≤ DIA <2000 | A02AB023 | 00012 | A02AB023-00012 | AR | A02 | Pile Work | AB | Pile Head Treatment | 023 | Cast-In-Place Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AR | 1800 ≤ DIA <2000 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB023 | A02AB023-00012
|  |  |  | A02AB023 Pile Work Pile Head Treatment Cast-In-Place Pile Work | A02AB023-00013 Pile Work Pile Head Treatment Cast-In-Place Pile Work 2000 ≤ DIA | A02AB023 | 00013 | A02AB023-00013 | AR | A02 | Pile Work | AB | Pile Head Treatment | 023 | Cast-In-Place Pile Work |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AS | 2000 ≤ DIA | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AB023 | A02AB023-00013
|  |  |  | A02AC024 Pile Work Pile Test Static Axial Compressive Load Test | A02AC024-00001 Pile Work Pile Test Static Axial Compressive Load Test | A02AC024 | 00001 | A02AC024-00001 | AR | A02 | Pile Work | AC | Pile Test | 024 | Static Axial Compressive Load Test |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AC024 | A02AC024-00001
|  |  |  | A02AC025 Pile Work Pile Test Static Axial Tensile Load Test | A02AC025-00001 Pile Work Pile Test Static Axial Tensile Load Test | A02AC025 | 00001 | A02AC025-00001 | AR | A02 | Pile Work | AC | Pile Test | 025 | Static Axial Tensile Load Test |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AC025 | A02AC025-00001
|  |  |  | A02AC026 Pile Work Pile Test Lateral Load Test | A02AC026-00001 Pile Work Pile Test Lateral Load Test | A02AC026 | 00001 | A02AC026-00001 | AR | A02 | Pile Work | AC | Pile Test | 026 | Lateral Load Test |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AC026 | A02AC026-00001
|  |  |  | A02AC027 Pile Work Pile Test Dynamic Load Test | A02AC027-00001 Pile Work Pile Test Dynamic Load Test | A02AC027 | 00001 | A02AC027-00001 | AR | A02 | Pile Work | AC | Pile Test | 027 | Dynamic Load Test |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AC027 | A02AC027-00001
|  |  |  | A02AC028 Pile Work Pile Test Integrity Test | A02AC028-00001 Pile Work Pile Test Integrity Test | A02AC028 | 00001 | A02AC028-00001 | AR | A02 | Pile Work | AC | Pile Test | 028 | Integrity Test |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A02AC028 | A02AC028-00001
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00001 Concrete Work Substructure Work Anchor Bolt (Installation only) M12 | A03AD029 | 00001 | A03AD029-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 37 | M12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00001
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00002 Concrete Work Substructure Work Anchor Bolt (Installation only) M16 | A03AD029 | 00002 | A03AD029-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 38 | M16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00002
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00003 Concrete Work Substructure Work Anchor Bolt (Installation only) M20 | A03AD029 | 00003 | A03AD029-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 39 | M20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00003
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00004 Concrete Work Substructure Work Anchor Bolt (Installation only) M22 | A03AD029 | 00004 | A03AD029-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 40 | M22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00004
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00005 Concrete Work Substructure Work Anchor Bolt (Installation only) M24 | A03AD029 | 00005 | A03AD029-00005 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 41 | M24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00005
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00006 Concrete Work Substructure Work Anchor Bolt (Installation only) M30 | A03AD029 | 00006 | A03AD029-00006 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 42 | M30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00006
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00007 Concrete Work Substructure Work Anchor Bolt (Installation only) M33 | A03AD029 | 00007 | A03AD029-00007 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 43 | M33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00007
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00008 Concrete Work Substructure Work Anchor Bolt (Installation only) M36 | A03AD029 | 00008 | A03AD029-00008 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 44 | M36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00008
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00009 Concrete Work Substructure Work Anchor Bolt (Installation only) M42 | A03AD029 | 00009 | A03AD029-00009 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 45 | M42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00009
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00010 Concrete Work Substructure Work Anchor Bolt (Installation only) M48 | A03AD029 | 00010 | A03AD029-00010 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 46 | M48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00010
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00011 Concrete Work Substructure Work Anchor Bolt (Installation only) M52 | A03AD029 | 00011 | A03AD029-00011 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 47 | M52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00011
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00012 Concrete Work Substructure Work Anchor Bolt (Installation only) M56 | A03AD029 | 00012 | A03AD029-00012 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 48 | M56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00012
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00013 Concrete Work Substructure Work Anchor Bolt (Installation only) M64 | A03AD029 | 00013 | A03AD029-00013 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49 | M64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00013
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00014 Concrete Work Substructure Work Anchor Bolt (Installation only) M72 | A03AD029 | 00014 | A03AD029-00014 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 50 | M72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00014
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00015 Concrete Work Substructure Work Anchor Bolt (Installation only) M76 | A03AD029 | 00015 | A03AD029-00015 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 51 | M76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00015
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00016 Concrete Work Substructure Work Anchor Bolt (Installation only) Over M76 | A03AD029 | 00016 | A03AD029-00016 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 52 | Over M76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00016
|  |  |  | A03AD029 Concrete Work Substructure Work Anchor Bolt (Installation only) | A03AD029-00017 Concrete Work Substructure Work Anchor Bolt (Installation only) M27 | A03AD029 | 00017 | A03AD029-00017 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | AU | M27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD029 | A03AD029-00017
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00001 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M12 | A03AD329 | 00001 | A03AD329-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 37 | M12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00001
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00002 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M16 | A03AD329 | 00002 | A03AD329-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 38 | M16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00002
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00003 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M20 | A03AD329 | 00003 | A03AD329-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 39 | M20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00003
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00004 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M22 | A03AD329 | 00004 | A03AD329-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 40 | M22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00004
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00005 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M24 | A03AD329 | 00005 | A03AD329-00005 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 41 | M24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00005
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00006 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M27 | A03AD329 | 00006 | A03AD329-00006 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | AU | M27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00006
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00007 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M30 | A03AD329 | 00007 | A03AD329-00007 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 42 | M30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00007
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00008 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M33 | A03AD329 | 00008 | A03AD329-00008 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 43 | M33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00008
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00009 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M36 | A03AD329 | 00009 | A03AD329-00009 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 44 | M36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00009
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00010 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M42 | A03AD329 | 00010 | A03AD329-00010 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 45 | M42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00010
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00011 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M48 | A03AD329 | 00011 | A03AD329-00011 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 46 | M48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00011
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00012 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M52 | A03AD329 | 00012 | A03AD329-00012 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 47 | M52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00012
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00013 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M56 | A03AD329 | 00013 | A03AD329-00013 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 48 | M56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00013
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00014 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M64 | A03AD329 | 00014 | A03AD329-00014 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49 | M64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00014
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00015 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M72 | A03AD329 | 00015 | A03AD329-00015 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 50 | M72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00015
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00016 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) M76 | A03AD329 | 00016 | A03AD329-00016 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 51 | M76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00016
|  |  |  | A03AD329 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) | A03AD329-00017 Concrete Work Substructure Work Anchor Bolt (Purchase & Installation) Over M76 | A03AD329 | 00017 | A03AD329-00017 | AR | A03 | Concrete Work | AD | Substructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 52 | Over M76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD329 | A03AD329-00017
|  |  |  | A03AD030 Concrete Work Substructure Work Chemical Anchor Bolt | A03AD030-00001 Concrete Work Substructure Work Chemical Anchor Bolt Including injected Chemical material M10 | A03AD030 | 00001 | A03AD030-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 36 | M10 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD030 | A03AD030-00001
|  |  |  | A03AD030 Concrete Work Substructure Work Chemical Anchor Bolt | A03AD030-00002 Concrete Work Substructure Work Chemical Anchor Bolt Including injected Chemical material M12 | A03AD030 | 00002 | A03AD030-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 37 | M12 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD030 | A03AD030-00002
|  |  |  | A03AD030 Concrete Work Substructure Work Chemical Anchor Bolt | A03AD030-00003 Concrete Work Substructure Work Chemical Anchor Bolt Including injected Chemical material M16 | A03AD030 | 00003 | A03AD030-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 38 | M16 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD030 | A03AD030-00003
|  |  |  | A03AD030 Concrete Work Substructure Work Chemical Anchor Bolt | A03AD030-00004 Concrete Work Substructure Work Chemical Anchor Bolt Including injected Chemical material M20 | A03AD030 | 00004 | A03AD030-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 39 | M20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD030 | A03AD030-00004
|  |  |  | A03AD030 Concrete Work Substructure Work Chemical Anchor Bolt | A03AD030-00005 Concrete Work Substructure Work Chemical Anchor Bolt Including injected Chemical material M22 | A03AD030 | 00005 | A03AD030-00005 | AR | A03 | Concrete Work | AD | Substructure Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 40 | M22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD030 | A03AD030-00005
|  |  |  | A03AD030 Concrete Work Substructure Work Chemical Anchor Bolt | A03AD030-00006 Concrete Work Substructure Work Chemical Anchor Bolt Including injected Chemical material M24 | A03AD030 | 00006 | A03AD030-00006 | AR | A03 | Concrete Work | AD | Substructure Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 41 | M24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD030 | A03AD030-00006
|  |  |  | A03AD031 Concrete Work Substructure Work Expansion Anchor Bolt | A03AD031-00001 Concrete Work Substructure Work Expansion Anchor Bolt M10 | A03AD031 | 00001 | A03AD031-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | M10 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD031 | A03AD031-00001
|  |  |  | A03AD031 Concrete Work Substructure Work Expansion Anchor Bolt | A03AD031-00002 Concrete Work Substructure Work Expansion Anchor Bolt M12 | A03AD031 | 00002 | A03AD031-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 37 | M12 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD031 | A03AD031-00002
|  |  |  | A03AD031 Concrete Work Substructure Work Expansion Anchor Bolt | A03AD031-00003 Concrete Work Substructure Work Expansion Anchor Bolt M16 | A03AD031 | 00003 | A03AD031-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 38 | M16 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD031 | A03AD031-00003
|  |  |  | A03AD031 Concrete Work Substructure Work Expansion Anchor Bolt | A03AD031-00004 Concrete Work Substructure Work Expansion Anchor Bolt M20 | A03AD031 | 00004 | A03AD031-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 39 | M20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD031 | A03AD031-00004
|  |  |  | A03AD031 Concrete Work Substructure Work Expansion Anchor Bolt | A03AD031-00005 Concrete Work Substructure Work Expansion Anchor Bolt M22 | A03AD031 | 00005 | A03AD031-00005 | AR | A03 | Concrete Work | AD | Substructure Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 40 | M22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD031 | A03AD031-00005
|  |  |  | A03AD031 Concrete Work Substructure Work Expansion Anchor Bolt | A03AD031-00006 Concrete Work Substructure Work Expansion Anchor Bolt M24 | A03AD031 | 00006 | A03AD031-00006 | AR | A03 | Concrete Work | AD | Substructure Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 41 | M24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD031 | A03AD031-00006
|  |  |  | A03AD032 Concrete Work Substructure Work Structural Concrete | A03AD032-00016 Concrete Work Substructure Work Structural Concrete Cement Type-1 35MPa ≤ F'c (Cylinder Strength) | A03AD032 | 00016 | A03AD032-00016 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 13 | 35MPa ≤ F'c (Cylinder Strength) |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD032 | A03AD032-00016
|  |  |  | A03AD032 Concrete Work Substructure Work Structural Concrete | A03AD032-00017 Concrete Work Substructure Work Structural Concrete Cement Type-2 35MPa ≤ F'c (Cylinder Strength) | A03AD032 | 00017 | A03AD032-00017 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 13 | 35MPa ≤ F'c (Cylinder Strength) |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD032 | A03AD032-00017
|  |  |  | A03AD032 Concrete Work Substructure Work Structural Concrete | A03AD032-00018 Concrete Work Substructure Work Structural Concrete Cement Type-5 35MPa ≤ F'c (Cylinder Strength) | A03AD032 | 00018 | A03AD032-00018 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 13 | 35MPa ≤ F'c (Cylinder Strength) |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD032 | A03AD032-00018
|  |  |  | A03AD032 Concrete Work Substructure Work Structural Concrete | A03AD032-00019 Concrete Work Substructure Work Structural Concrete Cement Type-1 30MPa ≤ F'c (Cylinder Strength) < 35MPa | A03AD032 | 00019 | A03AD032-00019 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 14 | 30MPa ≤ F'c (Cylinder Strength) < 35MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD032 | A03AD032-00019
|  |  |  | A03AD032 Concrete Work Substructure Work Structural Concrete | A03AD032-00020 Concrete Work Substructure Work Structural Concrete Cement Type-2 30MPa ≤ F'c (Cylinder Strength) < 35MPa | A03AD032 | 00020 | A03AD032-00020 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 14 | 30MPa ≤ F'c (Cylinder Strength) < 35MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD032 | A03AD032-00020
|  |  |  | A03AD032 Concrete Work Substructure Work Structural Concrete | A03AD032-00021 Concrete Work Substructure Work Structural Concrete Cement Type-5 30MPa ≤ F'c (Cylinder Strength) < 35MPa | A03AD032 | 00021 | A03AD032-00021 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 14 | 30MPa ≤ F'c (Cylinder Strength) < 35MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD032 | A03AD032-00021
|  |  |  | A03AD032 Concrete Work Substructure Work Structural Concrete | A03AD032-00022 Concrete Work Substructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032 | 00022 | A03AD032-00022 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 15 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD032 | A03AD032-00022
|  |  |  | A03AD032 Concrete Work Substructure Work Structural Concrete | A03AD032-00023 Concrete Work Substructure Work Structural Concrete Cement Type-2 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032 | 00023 | A03AD032-00023 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 15 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD032 | A03AD032-00023
|  |  |  | A03AD032 Concrete Work Substructure Work Structural Concrete | A03AD032-00024 Concrete Work Substructure Work Structural Concrete Cement Type-5 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD032 | 00024 | A03AD032-00024 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 15 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD032 | A03AD032-00024
|  |  |  | A03AD032 Concrete Work Substructure Work Structural Concrete | A03AD032-00025 Concrete Work Substructure Work Structural Concrete Cement Type-1 20MPa ≤ F'c (Cylinder Strength) < 25MPa | A03AD032 | 00025 | A03AD032-00025 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 16 | 20MPa ≤ F'c (Cylinder Strength) < 25MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD032 | A03AD032-00025
|  |  |  | A03AD032 Concrete Work Substructure Work Structural Concrete | A03AD032-00026 Concrete Work Substructure Work Structural Concrete Cement Type-2 20MPa ≤ F'c (Cylinder Strength) < 25MPa | A03AD032 | 00026 | A03AD032-00026 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 16 | 20MPa ≤ F'c (Cylinder Strength) < 25MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD032 | A03AD032-00026
|  |  |  | A03AD032 Concrete Work Substructure Work Structural Concrete | A03AD032-00027 Concrete Work Substructure Work Structural Concrete Cement Type-5 20MPa ≤ F'c (Cylinder Strength) < 25MPa | A03AD032 | 00027 | A03AD032-00027 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 16 | 20MPa ≤ F'c (Cylinder Strength) < 25MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD032 | A03AD032-00027
|  |  |  | A03AD032 Concrete Work Substructure Work Structural Concrete | A03AD032-00028 Concrete Work Substructure Work Structural Concrete Cement Type-1 F'c (Cylinder Strength) < 20MPa | A03AD032 | 00028 | A03AD032-00028 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 17 | F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD032 | A03AD032-00028
|  |  |  | A03AD032 Concrete Work Substructure Work Structural Concrete | A03AD032-00029 Concrete Work Substructure Work Structural Concrete Cement Type-2 F'c (Cylinder Strength) < 20MPa | A03AD032 | 00029 | A03AD032-00029 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 17 | F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD032 | A03AD032-00029
|  |  |  | A03AD032 Concrete Work Substructure Work Structural Concrete | A03AD032-00030 Concrete Work Substructure Work Structural Concrete Cement Type-5 F'c (Cylinder Strength) < 20MPa | A03AD032 | 00030 | A03AD032-00030 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 17 | F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD032 | A03AD032-00030
|  |  |  | A03AD033 Concrete Work Substructure Work Colored Concrete | A03AD033-00016 Concrete Work Substructure Work Colored Concrete Cement Type-1 35MPa ≤ F'c (Cylinder Strength) | A03AD033 | 00016 | A03AD033-00016 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  | 0 | 01 | Cement Type-1 | 13 | 35MPa ≤ F'c (Cylinder Strength) |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD033 | A03AD033-00016
|  |  |  | A03AD033 Concrete Work Substructure Work Colored Concrete | A03AD033-00017 Concrete Work Substructure Work Colored Concrete Cement Type-2 35MPa ≤ F'c (Cylinder Strength) | A03AD033 | 00017 | A03AD033-00017 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  | 0 | 02 | Cement Type-2 | 13 | 35MPa ≤ F'c (Cylinder Strength) |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD033 | A03AD033-00017
|  |  |  | A03AD033 Concrete Work Substructure Work Colored Concrete | A03AD033-00018 Concrete Work Substructure Work Colored Concrete Cement Type-5 35MPa ≤ F'c (Cylinder Strength) | A03AD033 | 00018 | A03AD033-00018 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  | 0 | 03 | Cement Type-5 | 13 | 35MPa ≤ F'c (Cylinder Strength) |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD033 | A03AD033-00018
|  |  |  | A03AD033 Concrete Work Substructure Work Colored Concrete | A03AD033-00019 Concrete Work Substructure Work Colored Concrete Cement Type-1 30MPa ≤ F'c (Cylinder Strength) < 35MPa | A03AD033 | 00019 | A03AD033-00019 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  | 0 | 01 | Cement Type-1 | 14 | 30MPa ≤ F'c (Cylinder Strength) < 35MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD033 | A03AD033-00019
|  |  |  | A03AD033 Concrete Work Substructure Work Colored Concrete | A03AD033-00020 Concrete Work Substructure Work Colored Concrete Cement Type-2 30MPa ≤ F'c (Cylinder Strength) < 35MPa | A03AD033 | 00020 | A03AD033-00020 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  | 0 | 02 | Cement Type-2 | 14 | 30MPa ≤ F'c (Cylinder Strength) < 35MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD033 | A03AD033-00020
|  |  |  | A03AD033 Concrete Work Substructure Work Colored Concrete | A03AD033-00021 Concrete Work Substructure Work Colored Concrete Cement Type-5 30MPa ≤ F'c (Cylinder Strength) < 35MPa | A03AD033 | 00021 | A03AD033-00021 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  | 0 | 03 | Cement Type-5 | 14 | 30MPa ≤ F'c (Cylinder Strength) < 35MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD033 | A03AD033-00021
|  |  |  | A03AD033 Concrete Work Substructure Work Colored Concrete | A03AD033-00022 Concrete Work Substructure Work Colored Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD033 | 00022 | A03AD033-00022 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  | 0 | 01 | Cement Type-1 | 15 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD033 | A03AD033-00022
|  |  |  | A03AD033 Concrete Work Substructure Work Colored Concrete | A03AD033-00023 Concrete Work Substructure Work Colored Concrete Cement Type-2 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD033 | 00023 | A03AD033-00023 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  | 0 | 02 | Cement Type-2 | 15 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD033 | A03AD033-00023
|  |  |  | A03AD033 Concrete Work Substructure Work Colored Concrete | A03AD033-00024 Concrete Work Substructure Work Colored Concrete Cement Type-5 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AD033 | 00024 | A03AD033-00024 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  | 0 | 03 | Cement Type-5 | 15 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD033 | A03AD033-00024
|  |  |  | A03AD033 Concrete Work Substructure Work Colored Concrete | A03AD033-00025 Concrete Work Substructure Work Colored Concrete Cement Type-1 20MPa ≤ F'c (Cylinder Strength) < 25MPa | A03AD033 | 00025 | A03AD033-00025 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  | 0 | 01 | Cement Type-1 | 16 | 20MPa ≤ F'c (Cylinder Strength) < 25MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD033 | A03AD033-00025
|  |  |  | A03AD033 Concrete Work Substructure Work Colored Concrete | A03AD033-00026 Concrete Work Substructure Work Colored Concrete Cement Type-2 20MPa ≤ F'c (Cylinder Strength) < 25MPa | A03AD033 | 00026 | A03AD033-00026 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  | 0 | 02 | Cement Type-2 | 16 | 20MPa ≤ F'c (Cylinder Strength) < 25MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD033 | A03AD033-00026
|  |  |  | A03AD033 Concrete Work Substructure Work Colored Concrete | A03AD033-00027 Concrete Work Substructure Work Colored Concrete Cement Type-5 20MPa ≤ F'c (Cylinder Strength) < 25MPa | A03AD033 | 00027 | A03AD033-00027 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  | 0 | 03 | Cement Type-5 | 16 | 20MPa ≤ F'c (Cylinder Strength) < 25MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD033 | A03AD033-00027
|  |  |  | A03AD033 Concrete Work Substructure Work Colored Concrete | A03AD033-00028 Concrete Work Substructure Work Colored Concrete Cement Type-1 F'c (Cylinder Strength) < 20MPa | A03AD033 | 00028 | A03AD033-00028 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  | 0 | 01 | Cement Type-1 | 17 | F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD033 | A03AD033-00028
|  |  |  | A03AD033 Concrete Work Substructure Work Colored Concrete | A03AD033-00029 Concrete Work Substructure Work Colored Concrete Cement Type-2 F'c (Cylinder Strength) < 20MPa | A03AD033 | 00029 | A03AD033-00029 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  | 0 | 02 | Cement Type-2 | 17 | F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD033 | A03AD033-00029
|  |  |  | A03AD033 Concrete Work Substructure Work Colored Concrete | A03AD033-00030 Concrete Work Substructure Work Colored Concrete Cement Type-5 F'c (Cylinder Strength) < 20MPa | A03AD033 | 00030 | A03AD033-00030 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  | 0 | 03 | Cement Type-5 | 17 | F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD033 | A03AD033-00030
|  |  |  | A03AD034 Concrete Work Substructure Work Lean Concrete (including Form work) | A03AD034-00010 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 15MPa ≤ F'c (Cylinder Strength) < 20MPa | A03AD034 | 00010 | A03AD034-00010 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  | 0 | 01 | Cement Type-1 | 18 | 15MPa ≤ F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD034 | A03AD034-00010
|  |  |  | A03AD034 Concrete Work Substructure Work Lean Concrete (including Form work) | A03AD034-00011 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-2 15MPa ≤ F'c (Cylinder Strength) < 20MPa | A03AD034 | 00011 | A03AD034-00011 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  | 0 | 02 | Cement Type-2 | 18 | 15MPa ≤ F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD034 | A03AD034-00011
|  |  |  | A03AD034 Concrete Work Substructure Work Lean Concrete (including Form work) | A03AD034-00012 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-5 15MPa ≤ F'c (Cylinder Strength) < 20MPa | A03AD034 | 00012 | A03AD034-00012 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  | 0 | 03 | Cement Type-5 | 18 | 15MPa ≤ F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD034 | A03AD034-00012
|  |  |  | A03AD034 Concrete Work Substructure Work Lean Concrete (including Form work) | A03AD034-00013 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034 | 00013 | A03AD034-00013 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  | 0 | 01 | Cement Type-1 | 19 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD034 | A03AD034-00013
|  |  |  | A03AD034 Concrete Work Substructure Work Lean Concrete (including Form work) | A03AD034-00014 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-2 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034 | 00014 | A03AD034-00014 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  | 0 | 02 | Cement Type-2 | 19 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD034 | A03AD034-00014
|  |  |  | A03AD034 Concrete Work Substructure Work Lean Concrete (including Form work) | A03AD034-00015 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-5 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AD034 | 00015 | A03AD034-00015 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  | 0 | 03 | Cement Type-5 | 19 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD034 | A03AD034-00015
|  |  |  | A03AD034 Concrete Work Substructure Work Lean Concrete (including Form work) | A03AD034-00016 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-1 F'c (Cylinder Strength) < 10MPa | A03AD034 | 00016 | A03AD034-00016 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  | 0 | 01 | Cement Type-1 | 20 | F'c (Cylinder Strength) < 10MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD034 | A03AD034-00016
|  |  |  | A03AD034 Concrete Work Substructure Work Lean Concrete (including Form work) | A03AD034-00017 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-2 F'c (Cylinder Strength) < 10MPa | A03AD034 | 00017 | A03AD034-00017 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  | 0 | 02 | Cement Type-2 | 20 | F'c (Cylinder Strength) < 10MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD034 | A03AD034-00017
|  |  |  | A03AD034 Concrete Work Substructure Work Lean Concrete (including Form work) | A03AD034-00018 Concrete Work Substructure Work Lean Concrete (including Form work) Cement Type-5 F'c (Cylinder Strength) < 10MPa | A03AD034 | 00018 | A03AD034-00018 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  | 0 | 03 | Cement Type-5 | 20 | F'c (Cylinder Strength) < 10MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AD034 | A03AD034-00018
|  |  |  | A03AD035 Concrete Work Substructure Work Form Work (3 times in use) | A03AD035-00001 Concrete Work Substructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035 | 00001 | A03AD035-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 035 | Form Work (3 times in use) | 25 | Flat Form |  | 0 |  | 0 |  | 0 |  | 0 | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AD035 | A03AD035-00001
|  |  |  | A03AD035 Concrete Work Substructure Work Form Work (3 times in use) | A03AD035-00002 Concrete Work Substructure Work Form Work (3 times in use) Circular Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD035 | 00002 | A03AD035-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 035 | Form Work (3 times in use) | 26 | Circular Form |  | 0 |  | 0 |  | 0 |  | 0 | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AD035 | A03AD035-00002
|  |  |  | A03AD036 Concrete Work Substructure Work Form Work (1 time in use) | A03AD036-00001 Concrete Work Substructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD036 | 00001 | A03AD036-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 036 | Form Work (1 time in use) | 25 | Flat Form |  | 0 |  | 0 |  | 0 |  | 0 | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AD036 | A03AD036-00001
|  |  |  | A03AD036 Concrete Work Substructure Work Form Work (1 time in use) | A03AD036-00002 Concrete Work Substructure Work Form Work (1 time in use) Circular Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AD036 | 00002 | A03AD036-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 036 | Form Work (1 time in use) | 26 | Circular Form |  | 0 |  | 0 |  | 0 |  | 0 | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AD036 | A03AD036-00002
|  |  |  | A03AD037 Concrete Work Substructure Work Rebar Work | A03AD037-00001 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) Fy>470MPa | A03AD037 | 00001 | A03AD037-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  | 0 | 09 | Fy>470MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AD037 | A03AD037-00001
|  |  |  | A03AD037 Concrete Work Substructure Work Rebar Work | A03AD037-00002 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 400MPa<Fy≤470MPa | A03AD037 | 00002 | A03AD037-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  | 0 | 10 | 400MPa<Fy≤470MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AD037 | A03AD037-00002
|  |  |  | A03AD037 Concrete Work Substructure Work Rebar Work | A03AD037-00003 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AD037 | 00003 | A03AD037-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  | 0 | 11 | 300MPa<Fy≤400MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AD037 | A03AD037-00003
|  |  |  | A03AD037 Concrete Work Substructure Work Rebar Work | A03AD037-00004 Concrete Work Substructure Work Rebar Work Deformed Bar (Non-Coat.) Fy≤300MPa | A03AD037 | 00004 | A03AD037-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  | 0 | 12 | Fy≤300MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AD037 | A03AD037-00004
|  |  |  | A03AD037 Concrete Work Substructure Work Rebar Work | A03AD037-00005 Concrete Work Substructure Work Rebar Work Deformed Bar (Epoxy Coat.) Fy>470MPa | A03AD037 | 00005 | A03AD037-00005 | AR | A03 | Concrete Work | AD | Substructure Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  | 0 | 09 | Fy>470MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AD037 | A03AD037-00005
|  |  |  | A03AD037 Concrete Work Substructure Work Rebar Work | A03AD037-00006 Concrete Work Substructure Work Rebar Work Deformed Bar (Epoxy Coat.) 400MPa<Fy≤470MPa | A03AD037 | 00006 | A03AD037-00006 | AR | A03 | Concrete Work | AD | Substructure Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  | 0 | 10 | 400MPa<Fy≤470MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AD037 | A03AD037-00006
|  |  |  | A03AD037 Concrete Work Substructure Work Rebar Work | A03AD037-00007 Concrete Work Substructure Work Rebar Work Deformed Bar (Epoxy Coat.) 300MPa<Fy≤400MPa | A03AD037 | 00007 | A03AD037-00007 | AR | A03 | Concrete Work | AD | Substructure Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  | 0 | 11 | 300MPa<Fy≤400MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AD037 | A03AD037-00007
|  |  |  | A03AD037 Concrete Work Substructure Work Rebar Work | A03AD037-00008 Concrete Work Substructure Work Rebar Work Deformed Bar (Epoxy Coat.) Fy≤300MPa | A03AD037 | 00008 | A03AD037-00008 | AR | A03 | Concrete Work | AD | Substructure Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  | 0 | 12 | Fy≤300MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AD037 | A03AD037-00008
|  |  |  | A03AD038 Concrete Work Substructure Work Welded Wire Fabric | A03AD038-00001 Concrete Work Substructure Work Welded Wire Fabric DIA≤6mm | A03AD038 | 00001 | A03AD038-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 038 | Welded Wire Fabric |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 53 | DIA≤6mm | 0 | Mesh Size=DIA( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AD038 | A03AD038-00001
|  |  |  | A03AD038 Concrete Work Substructure Work Welded Wire Fabric | A03AD038-00002 Concrete Work Substructure Work Welded Wire Fabric DIA>6mm | A03AD038 | 00002 | A03AD038-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 038 | Welded Wire Fabric |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 54 | DIA>6mm | 0 | Mesh Size=DIA( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AD038 | A03AD038-00002
|  |  |  | A03AD039 Concrete Work Substructure Work Expansion Joint (Exposed Type) | A03AD039-00001 Concrete Work Substructure Work Expansion Joint (Exposed Type) w/ Flexible Joint Filler, Sealant, Dowel Bar w/ PVC Sleeve | A03AD039 | 00001 | A03AD039-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 039 | Expansion Joint (Exposed Type) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 06 | w/ Flexible Joint Filler, Sealant, Dowel Bar w/ PVC Sleeve |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AD039 | A03AD039-00001
|  |  |  | A03AD040 Concrete Work Substructure Work Expansion Joint (w/ Aluminum Cover) | A03AD040-00001 Concrete Work Substructure Work Expansion Joint (w/ Aluminum Cover) w/ Flexible Joint Filler, Sealant, Aluminum Flashing Cover w/ Fixing Accessories | A03AD040 | 00001 | A03AD040-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 040 | Expansion Joint (w/ Aluminum Cover) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 07 | w/ Flexible Joint Filler, Sealant, Aluminum Flashing Cover w/ Fixing Accessories |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AD040 | A03AD040-00001
|  |  |  | A03AD041 Concrete Work Substructure Work Expansion Joint (w/ Galvanized Steel Cover) | A03AD041-00001 Concrete Work Substructure Work Expansion Joint (w/ Galvanized Steel Cover) w/ Flexible Joint Filler, Sealant, Galv. Steel Cover w/ Galv. Steel Angle, Fixing Accessories | A03AD041 | 00001 | A03AD041-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 041 | Expansion Joint (w/ Galvanized Steel Cover) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 08 | w/ Flexible Joint Filler, Sealant, Galv. Steel Cover w/ Galv. Steel Angle, Fixing Accessories |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AD041 | A03AD041-00001
|  |  |  | A03AD042 Concrete Work Substructure Work Expansion Joint (w/ Stainless Steel Cover) | A03AD042-00001 Concrete Work Substructure Work Expansion Joint (w/ Stainless Steel Cover) w/ Flexible Joint Filler, Sealant, SST Flashing Cover w/ Fixing Accessories | A03AD042 | 00001 | A03AD042-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 042 | Expansion Joint (w/ Stainless Steel Cover) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 09 | w/ Flexible Joint Filler, Sealant, SST Flashing Cover w/ Fixing Accessories |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AD042 | A03AD042-00001
|  |  |  | A03AD043 Concrete Work Substructure Work Expansion Joint (w/ Ready-Made Cover) | A03AD043-00001 Concrete Work Substructure Work Expansion Joint (w/ Ready-Made Cover) w/ Flexible Joint Filler, Sealant, Ready-Made Cover Profile w/ Fixing Accessories | A03AD043 | 00001 | A03AD043-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 043 | Expansion Joint (w/ Ready-Made Cover) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 10 | w/ Flexible Joint Filler, Sealant, Ready-Made Cover Profile w/ Fixing Accessories |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AD043 | A03AD043-00001
|  |  |  | A03AD044 Concrete Work Substructure Work Isolation Joint (Separation Joint) | A03AD044-00001 Concrete Work Substructure Work Isolation Joint (Separation Joint) w/ Flexible Joint Filler, Sealant | A03AD044 | 00001 | A03AD044-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 044 | Isolation Joint (Separation Joint) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 11 | w/ Flexible Joint Filler, Sealant |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AD044 | A03AD044-00001
|  |  |  | A03AD045 Concrete Work Substructure Work Control Joint | A03AD045-00001 Concrete Work Substructure Work Control Joint w/ Joint Sealant, Backstop | A03AD045 | 00001 | A03AD045-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 045 | Control Joint |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 12 | w/ Joint Sealant, Backstop |  | 0 |  | 0 | 0 | Saw Cut: W( )mm x D( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AD045 | A03AD045-00001
|  |  |  | A03AD045 Concrete Work Substructure Work Control Joint | A03AD045-00002 Concrete Work Substructure Work Control Joint w/ Joint Sealant, Backstop, Bottom Crack Inducer | A03AD045 | 00002 | A03AD045-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 045 | Control Joint |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 13 | w/ Joint Sealant, Backstop, Bottom Crack Inducer |  | 0 |  | 0 | 0 | Saw Cut: W( )mm x D( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AD045 | A03AD045-00002
|  |  |  | A03AD046 Concrete Work Substructure Work Water Stop | A03AD046-00001 Concrete Work Substructure Work Water Stop PVC Type | A03AD046 | 00001 | A03AD046-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 046 | Water Stop | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AD046 | A03AD046-00001
|  |  |  | A03AD046 Concrete Work Substructure Work Water Stop | A03AD046-00002 Concrete Work Substructure Work Water Stop Stainless Steel Type | A03AD046 | 00002 | A03AD046-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 046 | Water Stop | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AD046 | A03AD046-00002
|  |  |  | A03AD046 Concrete Work Substructure Work Water Stop | A03AD046-00003 Concrete Work Substructure Work Water Stop Expandable Rubber Type | A03AD046 | 00003 | A03AD046-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 046 | Water Stop | 31 | Expandable Rubber Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AD046 | A03AD046-00003
|  |  |  | A03AD046 Concrete Work Substructure Work Water Stop | A03AD046-00004 Concrete Work Substructure Work Water Stop Copper | A03AD046 | 00004 | A03AD046-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 046 | Water Stop | FS | Copper |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AD046 | A03AD046-00004
|  |  |  | A03AD047 Concrete Work Substructure Work Insulation under Ground Floor | A03AD047-00001 Concrete Work Substructure Work Insulation under Ground Floor Extruded Polystyrene Insulation Board THK<50mm | A03AD047 | 00001 | A03AD047-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 047 | Insulation under Ground Floor | 32 | Extruded Polystyrene Insulation Board |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 31 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AD047 | A03AD047-00001
|  |  |  | A03AD047 Concrete Work Substructure Work Insulation under Ground Floor | A03AD047-00002 Concrete Work Substructure Work Insulation under Ground Floor Extruded Polystyrene Insulation Board 50mm≤THK<75mm | A03AD047 | 00002 | A03AD047-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 047 | Insulation under Ground Floor | 32 | Extruded Polystyrene Insulation Board |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 09 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AD047 | A03AD047-00002
|  |  |  | A03AD047 Concrete Work Substructure Work Insulation under Ground Floor | A03AD047-00003 Concrete Work Substructure Work Insulation under Ground Floor Extruded Polystyrene Insulation Board 75mm≤THK<100mm | A03AD047 | 00003 | A03AD047-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 047 | Insulation under Ground Floor | 32 | Extruded Polystyrene Insulation Board |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 10 | 75mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AD047 | A03AD047-00003
|  |  |  | A03AD047 Concrete Work Substructure Work Insulation under Ground Floor | A03AD047-00004 Concrete Work Substructure Work Insulation under Ground Floor Extruded Polystyrene Insulation Board 100mm≤THK | A03AD047 | 00004 | A03AD047-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 047 | Insulation under Ground Floor | 32 | Extruded Polystyrene Insulation Board |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 11 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AD047 | A03AD047-00004
|  |  |  | A03AD048 Concrete Work Substructure Work Ladder Rung | A03AD048-00004 Concrete Work Substructure Work Ladder Rung Hot-Dip Galvanized Steel Galv.: ASTM A123 | A03AD048 | 00004 | A03AD048-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 048 | Ladder Rung | 33 | Hot-Dip Galvanized Steel |  | 0 |  | 0 |  | 0 |  | 0 | 14 | Galv.: ASTM A123 |  | 0 |  | 0 | 0 | L=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD048 | A03AD048-00004
|  |  |  | A03AD048 Concrete Work Substructure Work Ladder Rung | A03AD048-00005 Concrete Work Substructure Work Ladder Rung SUS SUS 304 | A03AD048 | 00005 | A03AD048-00005 | AR | A03 | Concrete Work | AD | Substructure Work | 048 | Ladder Rung | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 62 | SUS 304 |  | 0 |  | 0 | 0 | L=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD048 | A03AD048-00005
|  |  |  | A03AD048 Concrete Work Substructure Work Ladder Rung | A03AD048-00006 Concrete Work Substructure Work Ladder Rung SUS SUS 316L | A03AD048 | 00006 | A03AD048-00006 | AR | A03 | Concrete Work | AD | Substructure Work | 048 | Ladder Rung | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 63 | SUS 316L |  | 0 |  | 0 | 0 | L=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD048 | A03AD048-00006
|  |  |  | A03AD048 Concrete Work Substructure Work Ladder Rung | A03AD048-00007 Concrete Work Substructure Work Ladder Rung SUS SUS Duplex | A03AD048 | 00007 | A03AD048-00007 | AR | A03 | Concrete Work | AD | Substructure Work | 048 | Ladder Rung | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 64 | SUS Duplex |  | 0 |  | 0 | 0 | L=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD048 | A03AD048-00007
|  |  |  | A03AD048 Concrete Work Substructure Work Ladder Rung | A03AD048-00008 Concrete Work Substructure Work Ladder Rung FRP | A03AD048 | 00008 | A03AD048-00008 | AR | A03 | Concrete Work | AD | Substructure Work | 048 | Ladder Rung | 35 | FRP |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | L=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AD048 | A03AD048-00008
|  |  |  | A03AD049 Concrete Work Substructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | A03AD049-00001 Concrete Work Substructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) Hot-Dip Galvanized Steel Galv.: ASTM A123 | A03AD049 | 00001 | A03AD049-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 33 | Hot-Dip Galvanized Steel |  | 0 |  | 0 |  | 0 |  | 0 | 14 | Galv.: ASTM A123 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AD049 | A03AD049-00001
|  |  |  | A03AD049 Concrete Work Substructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | A03AD049-00003 Concrete Work Substructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) SUS SUS 304 | A03AD049 | 00003 | A03AD049-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 62 | SUS 304 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AD049 | A03AD049-00003
|  |  |  | A03AD049 Concrete Work Substructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | A03AD049-00004 Concrete Work Substructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) SUS SUS 316L | A03AD049 | 00004 | A03AD049-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 63 | SUS 316L |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AD049 | A03AD049-00004
|  |  |  | A03AD049 Concrete Work Substructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | A03AD049-00005 Concrete Work Substructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) SUS SUS Duplex | A03AD049 | 00005 | A03AD049-00005 | AR | A03 | Concrete Work | AD | Substructure Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 64 | SUS Duplex |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AD049 | A03AD049-00005
|  |  |  | A03AD050 Concrete Work Substructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | A03AD050-00001 Concrete Work Substructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) Hot-Dip Galvanized Steel Galv.: ASTM A123 | A03AD050 | 00001 | A03AD050-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 33 | Hot-Dip Galvanized Steel |  | 0 |  | 0 |  | 0 |  | 0 | 14 | Galv.: ASTM A123 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AD050 | A03AD050-00001
|  |  |  | A03AD050 Concrete Work Substructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | A03AD050-00003 Concrete Work Substructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) SUS SUS 304 | A03AD050 | 00003 | A03AD050-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 62 | SUS 304 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AD050 | A03AD050-00003
|  |  |  | A03AD050 Concrete Work Substructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | A03AD050-00004 Concrete Work Substructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) SUS SUS 316L | A03AD050 | 00004 | A03AD050-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 63 | SUS 316L |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AD050 | A03AD050-00004
|  |  |  | A03AD050 Concrete Work Substructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | A03AD050-00005 Concrete Work Substructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) SUS SUS Duplex | A03AD050 | 00005 | A03AD050-00005 | AR | A03 | Concrete Work | AD | Substructure Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 64 | SUS Duplex |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AD050 | A03AD050-00005
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00001 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) M12 | A03AE029 | 00001 | A03AE029-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 37 | M12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00001
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00002 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) M16 | A03AE029 | 00002 | A03AE029-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 38 | M16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00002
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00003 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) M20 | A03AE029 | 00003 | A03AE029-00003 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 39 | M20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00003
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00004 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) M22 | A03AE029 | 00004 | A03AE029-00004 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 40 | M22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00004
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00005 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) M24 | A03AE029 | 00005 | A03AE029-00005 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 41 | M24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00005
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00006 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) M30 | A03AE029 | 00006 | A03AE029-00006 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 42 | M30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00006
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00007 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) M33 | A03AE029 | 00007 | A03AE029-00007 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 43 | M33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00007
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00008 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) M36 | A03AE029 | 00008 | A03AE029-00008 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 44 | M36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00008
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00009 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) M42 | A03AE029 | 00009 | A03AE029-00009 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 45 | M42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00009
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00010 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) M48 | A03AE029 | 00010 | A03AE029-00010 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 46 | M48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00010
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00011 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) M52 | A03AE029 | 00011 | A03AE029-00011 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 47 | M52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00011
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00012 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) M56 | A03AE029 | 00012 | A03AE029-00012 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 48 | M56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00012
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00013 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) M64 | A03AE029 | 00013 | A03AE029-00013 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49 | M64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00013
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00014 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) M72 | A03AE029 | 00014 | A03AE029-00014 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 50 | M72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00014
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00015 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) M76 | A03AE029 | 00015 | A03AE029-00015 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 51 | M76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00015
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00016 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) Over M76 | A03AE029 | 00016 | A03AE029-00016 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 52 | Over M76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00016
|  |  |  | A03AE029 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) | A03AE029-00017 Concrete Work Mass Concrete Work Anchor Bolt (Installation only) M27 | A03AE029 | 00017 | A03AE029-00017 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | AU | M27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE029 | A03AE029-00017
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00001 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M12 | A03AE329 | 00001 | A03AE329-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 37 | M12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00001
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00002 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M16 | A03AE329 | 00002 | A03AE329-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 38 | M16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00002
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00003 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M20 | A03AE329 | 00003 | A03AE329-00003 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 39 | M20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00003
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00004 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M22 | A03AE329 | 00004 | A03AE329-00004 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 40 | M22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00004
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00005 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M24 | A03AE329 | 00005 | A03AE329-00005 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 41 | M24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00005
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00006 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M27 | A03AE329 | 00006 | A03AE329-00006 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | AU | M27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00006
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00007 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M30 | A03AE329 | 00007 | A03AE329-00007 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 42 | M30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00007
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00008 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M33 | A03AE329 | 00008 | A03AE329-00008 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 43 | M33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00008
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00009 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M36 | A03AE329 | 00009 | A03AE329-00009 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 44 | M36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00009
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00010 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M42 | A03AE329 | 00010 | A03AE329-00010 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 45 | M42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00010
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00011 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M48 | A03AE329 | 00011 | A03AE329-00011 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 46 | M48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00011
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00012 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M52 | A03AE329 | 00012 | A03AE329-00012 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 47 | M52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00012
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00013 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M56 | A03AE329 | 00013 | A03AE329-00013 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 48 | M56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00013
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00014 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M64 | A03AE329 | 00014 | A03AE329-00014 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49 | M64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00014
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00015 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M72 | A03AE329 | 00015 | A03AE329-00015 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 50 | M72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00015
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00016 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) M76 | A03AE329 | 00016 | A03AE329-00016 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 51 | M76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00016
|  |  |  | A03AE329 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) | A03AE329-00017 Concrete Work Mass Concrete Work Anchor Bolt (Purchase & Installation) Over M76 | A03AE329 | 00017 | A03AE329-00017 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 52 | Over M76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE329 | A03AE329-00017
|  |  |  | A03AE030 Concrete Work Mass Concrete Work Chemical Anchor Bolt | A03AE030-00001 Concrete Work Mass Concrete Work Chemical Anchor Bolt Including injected Chemical material M10 | A03AE030 | 00001 | A03AE030-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 36 | M10 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE030 | A03AE030-00001
|  |  |  | A03AE030 Concrete Work Mass Concrete Work Chemical Anchor Bolt | A03AE030-00002 Concrete Work Mass Concrete Work Chemical Anchor Bolt Including injected Chemical material M12 | A03AE030 | 00002 | A03AE030-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 37 | M12 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE030 | A03AE030-00002
|  |  |  | A03AE030 Concrete Work Mass Concrete Work Chemical Anchor Bolt | A03AE030-00003 Concrete Work Mass Concrete Work Chemical Anchor Bolt Including injected Chemical material M16 | A03AE030 | 00003 | A03AE030-00003 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 38 | M16 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE030 | A03AE030-00003
|  |  |  | A03AE030 Concrete Work Mass Concrete Work Chemical Anchor Bolt | A03AE030-00004 Concrete Work Mass Concrete Work Chemical Anchor Bolt Including injected Chemical material M20 | A03AE030 | 00004 | A03AE030-00004 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 39 | M20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE030 | A03AE030-00004
|  |  |  | A03AE030 Concrete Work Mass Concrete Work Chemical Anchor Bolt | A03AE030-00005 Concrete Work Mass Concrete Work Chemical Anchor Bolt Including injected Chemical material M22 | A03AE030 | 00005 | A03AE030-00005 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 40 | M22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE030 | A03AE030-00005
|  |  |  | A03AE030 Concrete Work Mass Concrete Work Chemical Anchor Bolt | A03AE030-00006 Concrete Work Mass Concrete Work Chemical Anchor Bolt Including injected Chemical material M24 | A03AE030 | 00006 | A03AE030-00006 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 41 | M24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE030 | A03AE030-00006
|  |  |  | A03AE031 Concrete Work Mass Concrete Work Expansion Anchor Bolt | A03AE031-00001 Concrete Work Mass Concrete Work Expansion Anchor Bolt M10 | A03AE031 | 00001 | A03AE031-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | M10 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE031 | A03AE031-00001
|  |  |  | A03AE031 Concrete Work Mass Concrete Work Expansion Anchor Bolt | A03AE031-00002 Concrete Work Mass Concrete Work Expansion Anchor Bolt M12 | A03AE031 | 00002 | A03AE031-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 37 | M12 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE031 | A03AE031-00002
|  |  |  | A03AE031 Concrete Work Mass Concrete Work Expansion Anchor Bolt | A03AE031-00003 Concrete Work Mass Concrete Work Expansion Anchor Bolt M16 | A03AE031 | 00003 | A03AE031-00003 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 38 | M16 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE031 | A03AE031-00003
|  |  |  | A03AE031 Concrete Work Mass Concrete Work Expansion Anchor Bolt | A03AE031-00004 Concrete Work Mass Concrete Work Expansion Anchor Bolt M20 | A03AE031 | 00004 | A03AE031-00004 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 39 | M20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE031 | A03AE031-00004
|  |  |  | A03AE031 Concrete Work Mass Concrete Work Expansion Anchor Bolt | A03AE031-00005 Concrete Work Mass Concrete Work Expansion Anchor Bolt M22 | A03AE031 | 00005 | A03AE031-00005 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 40 | M22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE031 | A03AE031-00005
|  |  |  | A03AE031 Concrete Work Mass Concrete Work Expansion Anchor Bolt | A03AE031-00006 Concrete Work Mass Concrete Work Expansion Anchor Bolt M24 | A03AE031 | 00006 | A03AE031-00006 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 41 | M24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE031 | A03AE031-00006
|  |  |  | A03AE032 Concrete Work Mass Concrete Work Structural Concrete | A03AE032-00016 Concrete Work Mass Concrete Work Structural Concrete Cement Type-1 35MPa ≤ F'c (Cylinder Strength) Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032 | 00016 | A03AE032-00016 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 13 | 35MPa ≤ F'c (Cylinder Strength) |  | 0 |  | 0 | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE032 | A03AE032-00016
|  |  |  | A03AE032 Concrete Work Mass Concrete Work Structural Concrete | A03AE032-00017 Concrete Work Mass Concrete Work Structural Concrete Cement Type-2 35MPa ≤ F'c (Cylinder Strength) Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032 | 00017 | A03AE032-00017 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 13 | 35MPa ≤ F'c (Cylinder Strength) |  | 0 |  | 0 | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE032 | A03AE032-00017
|  |  |  | A03AE032 Concrete Work Mass Concrete Work Structural Concrete | A03AE032-00018 Concrete Work Mass Concrete Work Structural Concrete Cement Type-5 35MPa ≤ F'c (Cylinder Strength) Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032 | 00018 | A03AE032-00018 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 13 | 35MPa ≤ F'c (Cylinder Strength) |  | 0 |  | 0 | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE032 | A03AE032-00018
|  |  |  | A03AE032 Concrete Work Mass Concrete Work Structural Concrete | A03AE032-00019 Concrete Work Mass Concrete Work Structural Concrete Cement Type-1 30MPa ≤ F'c (Cylinder Strength) < 35MPa Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032 | 00019 | A03AE032-00019 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 14 | 30MPa ≤ F'c (Cylinder Strength) < 35MPa |  | 0 |  | 0 | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE032 | A03AE032-00019
|  |  |  | A03AE032 Concrete Work Mass Concrete Work Structural Concrete | A03AE032-00020 Concrete Work Mass Concrete Work Structural Concrete Cement Type-2 30MPa ≤ F'c (Cylinder Strength) < 35MPa Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032 | 00020 | A03AE032-00020 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 14 | 30MPa ≤ F'c (Cylinder Strength) < 35MPa |  | 0 |  | 0 | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE032 | A03AE032-00020
|  |  |  | A03AE032 Concrete Work Mass Concrete Work Structural Concrete | A03AE032-00021 Concrete Work Mass Concrete Work Structural Concrete Cement Type-5 30MPa ≤ F'c (Cylinder Strength) < 35MPa Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032 | 00021 | A03AE032-00021 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 14 | 30MPa ≤ F'c (Cylinder Strength) < 35MPa |  | 0 |  | 0 | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE032 | A03AE032-00021
|  |  |  | A03AE032 Concrete Work Mass Concrete Work Structural Concrete | A03AE032-00022 Concrete Work Mass Concrete Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032 | 00022 | A03AE032-00022 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 15 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa |  | 0 |  | 0 | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE032 | A03AE032-00022
|  |  |  | A03AE032 Concrete Work Mass Concrete Work Structural Concrete | A03AE032-00023 Concrete Work Mass Concrete Work Structural Concrete Cement Type-2 25MPa ≤ F'c (Cylinder Strength) < 30MPa Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032 | 00023 | A03AE032-00023 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 15 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa |  | 0 |  | 0 | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE032 | A03AE032-00023
|  |  |  | A03AE032 Concrete Work Mass Concrete Work Structural Concrete | A03AE032-00024 Concrete Work Mass Concrete Work Structural Concrete Cement Type-5 25MPa ≤ F'c (Cylinder Strength) < 30MPa Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032 | 00024 | A03AE032-00024 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 15 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa |  | 0 |  | 0 | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE032 | A03AE032-00024
|  |  |  | A03AE032 Concrete Work Mass Concrete Work Structural Concrete | A03AE032-00025 Concrete Work Mass Concrete Work Structural Concrete Cement Type-1 20MPa ≤ F'c (Cylinder Strength) < 25MPa Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032 | 00025 | A03AE032-00025 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 16 | 20MPa ≤ F'c (Cylinder Strength) < 25MPa |  | 0 |  | 0 | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE032 | A03AE032-00025
|  |  |  | A03AE032 Concrete Work Mass Concrete Work Structural Concrete | A03AE032-00026 Concrete Work Mass Concrete Work Structural Concrete Cement Type-2 20MPa ≤ F'c (Cylinder Strength) < 25MPa Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032 | 00026 | A03AE032-00026 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 16 | 20MPa ≤ F'c (Cylinder Strength) < 25MPa |  | 0 |  | 0 | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE032 | A03AE032-00026
|  |  |  | A03AE032 Concrete Work Mass Concrete Work Structural Concrete | A03AE032-00027 Concrete Work Mass Concrete Work Structural Concrete Cement Type-5 20MPa ≤ F'c (Cylinder Strength) < 25MPa Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032 | 00027 | A03AE032-00027 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 16 | 20MPa ≤ F'c (Cylinder Strength) < 25MPa |  | 0 |  | 0 | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE032 | A03AE032-00027
|  |  |  | A03AE032 Concrete Work Mass Concrete Work Structural Concrete | A03AE032-00028 Concrete Work Mass Concrete Work Structural Concrete Cement Type-1 F'c (Cylinder Strength) < 20MPa Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032 | 00028 | A03AE032-00028 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 17 | F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE032 | A03AE032-00028
|  |  |  | A03AE032 Concrete Work Mass Concrete Work Structural Concrete | A03AE032-00029 Concrete Work Mass Concrete Work Structural Concrete Cement Type-2 F'c (Cylinder Strength) < 20MPa Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032 | 00029 | A03AE032-00029 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 17 | F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE032 | A03AE032-00029
|  |  |  | A03AE032 Concrete Work Mass Concrete Work Structural Concrete | A03AE032-00030 Concrete Work Mass Concrete Work Structural Concrete Cement Type-5 F'c (Cylinder Strength) < 20MPa Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | A03AE032 | 00030 | A03AE032-00030 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 17 | F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE032 | A03AE032-00030
|  |  |  | A03AE034 Concrete Work Mass Concrete Work Lean Concrete (including Form work) | A03AE034-00010 Concrete Work Mass Concrete Work Lean Concrete (including Form work) Cement Type-1 15MPa ≤ F'c (Cylinder Strength) < 20MPa | A03AE034 | 00010 | A03AE034-00010 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  | 0 | 01 | Cement Type-1 | 18 | 15MPa ≤ F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE034 | A03AE034-00010
|  |  |  | A03AE034 Concrete Work Mass Concrete Work Lean Concrete (including Form work) | A03AE034-00011 Concrete Work Mass Concrete Work Lean Concrete (including Form work) Cement Type-2 15MPa ≤ F'c (Cylinder Strength) < 20MPa | A03AE034 | 00011 | A03AE034-00011 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  | 0 | 02 | Cement Type-2 | 18 | 15MPa ≤ F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE034 | A03AE034-00011
|  |  |  | A03AE034 Concrete Work Mass Concrete Work Lean Concrete (including Form work) | A03AE034-00012 Concrete Work Mass Concrete Work Lean Concrete (including Form work) Cement Type-5 15MPa ≤ F'c (Cylinder Strength) < 20MPa | A03AE034 | 00012 | A03AE034-00012 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  | 0 | 03 | Cement Type-5 | 18 | 15MPa ≤ F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE034 | A03AE034-00012
|  |  |  | A03AE034 Concrete Work Mass Concrete Work Lean Concrete (including Form work) | A03AE034-00013 Concrete Work Mass Concrete Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AE034 | 00013 | A03AE034-00013 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  | 0 | 01 | Cement Type-1 | 19 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE034 | A03AE034-00013
|  |  |  | A03AE034 Concrete Work Mass Concrete Work Lean Concrete (including Form work) | A03AE034-00014 Concrete Work Mass Concrete Work Lean Concrete (including Form work) Cement Type-2 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AE034 | 00014 | A03AE034-00014 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  | 0 | 02 | Cement Type-2 | 19 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE034 | A03AE034-00014
|  |  |  | A03AE034 Concrete Work Mass Concrete Work Lean Concrete (including Form work) | A03AE034-00015 Concrete Work Mass Concrete Work Lean Concrete (including Form work) Cement Type-5 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AE034 | 00015 | A03AE034-00015 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  | 0 | 03 | Cement Type-5 | 19 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE034 | A03AE034-00015
|  |  |  | A03AE034 Concrete Work Mass Concrete Work Lean Concrete (including Form work) | A03AE034-00016 Concrete Work Mass Concrete Work Lean Concrete (including Form work) Cement Type-1 F'c (Cylinder Strength) < 10MPa | A03AE034 | 00016 | A03AE034-00016 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  | 0 | 01 | Cement Type-1 | 20 | F'c (Cylinder Strength) < 10MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE034 | A03AE034-00016
|  |  |  | A03AE034 Concrete Work Mass Concrete Work Lean Concrete (including Form work) | A03AE034-00017 Concrete Work Mass Concrete Work Lean Concrete (including Form work) Cement Type-2 F'c (Cylinder Strength) < 10MPa | A03AE034 | 00017 | A03AE034-00017 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  | 0 | 02 | Cement Type-2 | 20 | F'c (Cylinder Strength) < 10MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE034 | A03AE034-00017
|  |  |  | A03AE034 Concrete Work Mass Concrete Work Lean Concrete (including Form work) | A03AE034-00018 Concrete Work Mass Concrete Work Lean Concrete (including Form work) Cement Type-5 F'c (Cylinder Strength) < 10MPa | A03AE034 | 00018 | A03AE034-00018 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  | 0 | 03 | Cement Type-5 | 20 | F'c (Cylinder Strength) < 10MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE034 | A03AE034-00018
|  |  |  | A03AE035 Concrete Work Mass Concrete Work Form Work (3 times in use) | A03AE035-00001 Concrete Work Mass Concrete Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AE035 | 00001 | A03AE035-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 035 | Form Work (3 times in use) | 25 | Flat Form |  | 0 |  | 0 |  | 0 |  | 0 | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AE035 | A03AE035-00001
|  |  |  | A03AE035 Concrete Work Mass Concrete Work Form Work (3 times in use) | A03AE035-00002 Concrete Work Mass Concrete Work Form Work (3 times in use) Circular Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AE035 | 00002 | A03AE035-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 035 | Form Work (3 times in use) | 26 | Circular Form |  | 0 |  | 0 |  | 0 |  | 0 | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AE035 | A03AE035-00002
|  |  |  | A03AE036 Concrete Work Mass Concrete Work Form Work (1 time in use) | A03AE036-00001 Concrete Work Mass Concrete Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AE036 | 00001 | A03AE036-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 036 | Form Work (1 time in use) | 25 | Flat Form |  | 0 |  | 0 |  | 0 |  | 0 | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AE036 | A03AE036-00001
|  |  |  | A03AE036 Concrete Work Mass Concrete Work Form Work (1 time in use) | A03AE036-00002 Concrete Work Mass Concrete Work Form Work (1 time in use) Circular Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AE036 | 00002 | A03AE036-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 036 | Form Work (1 time in use) | 26 | Circular Form |  | 0 |  | 0 |  | 0 |  | 0 | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AE036 | A03AE036-00002
|  |  |  | A03AE037 Concrete Work Mass Concrete Work Rebar Work | A03AE037-00001 Concrete Work Mass Concrete Work Rebar Work Deformed Bar (Non-Coat.) Fy>470MPa | A03AE037 | 00001 | A03AE037-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  | 0 | 09 | Fy>470MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AE037 | A03AE037-00001
|  |  |  | A03AE037 Concrete Work Mass Concrete Work Rebar Work | A03AE037-00002 Concrete Work Mass Concrete Work Rebar Work Deformed Bar (Non-Coat.) 400MPa<Fy≤470MPa | A03AE037 | 00002 | A03AE037-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  | 0 | 10 | 400MPa<Fy≤470MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AE037 | A03AE037-00002
|  |  |  | A03AE037 Concrete Work Mass Concrete Work Rebar Work | A03AE037-00003 Concrete Work Mass Concrete Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AE037 | 00003 | A03AE037-00003 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  | 0 | 11 | 300MPa<Fy≤400MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AE037 | A03AE037-00003
|  |  |  | A03AE037 Concrete Work Mass Concrete Work Rebar Work | A03AE037-00004 Concrete Work Mass Concrete Work Rebar Work Deformed Bar (Non-Coat.) Fy≤300MPa | A03AE037 | 00004 | A03AE037-00004 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  | 0 | 12 | Fy≤300MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AE037 | A03AE037-00004
|  |  |  | A03AE037 Concrete Work Mass Concrete Work Rebar Work | A03AE037-00005 Concrete Work Mass Concrete Work Rebar Work Deformed Bar (Epoxy Coat.) Fy>470MPa | A03AE037 | 00005 | A03AE037-00005 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  | 0 | 09 | Fy>470MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AE037 | A03AE037-00005
|  |  |  | A03AE037 Concrete Work Mass Concrete Work Rebar Work | A03AE037-00006 Concrete Work Mass Concrete Work Rebar Work Deformed Bar (Epoxy Coat.) 400MPa<Fy≤470MPa | A03AE037 | 00006 | A03AE037-00006 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  | 0 | 10 | 400MPa<Fy≤470MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AE037 | A03AE037-00006
|  |  |  | A03AE037 Concrete Work Mass Concrete Work Rebar Work | A03AE037-00007 Concrete Work Mass Concrete Work Rebar Work Deformed Bar (Epoxy Coat.) 300MPa<Fy≤400MPa | A03AE037 | 00007 | A03AE037-00007 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  | 0 | 11 | 300MPa<Fy≤400MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AE037 | A03AE037-00007
|  |  |  | A03AE037 Concrete Work Mass Concrete Work Rebar Work | A03AE037-00008 Concrete Work Mass Concrete Work Rebar Work Deformed Bar (Epoxy Coat.) Fy≤300MPa | A03AE037 | 00008 | A03AE037-00008 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  | 0 | 12 | Fy≤300MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AE037 | A03AE037-00008
|  |  |  | A03AE046 Concrete Work Mass Concrete Work Water Stop | A03AE046-00001 Concrete Work Mass Concrete Work Water Stop PVC Type | A03AE046 | 00001 | A03AE046-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 046 | Water Stop | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AE046 | A03AE046-00001
|  |  |  | A03AE046 Concrete Work Mass Concrete Work Water Stop | A03AE046-00002 Concrete Work Mass Concrete Work Water Stop Stainless Steel Type | A03AE046 | 00002 | A03AE046-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 046 | Water Stop | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AE046 | A03AE046-00002
|  |  |  | A03AE046 Concrete Work Mass Concrete Work Water Stop | A03AE046-00003 Concrete Work Mass Concrete Work Water Stop Expandable Rubber Type | A03AE046 | 00003 | A03AE046-00003 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 046 | Water Stop | 31 | Expandable Rubber Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AE046 | A03AE046-00003
|  |  |  | A03AE046 Concrete Work Mass Concrete Work Water Stop | A03AE046-00004 Concrete Work Mass Concrete Work Water Stop Copper | A03AE046 | 00004 | A03AE046-00004 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 046 | Water Stop | FS | Copper |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AE046 | A03AE046-00004
|  |  |  | A03AE049 Concrete Work Mass Concrete Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | A03AE049-00001 Concrete Work Mass Concrete Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) Hot-Dip Galvanized Steel Galv.: ASTM A123 | A03AE049 | 00001 | A03AE049-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 33 | Hot-Dip Galvanized Steel |  | 0 |  | 0 |  | 0 |  | 0 | 14 | Galv.: ASTM A123 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AE049 | A03AE049-00001
|  |  |  | A03AE049 Concrete Work Mass Concrete Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | A03AE049-00003 Concrete Work Mass Concrete Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) SUS SUS 304 | A03AE049 | 00003 | A03AE049-00003 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 62 | SUS 304 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AE049 | A03AE049-00003
|  |  |  | A03AE049 Concrete Work Mass Concrete Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | A03AE049-00004 Concrete Work Mass Concrete Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) SUS SUS 316L | A03AE049 | 00004 | A03AE049-00004 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 63 | SUS 316L |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AE049 | A03AE049-00004
|  |  |  | A03AE049 Concrete Work Mass Concrete Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | A03AE049-00005 Concrete Work Mass Concrete Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) SUS SUS Duplex | A03AE049 | 00005 | A03AE049-00005 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 64 | SUS Duplex |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AE049 | A03AE049-00005
|  |  |  | A03AE050 Concrete Work Mass Concrete Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | A03AE050-00001 Concrete Work Mass Concrete Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) Hot-Dip Galvanized Steel Galv.: ASTM A123 | A03AE050 | 00001 | A03AE050-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 33 | Hot-Dip Galvanized Steel |  | 0 |  | 0 |  | 0 |  | 0 | 14 | Galv.: ASTM A123 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AE050 | A03AE050-00001
|  |  |  | A03AE050 Concrete Work Mass Concrete Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | A03AE050-00003 Concrete Work Mass Concrete Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) SUS SUS 304 | A03AE050 | 00003 | A03AE050-00003 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 62 | SUS 304 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AE050 | A03AE050-00003
|  |  |  | A03AE050 Concrete Work Mass Concrete Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | A03AE050-00004 Concrete Work Mass Concrete Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) SUS SUS 316L | A03AE050 | 00004 | A03AE050-00004 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 63 | SUS 316L |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AE050 | A03AE050-00004
|  |  |  | A03AE050 Concrete Work Mass Concrete Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | A03AE050-00005 Concrete Work Mass Concrete Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) SUS SUS Duplex | A03AE050 | 00005 | A03AE050-00005 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 64 | SUS Duplex |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AE050 | A03AE050-00005
|  |  |  | A03AE052 Concrete Work Mass Concrete Work Concrete Temperature Monitoring | A03AE052-00001 Concrete Work Mass Concrete Work Concrete Temperature Monitoring Including Themo Coupler, Monitoring & Record Acc. To Approved MS | A03AE052 | 00001 | A03AE052-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 052 | Concrete Temperature Monitoring |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 16 | Including Themo Coupler, Monitoring & Record Acc. To Approved MS |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | SET | SET | A03AE052 | A03AE052-00001
|  |  |  | A03AE053 Concrete Work Mass Concrete Work Steel Casing for CEP | A03AE053-00001 Concrete Work Mass Concrete Work Steel Casing for CEP Including Anchoring, Tar Epoxy Coating, Frame & Accessories, Weldings | A03AE053 | 00001 | A03AE053-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 053 | Steel Casing for CEP |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 17 | Including Anchoring, Tar Epoxy Coating, Frame & Accessories, Weldings |  | 0 |  | 0 | 0 | Steel Pipe: D( )mm x THK( )t x L( )m, Steel Plate: W( )mm x L( )mm x THK( )t | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AE053 | A03AE053-00001
|  |  |  | A03AE054 Concrete Work Mass Concrete Work System Form | A03AE054-00001 Concrete Work Mass Concrete Work System Form Heavy Duty Forms, Metal Framed Playwood forms Including Form Tie, All Accessories, Sealing of Form Tie Hole, Separator & Anchor Box out, Chamfer for Exposed Edge, Opening & Sleeve, Shoring, Scaffording, Safety Measures and Shop Drawing | A03AE054 | 00001 | A03AE054-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 054 | System Form | 36 | Heavy Duty Forms, Metal Framed Playwood forms |  | 0 |  | 0 |  | 0 |  | 0 | 18 | Including Form Tie, All Accessories, Sealing of Form Tie Hole, Separator & Anchor Box out, Chamfer for Exposed Edge, Opening & Sleeve, Shoring, Scaffording, Safety Measures and Shop Drawing |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE054 | A03AE054-00001
|  |  |  | A03AE055 Concrete Work Mass Concrete Work System Support | A03AE055-00001 Concrete Work Mass Concrete Work System Support | A03AE055 | 00001 | A03AE055-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 055 | System Support |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AE055 | A03AE055-00001
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00001 Concrete Work Superstructure Work Anchor Bolt (Installation only) M12 | A03AF029 | 00001 | A03AF029-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 37 | M12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00001
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00002 Concrete Work Superstructure Work Anchor Bolt (Installation only) M16 | A03AF029 | 00002 | A03AF029-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 38 | M16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00002
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00003 Concrete Work Superstructure Work Anchor Bolt (Installation only) M20 | A03AF029 | 00003 | A03AF029-00003 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 39 | M20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00003
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00004 Concrete Work Superstructure Work Anchor Bolt (Installation only) M22 | A03AF029 | 00004 | A03AF029-00004 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 40 | M22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00004
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00005 Concrete Work Superstructure Work Anchor Bolt (Installation only) M24 | A03AF029 | 00005 | A03AF029-00005 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 41 | M24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00005
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00006 Concrete Work Superstructure Work Anchor Bolt (Installation only) M30 | A03AF029 | 00006 | A03AF029-00006 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 42 | M30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00006
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00007 Concrete Work Superstructure Work Anchor Bolt (Installation only) M33 | A03AF029 | 00007 | A03AF029-00007 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 43 | M33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00007
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00008 Concrete Work Superstructure Work Anchor Bolt (Installation only) M36 | A03AF029 | 00008 | A03AF029-00008 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 44 | M36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00008
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00009 Concrete Work Superstructure Work Anchor Bolt (Installation only) M42 | A03AF029 | 00009 | A03AF029-00009 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 45 | M42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00009
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00010 Concrete Work Superstructure Work Anchor Bolt (Installation only) M48 | A03AF029 | 00010 | A03AF029-00010 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 46 | M48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00010
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00011 Concrete Work Superstructure Work Anchor Bolt (Installation only) M52 | A03AF029 | 00011 | A03AF029-00011 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 47 | M52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00011
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00012 Concrete Work Superstructure Work Anchor Bolt (Installation only) M56 | A03AF029 | 00012 | A03AF029-00012 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 48 | M56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00012
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00013 Concrete Work Superstructure Work Anchor Bolt (Installation only) M64 | A03AF029 | 00013 | A03AF029-00013 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49 | M64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00013
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00014 Concrete Work Superstructure Work Anchor Bolt (Installation only) M72 | A03AF029 | 00014 | A03AF029-00014 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 50 | M72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00014
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00015 Concrete Work Superstructure Work Anchor Bolt (Installation only) M76 | A03AF029 | 00015 | A03AF029-00015 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 51 | M76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00015
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00016 Concrete Work Superstructure Work Anchor Bolt (Installation only) Over M76 | A03AF029 | 00016 | A03AF029-00016 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 52 | Over M76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00016
|  |  |  | A03AF029 Concrete Work Superstructure Work Anchor Bolt (Installation only) | A03AF029-00017 Concrete Work Superstructure Work Anchor Bolt (Installation only) M27 | A03AF029 | 00017 | A03AF029-00017 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | AU | M27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF029 | A03AF029-00017
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00001 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) M12 | A03AF329 | 00001 | A03AF329-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 37 | M12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00001
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00002 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) M16 | A03AF329 | 00002 | A03AF329-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 38 | M16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00002
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00003 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) M20 | A03AF329 | 00003 | A03AF329-00003 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 39 | M20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00003
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00004 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) M22 | A03AF329 | 00004 | A03AF329-00004 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 40 | M22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00004
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00005 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) M24 | A03AF329 | 00005 | A03AF329-00005 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 41 | M24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00005
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00006 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) M27 | A03AF329 | 00006 | A03AF329-00006 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | AU | M27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00006
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00007 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) M30 | A03AF329 | 00007 | A03AF329-00007 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 42 | M30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00007
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00008 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) M33 | A03AF329 | 00008 | A03AF329-00008 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 43 | M33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00008
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00009 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) M36 | A03AF329 | 00009 | A03AF329-00009 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 44 | M36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00009
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00010 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) M42 | A03AF329 | 00010 | A03AF329-00010 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 45 | M42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00010
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00011 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) M48 | A03AF329 | 00011 | A03AF329-00011 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 46 | M48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00011
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00012 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) M52 | A03AF329 | 00012 | A03AF329-00012 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 47 | M52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00012
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00013 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) M56 | A03AF329 | 00013 | A03AF329-00013 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 48 | M56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00013
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00014 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) M64 | A03AF329 | 00014 | A03AF329-00014 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49 | M64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00014
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00015 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) M72 | A03AF329 | 00015 | A03AF329-00015 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 50 | M72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00015
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00016 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) M76 | A03AF329 | 00016 | A03AF329-00016 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 51 | M76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00016
|  |  |  | A03AF329 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) | A03AF329-00017 Concrete Work Superstructure Work Anchor Bolt (Purchase & Installation) Over M76 | A03AF329 | 00017 | A03AF329-00017 | AR | A03 | Concrete Work | AF | Superstructure Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 52 | Over M76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF329 | A03AF329-00017
|  |  |  | A03AF030 Concrete Work Superstructure Work Chemical Anchor Bolt | A03AF030-00001 Concrete Work Superstructure Work Chemical Anchor Bolt Including injected Chemical material M10 | A03AF030 | 00001 | A03AF030-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 36 | M10 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF030 | A03AF030-00001
|  |  |  | A03AF030 Concrete Work Superstructure Work Chemical Anchor Bolt | A03AF030-00002 Concrete Work Superstructure Work Chemical Anchor Bolt Including injected Chemical material M12 | A03AF030 | 00002 | A03AF030-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 37 | M12 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF030 | A03AF030-00002
|  |  |  | A03AF030 Concrete Work Superstructure Work Chemical Anchor Bolt | A03AF030-00003 Concrete Work Superstructure Work Chemical Anchor Bolt Including injected Chemical material M16 | A03AF030 | 00003 | A03AF030-00003 | AR | A03 | Concrete Work | AF | Superstructure Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 38 | M16 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF030 | A03AF030-00003
|  |  |  | A03AF030 Concrete Work Superstructure Work Chemical Anchor Bolt | A03AF030-00004 Concrete Work Superstructure Work Chemical Anchor Bolt Including injected Chemical material M20 | A03AF030 | 00004 | A03AF030-00004 | AR | A03 | Concrete Work | AF | Superstructure Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 39 | M20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF030 | A03AF030-00004
|  |  |  | A03AF030 Concrete Work Superstructure Work Chemical Anchor Bolt | A03AF030-00005 Concrete Work Superstructure Work Chemical Anchor Bolt Including injected Chemical material M22 | A03AF030 | 00005 | A03AF030-00005 | AR | A03 | Concrete Work | AF | Superstructure Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 40 | M22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF030 | A03AF030-00005
|  |  |  | A03AF030 Concrete Work Superstructure Work Chemical Anchor Bolt | A03AF030-00006 Concrete Work Superstructure Work Chemical Anchor Bolt Including injected Chemical material M24 | A03AF030 | 00006 | A03AF030-00006 | AR | A03 | Concrete Work | AF | Superstructure Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 41 | M24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF030 | A03AF030-00006
|  |  |  | A03AF031 Concrete Work Superstructure Work Expansion Anchor Bolt | A03AF031-00001 Concrete Work Superstructure Work Expansion Anchor Bolt M10 | A03AF031 | 00001 | A03AF031-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | M10 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF031 | A03AF031-00001
|  |  |  | A03AF031 Concrete Work Superstructure Work Expansion Anchor Bolt | A03AF031-00002 Concrete Work Superstructure Work Expansion Anchor Bolt M12 | A03AF031 | 00002 | A03AF031-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 37 | M12 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF031 | A03AF031-00002
|  |  |  | A03AF031 Concrete Work Superstructure Work Expansion Anchor Bolt | A03AF031-00003 Concrete Work Superstructure Work Expansion Anchor Bolt M16 | A03AF031 | 00003 | A03AF031-00003 | AR | A03 | Concrete Work | AF | Superstructure Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 38 | M16 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF031 | A03AF031-00003
|  |  |  | A03AF031 Concrete Work Superstructure Work Expansion Anchor Bolt | A03AF031-00004 Concrete Work Superstructure Work Expansion Anchor Bolt M20 | A03AF031 | 00004 | A03AF031-00004 | AR | A03 | Concrete Work | AF | Superstructure Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 39 | M20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF031 | A03AF031-00004
|  |  |  | A03AF031 Concrete Work Superstructure Work Expansion Anchor Bolt | A03AF031-00005 Concrete Work Superstructure Work Expansion Anchor Bolt M22 | A03AF031 | 00005 | A03AF031-00005 | AR | A03 | Concrete Work | AF | Superstructure Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 40 | M22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF031 | A03AF031-00005
|  |  |  | A03AF031 Concrete Work Superstructure Work Expansion Anchor Bolt | A03AF031-00006 Concrete Work Superstructure Work Expansion Anchor Bolt M24 | A03AF031 | 00006 | A03AF031-00006 | AR | A03 | Concrete Work | AF | Superstructure Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 41 | M24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AF031 | A03AF031-00006
|  |  |  | A03AF032 Concrete Work Superstructure Work Structural Concrete | A03AF032-00016 Concrete Work Superstructure Work Structural Concrete Cement Type-1 35MPa ≤ F'c (Cylinder Strength) | A03AF032 | 00016 | A03AF032-00016 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 13 | 35MPa ≤ F'c (Cylinder Strength) |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF032 | A03AF032-00016
|  |  |  | A03AF032 Concrete Work Superstructure Work Structural Concrete | A03AF032-00017 Concrete Work Superstructure Work Structural Concrete Cement Type-2 35MPa ≤ F'c (Cylinder Strength) | A03AF032 | 00017 | A03AF032-00017 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 13 | 35MPa ≤ F'c (Cylinder Strength) |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF032 | A03AF032-00017
|  |  |  | A03AF032 Concrete Work Superstructure Work Structural Concrete | A03AF032-00018 Concrete Work Superstructure Work Structural Concrete Cement Type-5 35MPa ≤ F'c (Cylinder Strength) | A03AF032 | 00018 | A03AF032-00018 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 13 | 35MPa ≤ F'c (Cylinder Strength) |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF032 | A03AF032-00018
|  |  |  | A03AF032 Concrete Work Superstructure Work Structural Concrete | A03AF032-00019 Concrete Work Superstructure Work Structural Concrete Cement Type-1 30MPa ≤ F'c (Cylinder Strength) < 35MPa | A03AF032 | 00019 | A03AF032-00019 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 14 | 30MPa ≤ F'c (Cylinder Strength) < 35MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF032 | A03AF032-00019
|  |  |  | A03AF032 Concrete Work Superstructure Work Structural Concrete | A03AF032-00020 Concrete Work Superstructure Work Structural Concrete Cement Type-2 30MPa ≤ F'c (Cylinder Strength) < 35MPa | A03AF032 | 00020 | A03AF032-00020 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 14 | 30MPa ≤ F'c (Cylinder Strength) < 35MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF032 | A03AF032-00020
|  |  |  | A03AF032 Concrete Work Superstructure Work Structural Concrete | A03AF032-00021 Concrete Work Superstructure Work Structural Concrete Cement Type-5 30MPa ≤ F'c (Cylinder Strength) < 35MPa | A03AF032 | 00021 | A03AF032-00021 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 14 | 30MPa ≤ F'c (Cylinder Strength) < 35MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF032 | A03AF032-00021
|  |  |  | A03AF032 Concrete Work Superstructure Work Structural Concrete | A03AF032-00022 Concrete Work Superstructure Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032 | 00022 | A03AF032-00022 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 15 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF032 | A03AF032-00022
|  |  |  | A03AF032 Concrete Work Superstructure Work Structural Concrete | A03AF032-00023 Concrete Work Superstructure Work Structural Concrete Cement Type-2 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032 | 00023 | A03AF032-00023 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 15 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF032 | A03AF032-00023
|  |  |  | A03AF032 Concrete Work Superstructure Work Structural Concrete | A03AF032-00024 Concrete Work Superstructure Work Structural Concrete Cement Type-5 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AF032 | 00024 | A03AF032-00024 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 15 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF032 | A03AF032-00024
|  |  |  | A03AF032 Concrete Work Superstructure Work Structural Concrete | A03AF032-00025 Concrete Work Superstructure Work Structural Concrete Cement Type-1 20MPa ≤ F'c (Cylinder Strength) < 25MPa | A03AF032 | 00025 | A03AF032-00025 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 16 | 20MPa ≤ F'c (Cylinder Strength) < 25MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF032 | A03AF032-00025
|  |  |  | A03AF032 Concrete Work Superstructure Work Structural Concrete | A03AF032-00026 Concrete Work Superstructure Work Structural Concrete Cement Type-2 20MPa ≤ F'c (Cylinder Strength) < 25MPa | A03AF032 | 00026 | A03AF032-00026 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 16 | 20MPa ≤ F'c (Cylinder Strength) < 25MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF032 | A03AF032-00026
|  |  |  | A03AF032 Concrete Work Superstructure Work Structural Concrete | A03AF032-00027 Concrete Work Superstructure Work Structural Concrete Cement Type-5 20MPa ≤ F'c (Cylinder Strength) < 25MPa | A03AF032 | 00027 | A03AF032-00027 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 16 | 20MPa ≤ F'c (Cylinder Strength) < 25MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF032 | A03AF032-00027
|  |  |  | A03AF032 Concrete Work Superstructure Work Structural Concrete | A03AF032-00028 Concrete Work Superstructure Work Structural Concrete Cement Type-1 F'c (Cylinder Strength) < 20MPa | A03AF032 | 00028 | A03AF032-00028 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 17 | F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF032 | A03AF032-00028
|  |  |  | A03AF032 Concrete Work Superstructure Work Structural Concrete | A03AF032-00029 Concrete Work Superstructure Work Structural Concrete Cement Type-2 F'c (Cylinder Strength) < 20MPa | A03AF032 | 00029 | A03AF032-00029 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 17 | F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF032 | A03AF032-00029
|  |  |  | A03AF032 Concrete Work Superstructure Work Structural Concrete | A03AF032-00030 Concrete Work Superstructure Work Structural Concrete Cement Type-5 F'c (Cylinder Strength) < 20MPa | A03AF032 | 00030 | A03AF032-00030 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 17 | F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF032 | A03AF032-00030
|  |  |  | A03AF035 Concrete Work Superstructure Work Form Work (3 times in use) | A03AF035-00001 Concrete Work Superstructure Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF035 | 00001 | A03AF035-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 035 | Form Work (3 times in use) | 25 | Flat Form |  | 0 |  | 0 |  | 0 |  | 0 | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AF035 | A03AF035-00001
|  |  |  | A03AF035 Concrete Work Superstructure Work Form Work (3 times in use) | A03AF035-00002 Concrete Work Superstructure Work Form Work (3 times in use) Circular Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF035 | 00002 | A03AF035-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 035 | Form Work (3 times in use) | 26 | Circular Form |  | 0 |  | 0 |  | 0 |  | 0 | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AF035 | A03AF035-00002
|  |  |  | A03AF036 Concrete Work Superstructure Work Form Work (1 time in use) | A03AF036-00001 Concrete Work Superstructure Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF036 | 00001 | A03AF036-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 036 | Form Work (1 time in use) | 25 | Flat Form |  | 0 |  | 0 |  | 0 |  | 0 | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AF036 | A03AF036-00001
|  |  |  | A03AF036 Concrete Work Superstructure Work Form Work (1 time in use) | A03AF036-00002 Concrete Work Superstructure Work Form Work (1 time in use) Circular Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AF036 | 00002 | A03AF036-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 036 | Form Work (1 time in use) | 26 | Circular Form |  | 0 |  | 0 |  | 0 |  | 0 | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AF036 | A03AF036-00002
|  |  |  | A03AF037 Concrete Work Superstructure Work Rebar Work | A03AF037-00001 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) Fy>470MPa | A03AF037 | 00001 | A03AF037-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  | 0 | 09 | Fy>470MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AF037 | A03AF037-00001
|  |  |  | A03AF037 Concrete Work Superstructure Work Rebar Work | A03AF037-00002 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 400MPa<Fy≤470MPa | A03AF037 | 00002 | A03AF037-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  | 0 | 10 | 400MPa<Fy≤470MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AF037 | A03AF037-00002
|  |  |  | A03AF037 Concrete Work Superstructure Work Rebar Work | A03AF037-00003 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AF037 | 00003 | A03AF037-00003 | AR | A03 | Concrete Work | AF | Superstructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  | 0 | 11 | 300MPa<Fy≤400MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AF037 | A03AF037-00003
|  |  |  | A03AF037 Concrete Work Superstructure Work Rebar Work | A03AF037-00004 Concrete Work Superstructure Work Rebar Work Deformed Bar (Non-Coat.) Fy≤300MPa | A03AF037 | 00004 | A03AF037-00004 | AR | A03 | Concrete Work | AF | Superstructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  | 0 | 12 | Fy≤300MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AF037 | A03AF037-00004
|  |  |  | A03AF037 Concrete Work Superstructure Work Rebar Work | A03AF037-00005 Concrete Work Superstructure Work Rebar Work Deformed Bar (Epoxy Coat.) Fy>470MPa | A03AF037 | 00005 | A03AF037-00005 | AR | A03 | Concrete Work | AF | Superstructure Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  | 0 | 09 | Fy>470MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AF037 | A03AF037-00005
|  |  |  | A03AF037 Concrete Work Superstructure Work Rebar Work | A03AF037-00006 Concrete Work Superstructure Work Rebar Work Deformed Bar (Epoxy Coat.) 400MPa<Fy≤470MPa | A03AF037 | 00006 | A03AF037-00006 | AR | A03 | Concrete Work | AF | Superstructure Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  | 0 | 10 | 400MPa<Fy≤470MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AF037 | A03AF037-00006
|  |  |  | A03AF037 Concrete Work Superstructure Work Rebar Work | A03AF037-00007 Concrete Work Superstructure Work Rebar Work Deformed Bar (Epoxy Coat.) 300MPa<Fy≤400MPa | A03AF037 | 00007 | A03AF037-00007 | AR | A03 | Concrete Work | AF | Superstructure Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  | 0 | 11 | 300MPa<Fy≤400MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AF037 | A03AF037-00007
|  |  |  | A03AF037 Concrete Work Superstructure Work Rebar Work | A03AF037-00008 Concrete Work Superstructure Work Rebar Work Deformed Bar (Epoxy Coat.) Fy≤300MPa | A03AF037 | 00008 | A03AF037-00008 | AR | A03 | Concrete Work | AF | Superstructure Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  | 0 | 12 | Fy≤300MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AF037 | A03AF037-00008
|  |  |  | A03AF038 Concrete Work Superstructure Work Welded Wire Fabric | A03AF038-00001 Concrete Work Superstructure Work Welded Wire Fabric DIA≤6mm | A03AF038 | 00001 | A03AF038-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 038 | Welded Wire Fabric |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 53 | DIA≤6mm | 0 | Mesh Size=DIA( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AF038 | A03AF038-00001
|  |  |  | A03AF038 Concrete Work Superstructure Work Welded Wire Fabric | A03AF038-00002 Concrete Work Superstructure Work Welded Wire Fabric DIA>6mm | A03AF038 | 00002 | A03AF038-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 038 | Welded Wire Fabric |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 54 | DIA>6mm | 0 | Mesh Size=DIA( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AF038 | A03AF038-00002
|  |  |  | A03AF039 Concrete Work Superstructure Work Expansion Joint (Exposed Type) | A03AF039-00001 Concrete Work Superstructure Work Expansion Joint (Exposed Type) w/ Flexible Joint Filler, Sealant, Dowel Bar w/ PVC Sleeve | A03AF039 | 00001 | A03AF039-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 039 | Expansion Joint (Exposed Type) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 06 | w/ Flexible Joint Filler, Sealant, Dowel Bar w/ PVC Sleeve |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AF039 | A03AF039-00001
|  |  |  | A03AF040 Concrete Work Superstructure Work Expansion Joint (w/ Aluminum Cover) | A03AF040-00001 Concrete Work Superstructure Work Expansion Joint (w/ Aluminum Cover) w/ Flexible Joint Filler, Sealant, Aluminum Flashing Cover w/ Fixing Accessories | A03AF040 | 00001 | A03AF040-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 040 | Expansion Joint (w/ Aluminum Cover) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 07 | w/ Flexible Joint Filler, Sealant, Aluminum Flashing Cover w/ Fixing Accessories |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AF040 | A03AF040-00001
|  |  |  | A03AF041 Concrete Work Superstructure Work Expansion Joint (w/ Galvanized Steel Cover) | A03AF041-00001 Concrete Work Superstructure Work Expansion Joint (w/ Galvanized Steel Cover) w/ Flexible Joint Filler, Sealant, Galv. Steel Cover w/ Galv. Steel Angle, Fixing Accessories | A03AF041 | 00001 | A03AF041-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 041 | Expansion Joint (w/ Galvanized Steel Cover) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 08 | w/ Flexible Joint Filler, Sealant, Galv. Steel Cover w/ Galv. Steel Angle, Fixing Accessories |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AF041 | A03AF041-00001
|  |  |  | A03AF042 Concrete Work Superstructure Work Expansion Joint (w/ Stainless Steel Cover) | A03AF042-00001 Concrete Work Superstructure Work Expansion Joint (w/ Stainless Steel Cover) w/ Flexible Joint Filler, Sealant, SST Flashing Cover w/ Fixing Accessories | A03AF042 | 00001 | A03AF042-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 042 | Expansion Joint (w/ Stainless Steel Cover) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 09 | w/ Flexible Joint Filler, Sealant, SST Flashing Cover w/ Fixing Accessories |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AF042 | A03AF042-00001
|  |  |  | A03AF043 Concrete Work Superstructure Work Expansion Joint (w/ Ready-Made Cover) | A03AF043-00001 Concrete Work Superstructure Work Expansion Joint (w/ Ready-Made Cover) w/ Flexible Joint Filler, Sealant, Ready-Made Cover Profile w/ Fixing Accessories | A03AF043 | 00001 | A03AF043-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 043 | Expansion Joint (w/ Ready-Made Cover) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 10 | w/ Flexible Joint Filler, Sealant, Ready-Made Cover Profile w/ Fixing Accessories |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AF043 | A03AF043-00001
|  |  |  | A03AF044 Concrete Work Superstructure Work Isolation Joint (Separation Joint) | A03AF044-00001 Concrete Work Superstructure Work Isolation Joint (Separation Joint) w/ Flexible Joint Filler, Sealant | A03AF044 | 00001 | A03AF044-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 044 | Isolation Joint (Separation Joint) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 11 | w/ Flexible Joint Filler, Sealant |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AF044 | A03AF044-00001
|  |  |  | A03AF045 Concrete Work Superstructure Work Control Joint | A03AF045-00001 Concrete Work Superstructure Work Control Joint w/ Joint Sealant, Backstop | A03AF045 | 00001 | A03AF045-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 045 | Control Joint |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 12 | w/ Joint Sealant, Backstop |  | 0 |  | 0 | 0 | Saw Cut: W( )mm x D( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AF045 | A03AF045-00001
|  |  |  | A03AF045 Concrete Work Superstructure Work Control Joint | A03AF045-00002 Concrete Work Superstructure Work Control Joint w/ Joint Sealant, Backstop, Bottom Crack Inducer | A03AF045 | 00002 | A03AF045-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 045 | Control Joint |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 13 | w/ Joint Sealant, Backstop, Bottom Crack Inducer |  | 0 |  | 0 | 0 | Saw Cut: W( )mm x D( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AF045 | A03AF045-00002
|  |  |  | A03AF046 Concrete Work Superstructure Work Water Stop | A03AF046-00001 Concrete Work Superstructure Work Water Stop PVC Type | A03AF046 | 00001 | A03AF046-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 046 | Water Stop | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AF046 | A03AF046-00001
|  |  |  | A03AF046 Concrete Work Superstructure Work Water Stop | A03AF046-00002 Concrete Work Superstructure Work Water Stop Stainless Steel Type | A03AF046 | 00002 | A03AF046-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 046 | Water Stop | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AF046 | A03AF046-00002
|  |  |  | A03AF046 Concrete Work Superstructure Work Water Stop | A03AF046-00003 Concrete Work Superstructure Work Water Stop Expandable Rubber Type | A03AF046 | 00003 | A03AF046-00003 | AR | A03 | Concrete Work | AF | Superstructure Work | 046 | Water Stop | 31 | Expandable Rubber Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AF046 | A03AF046-00003
|  |  |  | A03AF046 Concrete Work Superstructure Work Water Stop | A03AF046-00004 Concrete Work Superstructure Work Water Stop Copper | A03AF046 | 00004 | A03AF046-00004 | AR | A03 | Concrete Work | AF | Superstructure Work | 046 | Water Stop | FS | Copper |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AF046 | A03AF046-00004
|  |  |  | A03AF049 Concrete Work Superstructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | A03AF049-00001 Concrete Work Superstructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) Hot-Dip Galvanized Steel Galv.: ASTM A123 | A03AF049 | 00001 | A03AF049-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 33 | Hot-Dip Galvanized Steel |  | 0 |  | 0 |  | 0 |  | 0 | 14 | Galv.: ASTM A123 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AF049 | A03AF049-00001
|  |  |  | A03AF049 Concrete Work Superstructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | A03AF049-00003 Concrete Work Superstructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) SUS SUS 304 | A03AF049 | 00003 | A03AF049-00003 | AR | A03 | Concrete Work | AF | Superstructure Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 62 | SUS 304 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AF049 | A03AF049-00003
|  |  |  | A03AF049 Concrete Work Superstructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | A03AF049-00004 Concrete Work Superstructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) SUS SUS 316L | A03AF049 | 00004 | A03AF049-00004 | AR | A03 | Concrete Work | AF | Superstructure Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 63 | SUS 316L |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AF049 | A03AF049-00004
|  |  |  | A03AF049 Concrete Work Superstructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | A03AF049-00005 Concrete Work Superstructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) SUS SUS Duplex | A03AF049 | 00005 | A03AF049-00005 | AR | A03 | Concrete Work | AF | Superstructure Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 64 | SUS Duplex |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AF049 | A03AF049-00005
|  |  |  | A03AF050 Concrete Work Superstructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | A03AF050-00001 Concrete Work Superstructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) Hot-Dip Galvanized Steel Galv.: ASTM A123 | A03AF050 | 00001 | A03AF050-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 33 | Hot-Dip Galvanized Steel |  | 0 |  | 0 |  | 0 |  | 0 | 14 | Galv.: ASTM A123 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AF050 | A03AF050-00001
|  |  |  | A03AF050 Concrete Work Superstructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | A03AF050-00003 Concrete Work Superstructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) SUS SUS 304 | A03AF050 | 00003 | A03AF050-00003 | AR | A03 | Concrete Work | AF | Superstructure Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 62 | SUS 304 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AF050 | A03AF050-00003
|  |  |  | A03AF050 Concrete Work Superstructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | A03AF050-00004 Concrete Work Superstructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) SUS SUS 316L | A03AF050 | 00004 | A03AF050-00004 | AR | A03 | Concrete Work | AF | Superstructure Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 63 | SUS 316L |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AF050 | A03AF050-00004
|  |  |  | A03AF050 Concrete Work Superstructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | A03AF050-00005 Concrete Work Superstructure Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) SUS SUS Duplex | A03AF050 | 00005 | A03AF050-00005 | AR | A03 | Concrete Work | AF | Superstructure Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 64 | SUS Duplex |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AF050 | A03AF050-00005
|  |  |  | A03AF051 Concrete Work Superstructure Work Groove Joint | A03AF051-00001 Concrete Work Superstructure Work Groove Joint | A03AF051 | 00001 | A03AF051-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 051 | Groove Joint |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AF051 | A03AF051-00001
|  |  |  | A03AF054 Concrete Work Superstructure Work System Form | A03AF054-00001 Concrete Work Superstructure Work System Form Heavy Duty Forms, Metal Framed Playwood forms Including Form Tie, All Accessories, Sealing of Form Tie Hole, Separator & Anchor Box out, Chamfer for Exposed Edge, Opening & Sleeve, Shoring, Scaffording, Safety Measures and Shop Drawing | A03AF054 | 00001 | A03AF054-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 054 | System Form | 36 | Heavy Duty Forms, Metal Framed Playwood forms |  | 0 |  | 0 |  | 0 |  | 0 | 18 | Including Form Tie, All Accessories, Sealing of Form Tie Hole, Separator & Anchor Box out, Chamfer for Exposed Edge, Opening & Sleeve, Shoring, Scaffording, Safety Measures and Shop Drawing |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF054 | A03AF054-00001
|  |  |  | A03AF055 Concrete Work Superstructure Work System Support | A03AF055-00001 Concrete Work Superstructure Work System Support | A03AF055 | 00001 | A03AF055-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 055 | System Support |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AF055 | A03AF055-00001
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00001 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) M12 | A03AG029 | 00001 | A03AG029-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 37 | M12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00001
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00002 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) M16 | A03AG029 | 00002 | A03AG029-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 38 | M16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00002
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00003 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) M20 | A03AG029 | 00003 | A03AG029-00003 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 39 | M20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00003
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00004 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) M22 | A03AG029 | 00004 | A03AG029-00004 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 40 | M22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00004
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00005 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) M24 | A03AG029 | 00005 | A03AG029-00005 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 41 | M24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00005
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00006 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) M30 | A03AG029 | 00006 | A03AG029-00006 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 42 | M30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00006
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00007 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) M33 | A03AG029 | 00007 | A03AG029-00007 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 43 | M33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00007
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00008 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) M36 | A03AG029 | 00008 | A03AG029-00008 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 44 | M36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00008
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00009 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) M42 | A03AG029 | 00009 | A03AG029-00009 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 45 | M42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00009
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00010 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) M48 | A03AG029 | 00010 | A03AG029-00010 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 46 | M48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00010
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00011 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) M52 | A03AG029 | 00011 | A03AG029-00011 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 47 | M52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00011
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00012 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) M56 | A03AG029 | 00012 | A03AG029-00012 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 48 | M56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00012
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00013 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) M64 | A03AG029 | 00013 | A03AG029-00013 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49 | M64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00013
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00014 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) M72 | A03AG029 | 00014 | A03AG029-00014 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 50 | M72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00014
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00015 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) M76 | A03AG029 | 00015 | A03AG029-00015 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 51 | M76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00015
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00016 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) Over M76 | A03AG029 | 00016 | A03AG029-00016 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 52 | Over M76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00016
|  |  |  | A03AG029 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) | A03AG029-00017 Concrete Work Equipment Foundation Work Anchor Bolt (Installation only) M27 | A03AG029 | 00017 | A03AG029-00017 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | AU | M27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG029 | A03AG029-00017
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00001 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M12 | A03AG329 | 00001 | A03AG329-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 37 | M12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00001
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00002 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M16 | A03AG329 | 00002 | A03AG329-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 38 | M16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00002
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00003 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M20 | A03AG329 | 00003 | A03AG329-00003 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 39 | M20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00003
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00004 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M22 | A03AG329 | 00004 | A03AG329-00004 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 40 | M22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00004
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00005 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M24 | A03AG329 | 00005 | A03AG329-00005 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 41 | M24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00005
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00006 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M27 | A03AG329 | 00006 | A03AG329-00006 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | AU | M27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00006
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00007 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M30 | A03AG329 | 00007 | A03AG329-00007 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 42 | M30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00007
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00008 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M33 | A03AG329 | 00008 | A03AG329-00008 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 43 | M33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00008
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00009 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M36 | A03AG329 | 00009 | A03AG329-00009 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 44 | M36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00009
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00010 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M42 | A03AG329 | 00010 | A03AG329-00010 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 45 | M42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00010
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00011 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M48 | A03AG329 | 00011 | A03AG329-00011 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 46 | M48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00011
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00012 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M52 | A03AG329 | 00012 | A03AG329-00012 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 47 | M52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00012
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00013 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M56 | A03AG329 | 00013 | A03AG329-00013 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 48 | M56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00013
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00014 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M64 | A03AG329 | 00014 | A03AG329-00014 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49 | M64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00014
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00015 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M72 | A03AG329 | 00015 | A03AG329-00015 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 50 | M72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00015
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00016 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) M76 | A03AG329 | 00016 | A03AG329-00016 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 51 | M76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00016
|  |  |  | A03AG329 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) | A03AG329-00017 Concrete Work Equipment Foundation Work Anchor Bolt (Purchase & Installation) Over M76 | A03AG329 | 00017 | A03AG329-00017 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 329 | Anchor Bolt (Purchase & Installation) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 52 | Over M76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG329 | A03AG329-00017
|  |  |  | A03AG030 Concrete Work Equipment Foundation Work Chemical Anchor Bolt | A03AG030-00001 Concrete Work Equipment Foundation Work Chemical Anchor Bolt Including injected Chemical material M10 | A03AG030 | 00001 | A03AG030-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 36 | M10 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG030 | A03AG030-00001
|  |  |  | A03AG030 Concrete Work Equipment Foundation Work Chemical Anchor Bolt | A03AG030-00002 Concrete Work Equipment Foundation Work Chemical Anchor Bolt Including injected Chemical material M12 | A03AG030 | 00002 | A03AG030-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 37 | M12 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG030 | A03AG030-00002
|  |  |  | A03AG030 Concrete Work Equipment Foundation Work Chemical Anchor Bolt | A03AG030-00003 Concrete Work Equipment Foundation Work Chemical Anchor Bolt Including injected Chemical material M16 | A03AG030 | 00003 | A03AG030-00003 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 38 | M16 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG030 | A03AG030-00003
|  |  |  | A03AG030 Concrete Work Equipment Foundation Work Chemical Anchor Bolt | A03AG030-00004 Concrete Work Equipment Foundation Work Chemical Anchor Bolt Including injected Chemical material M20 | A03AG030 | 00004 | A03AG030-00004 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 39 | M20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG030 | A03AG030-00004
|  |  |  | A03AG030 Concrete Work Equipment Foundation Work Chemical Anchor Bolt | A03AG030-00005 Concrete Work Equipment Foundation Work Chemical Anchor Bolt Including injected Chemical material M22 | A03AG030 | 00005 | A03AG030-00005 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 40 | M22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG030 | A03AG030-00005
|  |  |  | A03AG030 Concrete Work Equipment Foundation Work Chemical Anchor Bolt | A03AG030-00006 Concrete Work Equipment Foundation Work Chemical Anchor Bolt Including injected Chemical material M24 | A03AG030 | 00006 | A03AG030-00006 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 030 | Chemical Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 04 | Including injected Chemical material |  | 0 | 41 | M24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG030 | A03AG030-00006
|  |  |  | A03AG031 Concrete Work Equipment Foundation Work Expansion Anchor Bolt | A03AG031-00001 Concrete Work Equipment Foundation Work Expansion Anchor Bolt M10 | A03AG031 | 00001 | A03AG031-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | M10 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG031 | A03AG031-00001
|  |  |  | A03AG031 Concrete Work Equipment Foundation Work Expansion Anchor Bolt | A03AG031-00002 Concrete Work Equipment Foundation Work Expansion Anchor Bolt M12 | A03AG031 | 00002 | A03AG031-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 37 | M12 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG031 | A03AG031-00002
|  |  |  | A03AG031 Concrete Work Equipment Foundation Work Expansion Anchor Bolt | A03AG031-00003 Concrete Work Equipment Foundation Work Expansion Anchor Bolt M16 | A03AG031 | 00003 | A03AG031-00003 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 38 | M16 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG031 | A03AG031-00003
|  |  |  | A03AG031 Concrete Work Equipment Foundation Work Expansion Anchor Bolt | A03AG031-00004 Concrete Work Equipment Foundation Work Expansion Anchor Bolt M20 | A03AG031 | 00004 | A03AG031-00004 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 39 | M20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG031 | A03AG031-00004
|  |  |  | A03AG031 Concrete Work Equipment Foundation Work Expansion Anchor Bolt | A03AG031-00005 Concrete Work Equipment Foundation Work Expansion Anchor Bolt M22 | A03AG031 | 00005 | A03AG031-00005 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 40 | M22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG031 | A03AG031-00005
|  |  |  | A03AG031 Concrete Work Equipment Foundation Work Expansion Anchor Bolt | A03AG031-00006 Concrete Work Equipment Foundation Work Expansion Anchor Bolt M24 | A03AG031 | 00006 | A03AG031-00006 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 031 | Expansion Anchor Bolt |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 41 | M24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A03AG031 | A03AG031-00006
|  |  |  | A03AG032 Concrete Work Equipment Foundation Work Structural Concrete | A03AG032-00016 Concrete Work Equipment Foundation Work Structural Concrete Cement Type-1 35MPa ≤ F'c (Cylinder Strength) | A03AG032 | 00016 | A03AG032-00016 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 13 | 35MPa ≤ F'c (Cylinder Strength) |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG032 | A03AG032-00016
|  |  |  | A03AG032 Concrete Work Equipment Foundation Work Structural Concrete | A03AG032-00017 Concrete Work Equipment Foundation Work Structural Concrete Cement Type-2 35MPa ≤ F'c (Cylinder Strength) | A03AG032 | 00017 | A03AG032-00017 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 13 | 35MPa ≤ F'c (Cylinder Strength) |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG032 | A03AG032-00017
|  |  |  | A03AG032 Concrete Work Equipment Foundation Work Structural Concrete | A03AG032-00018 Concrete Work Equipment Foundation Work Structural Concrete Cement Type-5 35MPa ≤ F'c (Cylinder Strength) | A03AG032 | 00018 | A03AG032-00018 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 13 | 35MPa ≤ F'c (Cylinder Strength) |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG032 | A03AG032-00018
|  |  |  | A03AG032 Concrete Work Equipment Foundation Work Structural Concrete | A03AG032-00019 Concrete Work Equipment Foundation Work Structural Concrete Cement Type-1 30MPa ≤ F'c (Cylinder Strength) < 35MPa | A03AG032 | 00019 | A03AG032-00019 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 14 | 30MPa ≤ F'c (Cylinder Strength) < 35MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG032 | A03AG032-00019
|  |  |  | A03AG032 Concrete Work Equipment Foundation Work Structural Concrete | A03AG032-00020 Concrete Work Equipment Foundation Work Structural Concrete Cement Type-2 30MPa ≤ F'c (Cylinder Strength) < 35MPa | A03AG032 | 00020 | A03AG032-00020 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 14 | 30MPa ≤ F'c (Cylinder Strength) < 35MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG032 | A03AG032-00020
|  |  |  | A03AG032 Concrete Work Equipment Foundation Work Structural Concrete | A03AG032-00021 Concrete Work Equipment Foundation Work Structural Concrete Cement Type-5 30MPa ≤ F'c (Cylinder Strength) < 35MPa | A03AG032 | 00021 | A03AG032-00021 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 14 | 30MPa ≤ F'c (Cylinder Strength) < 35MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG032 | A03AG032-00021
|  |  |  | A03AG032 Concrete Work Equipment Foundation Work Structural Concrete | A03AG032-00022 Concrete Work Equipment Foundation Work Structural Concrete Cement Type-1 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AG032 | 00022 | A03AG032-00022 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 15 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG032 | A03AG032-00022
|  |  |  | A03AG032 Concrete Work Equipment Foundation Work Structural Concrete | A03AG032-00023 Concrete Work Equipment Foundation Work Structural Concrete Cement Type-2 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AG032 | 00023 | A03AG032-00023 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 15 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG032 | A03AG032-00023
|  |  |  | A03AG032 Concrete Work Equipment Foundation Work Structural Concrete | A03AG032-00024 Concrete Work Equipment Foundation Work Structural Concrete Cement Type-5 25MPa ≤ F'c (Cylinder Strength) < 30MPa | A03AG032 | 00024 | A03AG032-00024 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 15 | 25MPa ≤ F'c (Cylinder Strength) < 30MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG032 | A03AG032-00024
|  |  |  | A03AG032 Concrete Work Equipment Foundation Work Structural Concrete | A03AG032-00025 Concrete Work Equipment Foundation Work Structural Concrete Cement Type-1 20MPa ≤ F'c (Cylinder Strength) < 25MPa | A03AG032 | 00025 | A03AG032-00025 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 16 | 20MPa ≤ F'c (Cylinder Strength) < 25MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG032 | A03AG032-00025
|  |  |  | A03AG032 Concrete Work Equipment Foundation Work Structural Concrete | A03AG032-00026 Concrete Work Equipment Foundation Work Structural Concrete Cement Type-2 20MPa ≤ F'c (Cylinder Strength) < 25MPa | A03AG032 | 00026 | A03AG032-00026 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 16 | 20MPa ≤ F'c (Cylinder Strength) < 25MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG032 | A03AG032-00026
|  |  |  | A03AG032 Concrete Work Equipment Foundation Work Structural Concrete | A03AG032-00027 Concrete Work Equipment Foundation Work Structural Concrete Cement Type-5 20MPa ≤ F'c (Cylinder Strength) < 25MPa | A03AG032 | 00027 | A03AG032-00027 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 16 | 20MPa ≤ F'c (Cylinder Strength) < 25MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG032 | A03AG032-00027
|  |  |  | A03AG032 Concrete Work Equipment Foundation Work Structural Concrete | A03AG032-00028 Concrete Work Equipment Foundation Work Structural Concrete Cement Type-1 F'c (Cylinder Strength) < 20MPa | A03AG032 | 00028 | A03AG032-00028 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  | 0 | 01 | Cement Type-1 | 17 | F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG032 | A03AG032-00028
|  |  |  | A03AG032 Concrete Work Equipment Foundation Work Structural Concrete | A03AG032-00029 Concrete Work Equipment Foundation Work Structural Concrete Cement Type-2 F'c (Cylinder Strength) < 20MPa | A03AG032 | 00029 | A03AG032-00029 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  | 0 | 02 | Cement Type-2 | 17 | F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG032 | A03AG032-00029
|  |  |  | A03AG032 Concrete Work Equipment Foundation Work Structural Concrete | A03AG032-00030 Concrete Work Equipment Foundation Work Structural Concrete Cement Type-5 F'c (Cylinder Strength) < 20MPa | A03AG032 | 00030 | A03AG032-00030 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  | 0 | 03 | Cement Type-5 | 17 | F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG032 | A03AG032-00030
|  |  |  | A03AG034 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) | A03AG034-00010 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) Cement Type-1 15MPa ≤ F'c (Cylinder Strength) < 20MPa | A03AG034 | 00010 | A03AG034-00010 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  | 0 | 01 | Cement Type-1 | 18 | 15MPa ≤ F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG034 | A03AG034-00010
|  |  |  | A03AG034 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) | A03AG034-00011 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) Cement Type-2 15MPa ≤ F'c (Cylinder Strength) < 20MPa | A03AG034 | 00011 | A03AG034-00011 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  | 0 | 02 | Cement Type-2 | 18 | 15MPa ≤ F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG034 | A03AG034-00011
|  |  |  | A03AG034 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) | A03AG034-00012 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) Cement Type-5 15MPa ≤ F'c (Cylinder Strength) < 20MPa | A03AG034 | 00012 | A03AG034-00012 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  | 0 | 03 | Cement Type-5 | 18 | 15MPa ≤ F'c (Cylinder Strength) < 20MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG034 | A03AG034-00012
|  |  |  | A03AG034 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) | A03AG034-00013 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) Cement Type-1 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AG034 | 00013 | A03AG034-00013 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  | 0 | 01 | Cement Type-1 | 19 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG034 | A03AG034-00013
|  |  |  | A03AG034 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) | A03AG034-00014 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) Cement Type-2 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AG034 | 00014 | A03AG034-00014 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  | 0 | 02 | Cement Type-2 | 19 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG034 | A03AG034-00014
|  |  |  | A03AG034 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) | A03AG034-00015 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) Cement Type-5 10MPa ≤ F'c (Cylinder Strength) < 15MPa | A03AG034 | 00015 | A03AG034-00015 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  | 0 | 03 | Cement Type-5 | 19 | 10MPa ≤ F'c (Cylinder Strength) < 15MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG034 | A03AG034-00015
|  |  |  | A03AG034 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) | A03AG034-00016 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) Cement Type-1 F'c (Cylinder Strength) < 10MPa | A03AG034 | 00016 | A03AG034-00016 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  | 0 | 01 | Cement Type-1 | 20 | F'c (Cylinder Strength) < 10MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG034 | A03AG034-00016
|  |  |  | A03AG034 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) | A03AG034-00017 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) Cement Type-2 F'c (Cylinder Strength) < 10MPa | A03AG034 | 00017 | A03AG034-00017 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  | 0 | 02 | Cement Type-2 | 20 | F'c (Cylinder Strength) < 10MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG034 | A03AG034-00017
|  |  |  | A03AG034 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) | A03AG034-00018 Concrete Work Equipment Foundation Work Lean Concrete (including Form work) Cement Type-5 F'c (Cylinder Strength) < 10MPa | A03AG034 | 00018 | A03AG034-00018 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  | 0 | 03 | Cement Type-5 | 20 | F'c (Cylinder Strength) < 10MPa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG034 | A03AG034-00018
|  |  |  | A03AG035 Concrete Work Equipment Foundation Work Form Work (3 times in use) | A03AG035-00001 Concrete Work Equipment Foundation Work Form Work (3 times in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AG035 | 00001 | A03AG035-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 035 | Form Work (3 times in use) | 25 | Flat Form |  | 0 |  | 0 |  | 0 |  | 0 | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AG035 | A03AG035-00001
|  |  |  | A03AG035 Concrete Work Equipment Foundation Work Form Work (3 times in use) | A03AG035-00002 Concrete Work Equipment Foundation Work Form Work (3 times in use) Circular Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AG035 | 00002 | A03AG035-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 035 | Form Work (3 times in use) | 26 | Circular Form |  | 0 |  | 0 |  | 0 |  | 0 | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AG035 | A03AG035-00002
|  |  |  | A03AG036 Concrete Work Equipment Foundation Work Form Work (1 time in use) | A03AG036-00001 Concrete Work Equipment Foundation Work Form Work (1 time in use) Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AG036 | 00001 | A03AG036-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 036 | Form Work (1 time in use) | 25 | Flat Form |  | 0 |  | 0 |  | 0 |  | 0 | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AG036 | A03AG036-00001
|  |  |  | A03AG036 Concrete Work Equipment Foundation Work Form Work (1 time in use) | A03AG036-00002 Concrete Work Equipment Foundation Work Form Work (1 time in use) Circular Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | A03AG036 | 00002 | A03AG036-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 036 | Form Work (1 time in use) | 26 | Circular Form |  | 0 |  | 0 |  | 0 |  | 0 | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AG036 | A03AG036-00002
|  |  |  | A03AG037 Concrete Work Equipment Foundation Work Rebar Work | A03AG037-00001 Concrete Work Equipment Foundation Work Rebar Work Deformed Bar (Non-Coat.) Fy>470MPa | A03AG037 | 00001 | A03AG037-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  | 0 | 09 | Fy>470MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AG037 | A03AG037-00001
|  |  |  | A03AG037 Concrete Work Equipment Foundation Work Rebar Work | A03AG037-00002 Concrete Work Equipment Foundation Work Rebar Work Deformed Bar (Non-Coat.) 400MPa<Fy≤470MPa | A03AG037 | 00002 | A03AG037-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  | 0 | 10 | 400MPa<Fy≤470MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AG037 | A03AG037-00002
|  |  |  | A03AG037 Concrete Work Equipment Foundation Work Rebar Work | A03AG037-00003 Concrete Work Equipment Foundation Work Rebar Work Deformed Bar (Non-Coat.) 300MPa<Fy≤400MPa | A03AG037 | 00003 | A03AG037-00003 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  | 0 | 11 | 300MPa<Fy≤400MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AG037 | A03AG037-00003
|  |  |  | A03AG037 Concrete Work Equipment Foundation Work Rebar Work | A03AG037-00004 Concrete Work Equipment Foundation Work Rebar Work Deformed Bar (Non-Coat.) Fy≤300MPa | A03AG037 | 00004 | A03AG037-00004 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  | 0 | 12 | Fy≤300MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AG037 | A03AG037-00004
|  |  |  | A03AG037 Concrete Work Equipment Foundation Work Rebar Work | A03AG037-00005 Concrete Work Equipment Foundation Work Rebar Work Deformed Bar (Epoxy Coat.) Fy>470MPa | A03AG037 | 00005 | A03AG037-00005 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  | 0 | 09 | Fy>470MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AG037 | A03AG037-00005
|  |  |  | A03AG037 Concrete Work Equipment Foundation Work Rebar Work | A03AG037-00006 Concrete Work Equipment Foundation Work Rebar Work Deformed Bar (Epoxy Coat.) 400MPa<Fy≤470MPa | A03AG037 | 00006 | A03AG037-00006 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  | 0 | 10 | 400MPa<Fy≤470MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AG037 | A03AG037-00006
|  |  |  | A03AG037 Concrete Work Equipment Foundation Work Rebar Work | A03AG037-00007 Concrete Work Equipment Foundation Work Rebar Work Deformed Bar (Epoxy Coat.) 300MPa<Fy≤400MPa | A03AG037 | 00007 | A03AG037-00007 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  | 0 | 11 | 300MPa<Fy≤400MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AG037 | A03AG037-00007
|  |  |  | A03AG037 Concrete Work Equipment Foundation Work Rebar Work | A03AG037-00008 Concrete Work Equipment Foundation Work Rebar Work Deformed Bar (Epoxy Coat.) Fy≤300MPa | A03AG037 | 00008 | A03AG037-00008 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  | 0 | 12 | Fy≤300MPa |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AG037 | A03AG037-00008
|  |  |  | A03AG046 Concrete Work Equipment Foundation Work Water Stop | A03AG046-00001 Concrete Work Equipment Foundation Work Water Stop PVC Type | A03AG046 | 00001 | A03AG046-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 046 | Water Stop | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AG046 | A03AG046-00001
|  |  |  | A03AG046 Concrete Work Equipment Foundation Work Water Stop | A03AG046-00002 Concrete Work Equipment Foundation Work Water Stop Stainless Steel Type | A03AG046 | 00002 | A03AG046-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 046 | Water Stop | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AG046 | A03AG046-00002
|  |  |  | A03AG046 Concrete Work Equipment Foundation Work Water Stop | A03AG046-00003 Concrete Work Equipment Foundation Work Water Stop Expandable Rubber Type | A03AG046 | 00003 | A03AG046-00003 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 046 | Water Stop | 31 | Expandable Rubber Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AG046 | A03AG046-00003
|  |  |  | A03AG046 Concrete Work Equipment Foundation Work Water Stop | A03AG046-00004 Concrete Work Equipment Foundation Work Water Stop Copper | A03AG046 | 00004 | A03AG046-00004 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 046 | Water Stop | FS | Copper |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A03AG046 | A03AG046-00004
|  |  |  | A03AG049 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | A03AG049-00001 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) Hot-Dip Galvanized Steel Galv.: ASTM A123 | A03AG049 | 00001 | A03AG049-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 33 | Hot-Dip Galvanized Steel |  | 0 |  | 0 |  | 0 |  | 0 | 14 | Galv.: ASTM A123 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AG049 | A03AG049-00001
|  |  |  | A03AG049 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | A03AG049-00003 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) SUS SUS 304 | A03AG049 | 00003 | A03AG049-00003 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 62 | SUS 304 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AG049 | A03AG049-00003
|  |  |  | A03AG049 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | A03AG049-00004 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) SUS SUS 316L | A03AG049 | 00004 | A03AG049-00004 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 63 | SUS 316L |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AG049 | A03AG049-00004
|  |  |  | A03AG049 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | A03AG049-00005 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) SUS SUS Duplex | A03AG049 | 00005 | A03AG049-00005 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 64 | SUS Duplex |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AG049 | A03AG049-00005
|  |  |  | A03AG050 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | A03AG050-00001 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) Hot-Dip Galvanized Steel Galv.: ASTM A123 | A03AG050 | 00001 | A03AG050-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 33 | Hot-Dip Galvanized Steel |  | 0 |  | 0 |  | 0 |  | 0 | 14 | Galv.: ASTM A123 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AG050 | A03AG050-00001
|  |  |  | A03AG050 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | A03AG050-00003 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) SUS SUS 304 | A03AG050 | 00003 | A03AG050-00003 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 62 | SUS 304 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AG050 | A03AG050-00003
|  |  |  | A03AG050 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | A03AG050-00004 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) SUS SUS 316L | A03AG050 | 00004 | A03AG050-00004 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 63 | SUS 316L |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AG050 | A03AG050-00004
|  |  |  | A03AG050 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | A03AG050-00005 Concrete Work Equipment Foundation Work Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) SUS SUS Duplex | A03AG050 | 00005 | A03AG050-00005 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 34 | SUS |  | 0 |  | 0 |  | 0 |  | 0 | 64 | SUS Duplex |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | TON | TON | A03AG050 | A03AG050-00005
|  |  |  | A03AG054 Concrete Work Equipment Foundation Work System Form | A03AG054-00001 Concrete Work Equipment Foundation Work System Form Heavy Duty Forms, Metal Framed Playwood forms Including Form Tie, All Accessories, Sealing of Form Tie Hole, Separator & Anchor Box out, Chamfer for Exposed Edge, Opening & Sleeve, Shoring, Scaffording, Safety Measures and Shop Drawing | A03AG054 | 00001 | A03AG054-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 054 | System Form | 36 | Heavy Duty Forms, Metal Framed Playwood forms |  | 0 |  | 0 |  | 0 |  | 0 | 18 | Including Form Tie, All Accessories, Sealing of Form Tie Hole, Separator & Anchor Box out, Chamfer for Exposed Edge, Opening & Sleeve, Shoring, Scaffording, Safety Measures and Shop Drawing |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG054 | A03AG054-00001
|  |  |  | A03AG055 Concrete Work Equipment Foundation Work System Support | A03AG055-00001 Concrete Work Equipment Foundation Work System Support | A03AG055 | 00001 | A03AG055-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 055 | System Support |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AG055 | A03AG055-00001
|  |  |  | A03AH056 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056-00001 Concrete Work Concrete Protective Coating (U/G) Bitumen/Bituminous/Asphalt Coating | A03AH056 | 00001 | A03AH056-00001 | AR | A03 | Concrete Work | AH | Concrete Protective Coating (U/G) | 056 | Bitumen/Bituminous/Asphalt Coating |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AH056 | A03AH056-00001
|  |  |  | A03AH057 Concrete Work Concrete Protective Coating (U/G) Coal Tar Epoxy | A03AH057-00001 Concrete Work Concrete Protective Coating (U/G) Coal Tar Epoxy | A03AH057 | 00001 | A03AH057-00001 | AR | A03 | Concrete Work | AH | Concrete Protective Coating (U/G) | 057 | Coal Tar Epoxy |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AH057 | A03AH057-00001
|  |  |  | A03AH058 Concrete Work Concrete Protective Coating (U/G) Epoxy Coating (Epoxy Resin Based Coating) | A03AH058-00001 Concrete Work Concrete Protective Coating (U/G) Epoxy Coating (Epoxy Resin Based Coating) | A03AH058 | 00001 | A03AH058-00001 | AR | A03 | Concrete Work | AH | Concrete Protective Coating (U/G) | 058 | Epoxy Coating (Epoxy Resin Based Coating) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AH058 | A03AH058-00001
|  |  |  | A03AH059 Concrete Work Concrete Protective Coating (U/G) Sheet Membrane | A03AH059-00001 Concrete Work Concrete Protective Coating (U/G) Sheet Membrane Adhesive Rubber Sheet or Bitumen Polyethylene Laminated Waterproofing Membrane | A03AH059 | 00001 | A03AH059-00001 | AR | A03 | Concrete Work | AH | Concrete Protective Coating (U/G) | 059 | Sheet Membrane | 37 | Adhesive Rubber Sheet or Bitumen Polyethylene Laminated Waterproofing Membrane |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AH059 | A03AH059-00001
|  |  |  | A03AH060 Concrete Work Concrete Protective Coating (U/G) Memebrane Protection Board | A03AH060-00001 Concrete Work Concrete Protective Coating (U/G) Memebrane Protection Board Bitumen Impregnated Fiberboard | A03AH060 | 00001 | A03AH060-00001 | AR | A03 | Concrete Work | AH | Concrete Protective Coating (U/G) | 060 | Memebrane Protection Board | 38 | Bitumen Impregnated Fiberboard |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AH060 | A03AH060-00001
|  |  |  | A03AH060 Concrete Work Concrete Protective Coating (U/G) Memebrane Protection Board | A03AH060-00002 Concrete Work Concrete Protective Coating (U/G) Memebrane Protection Board Bitumen Impregnated Softboard | A03AH060 | 00002 | A03AH060-00002 | AR | A03 | Concrete Work | AH | Concrete Protective Coating (U/G) | 060 | Memebrane Protection Board | 39 | Bitumen Impregnated Softboard |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AH060 | A03AH060-00002
|  |  |  | A03AH061 Concrete Work Concrete Protective Coating (U/G) Protective Screed | A03AH061-00001 Concrete Work Concrete Protective Coating (U/G) Protective Screed | A03AH061 | 00001 | A03AH061-00001 | AR | A03 | Concrete Work | AH | Concrete Protective Coating (U/G) | 061 | Protective Screed |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AH061 | A03AH061-00001
|  |  |  | A03AJ058 Concrete Work Concrete Protective Coating (A/G) Epoxy Coating (Epoxy Resin Based Coating) | A03AJ058-00001 Concrete Work Concrete Protective Coating (A/G) Epoxy Coating (Epoxy Resin Based Coating) | A03AJ058 | 00001 | A03AJ058-00001 | AR | A03 | Concrete Work | AJ | Concrete Protective Coating (A/G) | 058 | Epoxy Coating (Epoxy Resin Based Coating) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AJ058 | A03AJ058-00001
|  |  |  | A03AJ062 Concrete Work Concrete Protective Coating (A/G) Acrylic Polymer Coating | A03AJ062-00001 Concrete Work Concrete Protective Coating (A/G) Acrylic Polymer Coating | A03AJ062 | 00001 | A03AJ062-00001 | AR | A03 | Concrete Work | AJ | Concrete Protective Coating (A/G) | 062 | Acrylic Polymer Coating |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AJ062 | A03AJ062-00001
|  |  |  | A03AJ063 Concrete Work Concrete Protective Coating (A/G) Bituminous Damp Proofing | A03AJ063-00001 Concrete Work Concrete Protective Coating (A/G) Bituminous Damp Proofing for External Conc. Wall behind Panel (Granite, Marble, Aluminum Panel, ETC.) | A03AJ063 | 00001 | A03AJ063-00001 | AR | A03 | Concrete Work | AJ | Concrete Protective Coating (A/G) | 063 | Bituminous Damp Proofing |  | 0 |  | 0 |  | 0 |  | 0 | 01 | for External Conc. Wall behind Panel (Granite, Marble, Aluminum Panel, ETC.) |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A03AJ063 | A03AJ063-00001
|  |  |  | A03AK064 Concrete Work Precast Concrete Work PC Slab/Roof Panel | A03AK064-00001 Concrete Work Precast Concrete Work PC Slab/Roof Panel Hollow Core Slab Including Supply and Install Work w/ All Items to Complete the Work 100mm<THK≤120mm | A03AK064 | 00001 | A03AK064-00001 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Slab/Roof Panel | 40 | Hollow Core Slab |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 12 | 100mm<THK≤120mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK064 | A03AK064-00001
|  |  |  | A03AK064 Concrete Work Precast Concrete Work PC Slab/Roof Panel | A03AK064-00002 Concrete Work Precast Concrete Work PC Slab/Roof Panel Hollow Core Slab Including Supply and Install Work w/ All Items to Complete the Work 120mm<THK≤150mm | A03AK064 | 00002 | A03AK064-00002 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Slab/Roof Panel | 40 | Hollow Core Slab |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 13 | 120mm<THK≤150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK064 | A03AK064-00002
|  |  |  | A03AK064 Concrete Work Precast Concrete Work PC Slab/Roof Panel | A03AK064-00003 Concrete Work Precast Concrete Work PC Slab/Roof Panel Hollow Core Slab Including Supply and Install Work w/ All Items to Complete the Work 150mm<THK≤200mm | A03AK064 | 00003 | A03AK064-00003 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Slab/Roof Panel | 40 | Hollow Core Slab |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 02 | 150mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK064 | A03AK064-00003
|  |  |  | A03AK064 Concrete Work Precast Concrete Work PC Slab/Roof Panel | A03AK064-00004 Concrete Work Precast Concrete Work PC Slab/Roof Panel Hollow Core Slab Including Supply and Install Work w/ All Items to Complete the Work 200mm<THK | A03AK064 | 00004 | A03AK064-00004 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Slab/Roof Panel | 40 | Hollow Core Slab |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 14 | 200mm<THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK064 | A03AK064-00004
|  |  |  | A03AK064 Concrete Work Precast Concrete Work PC Slab/Roof Panel | A03AK064-00005 Concrete Work Precast Concrete Work PC Slab/Roof Panel Single Tee Slab Including Supply and Install Work w/ All Items to Complete the Work 100mm<THK≤120mm | A03AK064 | 00005 | A03AK064-00005 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Slab/Roof Panel | 41 | Single Tee Slab |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 12 | 100mm<THK≤120mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK064 | A03AK064-00005
|  |  |  | A03AK064 Concrete Work Precast Concrete Work PC Slab/Roof Panel | A03AK064-00006 Concrete Work Precast Concrete Work PC Slab/Roof Panel Single Tee Slab Including Supply and Install Work w/ All Items to Complete the Work 120mm<THK≤150mm | A03AK064 | 00006 | A03AK064-00006 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Slab/Roof Panel | 41 | Single Tee Slab |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 13 | 120mm<THK≤150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK064 | A03AK064-00006
|  |  |  | A03AK064 Concrete Work Precast Concrete Work PC Slab/Roof Panel | A03AK064-00007 Concrete Work Precast Concrete Work PC Slab/Roof Panel Single Tee Slab Including Supply and Install Work w/ All Items to Complete the Work 150mm<THK≤200mm | A03AK064 | 00007 | A03AK064-00007 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Slab/Roof Panel | 41 | Single Tee Slab |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 02 | 150mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK064 | A03AK064-00007
|  |  |  | A03AK064 Concrete Work Precast Concrete Work PC Slab/Roof Panel | A03AK064-00008 Concrete Work Precast Concrete Work PC Slab/Roof Panel Single Tee Slab Including Supply and Install Work w/ All Items to Complete the Work 200mm<THK | A03AK064 | 00008 | A03AK064-00008 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Slab/Roof Panel | 41 | Single Tee Slab |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 14 | 200mm<THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK064 | A03AK064-00008
|  |  |  | A03AK064 Concrete Work Precast Concrete Work PC Slab/Roof Panel | A03AK064-00009 Concrete Work Precast Concrete Work PC Slab/Roof Panel Doube Tee Slab Including Supply and Install Work w/ All Items to Complete the Work 100mm<THK≤120mm | A03AK064 | 00009 | A03AK064-00009 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Slab/Roof Panel | 42 | Doube Tee Slab |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 12 | 100mm<THK≤120mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK064 | A03AK064-00009
|  |  |  | A03AK064 Concrete Work Precast Concrete Work PC Slab/Roof Panel | A03AK064-00010 Concrete Work Precast Concrete Work PC Slab/Roof Panel Doube Tee Slab Including Supply and Install Work w/ All Items to Complete the Work 120mm<THK≤150mm | A03AK064 | 00010 | A03AK064-00010 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Slab/Roof Panel | 42 | Doube Tee Slab |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 13 | 120mm<THK≤150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK064 | A03AK064-00010
|  |  |  | A03AK064 Concrete Work Precast Concrete Work PC Slab/Roof Panel | A03AK064-00011 Concrete Work Precast Concrete Work PC Slab/Roof Panel Doube Tee Slab Including Supply and Install Work w/ All Items to Complete the Work 150mm<THK≤200mm | A03AK064 | 00011 | A03AK064-00011 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Slab/Roof Panel | 42 | Doube Tee Slab |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 02 | 150mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK064 | A03AK064-00011
|  |  |  | A03AK064 Concrete Work Precast Concrete Work PC Slab/Roof Panel | A03AK064-00012 Concrete Work Precast Concrete Work PC Slab/Roof Panel Doube Tee Slab Including Supply and Install Work w/ All Items to Complete the Work 200mm<THK | A03AK064 | 00012 | A03AK064-00012 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Slab/Roof Panel | 42 | Doube Tee Slab |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 14 | 200mm<THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK064 | A03AK064-00012
|  |  |  | A03AK065 Concrete Work Precast Concrete Work PC Wall Panel | A03AK065-00001 Concrete Work Precast Concrete Work PC Wall Panel Including Supply and Install Work w/ All Items to Complete the Work 150mm<THK≤200mm | A03AK065 | 00001 | A03AK065-00001 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 065 | PC Wall Panel |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 02 | 150mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK065 | A03AK065-00001
|  |  |  | A03AK065 Concrete Work Precast Concrete Work PC Wall Panel | A03AK065-00002 Concrete Work Precast Concrete Work PC Wall Panel Including Supply and Install Work w/ All Items to Complete the Work 200mm<THK≤250mm | A03AK065 | 00002 | A03AK065-00002 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 065 | PC Wall Panel |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 03 | 200mm<THK≤250mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK065 | A03AK065-00002
|  |  |  | A03AK065 Concrete Work Precast Concrete Work PC Wall Panel | A03AK065-00003 Concrete Work Precast Concrete Work PC Wall Panel Including Supply and Install Work w/ All Items to Complete the Work 250mm<THK≤300mm | A03AK065 | 00003 | A03AK065-00003 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 065 | PC Wall Panel |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 04 | 250mm<THK≤300mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK065 | A03AK065-00003
|  |  |  | A03AK065 Concrete Work Precast Concrete Work PC Wall Panel | A03AK065-00004 Concrete Work Precast Concrete Work PC Wall Panel Including Supply and Install Work w/ All Items to Complete the Work 300mm<THK≤350mm | A03AK065 | 00004 | A03AK065-00004 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 065 | PC Wall Panel |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 05 | 300mm<THK≤350mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK065 | A03AK065-00004
|  |  |  | A03AK065 Concrete Work Precast Concrete Work PC Wall Panel | A03AK065-00005 Concrete Work Precast Concrete Work PC Wall Panel Including Supply and Install Work w/ All Items to Complete the Work 350mm<THK≤400mm | A03AK065 | 00005 | A03AK065-00005 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 065 | PC Wall Panel |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 15 | 350mm<THK≤400mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK065 | A03AK065-00005
|  |  |  | A03AK065 Concrete Work Precast Concrete Work PC Wall Panel | A03AK065-00006 Concrete Work Precast Concrete Work PC Wall Panel Including Supply and Install Work w/ All Items to Complete the Work 400mm<THK≤450mm | A03AK065 | 00006 | A03AK065-00006 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 065 | PC Wall Panel |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 | 16 | 400mm<THK≤450mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK065 | A03AK065-00006
|  |  |  | A03AK066 Concrete Work Precast Concrete Work PC Column | A03AK066-00001 Concrete Work Precast Concrete Work PC Column Including Supply and Install Work w/ All Items to Complete the Work | A03AK066 | 00001 | A03AK066-00001 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 066 | PC Column |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 |  | 0 | 0 | W( )mm x L( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK066 | A03AK066-00001
|  |  |  | A03AK067 Concrete Work Precast Concrete Work PC Girder & Beam | A03AK067-00001 Concrete Work Precast Concrete Work PC Girder & Beam Including Supply and Install Work w/ All Items to Complete the Work | A03AK067 | 00001 | A03AK067-00001 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 067 | PC Girder & Beam |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 |  | 0 | 0 | W( )mm x H( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK067 | A03AK067-00001
|  |  |  | A03AK068 Concrete Work Precast Concrete Work PC Cover | A03AK068-00001 Concrete Work Precast Concrete Work PC Cover Including Supply and Install Work w/ All Items to Complete the Work | A03AK068 | 00001 | A03AK068-00001 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 068 | PC Cover |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  | 0 |  | 0 | 0 | W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A03AK068 | A03AK068-00001
|  |  |  | A04AL012 Finishing Work Masonry Work PE Sheet (Vapor Barrier) | A04AL012-00001 Finishing Work Masonry Work PE Sheet (Vapor Barrier) | A04AL012 | 00001 | A04AL012-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 012 | PE Sheet (Vapor Barrier) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL012 | A04AL012-00001
|  |  |  | A04AL069 Finishing Work Masonry Work Reinforced Concrete Block | A04AL069-00001 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 50mm<THK≤100mm | A04AL069 | 00001 | A04AL069-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 069 | Reinforced Concrete Block |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 17 | 50mm<THK≤100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL069 | A04AL069-00001
|  |  |  | A04AL069 Finishing Work Masonry Work Reinforced Concrete Block | A04AL069-00002 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 100mm<THK≤200mm | A04AL069 | 00002 | A04AL069-00002 | AR | A04 | Finishing Work | AL | Masonry Work | 069 | Reinforced Concrete Block |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 18 | 100mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL069 | A04AL069-00002
|  |  |  | A04AL069 Finishing Work Masonry Work Reinforced Concrete Block | A04AL069-00003 Finishing Work Masonry Work Reinforced Concrete Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 200mm<THK | A04AL069 | 00003 | A04AL069-00003 | AR | A04 | Finishing Work | AL | Masonry Work | 069 | Reinforced Concrete Block |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 14 | 200mm<THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL069 | A04AL069-00003
|  |  |  | A04AL070 Finishing Work Masonry Work AAC (Autoclaved Aerated Concrete) Block | A04AL070-00001 Finishing Work Masonry Work AAC (Autoclaved Aerated Concrete) Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 50mm<THK≤100mm | A04AL070 | 00001 | A04AL070-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 070 | AAC (Autoclaved Aerated Concrete) Block |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 17 | 50mm<THK≤100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL070 | A04AL070-00001
|  |  |  | A04AL070 Finishing Work Masonry Work AAC (Autoclaved Aerated Concrete) Block | A04AL070-00002 Finishing Work Masonry Work AAC (Autoclaved Aerated Concrete) Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 100mm<THK≤200mm | A04AL070 | 00002 | A04AL070-00002 | AR | A04 | Finishing Work | AL | Masonry Work | 070 | AAC (Autoclaved Aerated Concrete) Block |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 18 | 100mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL070 | A04AL070-00002
|  |  |  | A04AL070 Finishing Work Masonry Work AAC (Autoclaved Aerated Concrete) Block | A04AL070-00003 Finishing Work Masonry Work AAC (Autoclaved Aerated Concrete) Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 200mm<THK | A04AL070 | 00003 | A04AL070-00003 | AR | A04 | Finishing Work | AL | Masonry Work | 070 | AAC (Autoclaved Aerated Concrete) Block |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 14 | 200mm<THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL070 | A04AL070-00003
|  |  |  | A04AL071 Finishing Work Masonry Work Glass Block | A04AL071-00001 Finishing Work Masonry Work Glass Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 50mm<THK≤80mm | A04AL071 | 00001 | A04AL071-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 071 | Glass Block |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 19 | 50mm<THK≤80mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL071 | A04AL071-00001
|  |  |  | A04AL071 Finishing Work Masonry Work Glass Block | A04AL071-00002 Finishing Work Masonry Work Glass Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 80mm<THK≤90mm | A04AL071 | 00002 | A04AL071-00002 | AR | A04 | Finishing Work | AL | Masonry Work | 071 | Glass Block |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 20 | 80mm<THK≤90mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL071 | A04AL071-00002
|  |  |  | A04AL071 Finishing Work Masonry Work Glass Block | A04AL071-00003 Finishing Work Masonry Work Glass Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK | A04AL071 | 00003 | A04AL071-00003 | AR | A04 | Finishing Work | AL | Masonry Work | 071 | Glass Block |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 21 | 90mm<THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL071 | A04AL071-00003
|  |  |  | A04AL072 Finishing Work Masonry Work Clay Block | A04AL072-00001 Finishing Work Masonry Work Clay Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 50mm<THK≤100mm | A04AL072 | 00001 | A04AL072-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 072 | Clay Block |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 17 | 50mm<THK≤100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL072 | A04AL072-00001
|  |  |  | A04AL072 Finishing Work Masonry Work Clay Block | A04AL072-00002 Finishing Work Masonry Work Clay Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 100mm<THK≤200mm | A04AL072 | 00002 | A04AL072-00002 | AR | A04 | Finishing Work | AL | Masonry Work | 072 | Clay Block |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 18 | 100mm<THK≤200mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL072 | A04AL072-00002
|  |  |  | A04AL072 Finishing Work Masonry Work Clay Block | A04AL072-00003 Finishing Work Masonry Work Clay Block w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 200mm<THK | A04AL072 | 00003 | A04AL072-00003 | AR | A04 | Finishing Work | AL | Masonry Work | 072 | Clay Block |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 14 | 200mm<THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL072 | A04AL072-00003
|  |  |  | A04AL073 Finishing Work Masonry Work Concrete Brick | A04AL073-00001 Finishing Work Masonry Work Concrete Brick [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. THK≤90mm | A04AL073 | 00001 | A04AL073-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 073 | Concrete Brick |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 22 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 22 | THK≤90mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL073 | A04AL073-00001
|  |  |  | A04AL073 Finishing Work Masonry Work Concrete Brick | A04AL073-00002 Finishing Work Masonry Work Concrete Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL073 | 00002 | A04AL073-00002 | AR | A04 | Finishing Work | AL | Masonry Work | 073 | Concrete Brick |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 23 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 23 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL073 | A04AL073-00002
|  |  |  | A04AL073 Finishing Work Masonry Work Concrete Brick | A04AL073-00003 Finishing Work Masonry Work Concrete Brick [1.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 190mm<THK≤290mm | A04AL073 | 00003 | A04AL073-00003 | AR | A04 | Finishing Work | AL | Masonry Work | 073 | Concrete Brick |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 24 | [1.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 24 | 190mm<THK≤290mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL073 | A04AL073-00003
|  |  |  | A04AL073 Finishing Work Masonry Work Concrete Brick | A04AL073-00004 Finishing Work Masonry Work Concrete Brick [2.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 290mm<THK | A04AL073 | 00004 | A04AL073-00004 | AR | A04 | Finishing Work | AL | Masonry Work | 073 | Concrete Brick |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 25 | [2.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 25 | 290mm<THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL073 | A04AL073-00004
|  |  |  | A04AL074 Finishing Work Masonry Work Burnt Clay Brick | A04AL074-00001 Finishing Work Masonry Work Burnt Clay Brick [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. THK≤90mm | A04AL074 | 00001 | A04AL074-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 074 | Burnt Clay Brick |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 22 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 22 | THK≤90mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL074 | A04AL074-00001
|  |  |  | A04AL074 Finishing Work Masonry Work Burnt Clay Brick | A04AL074-00002 Finishing Work Masonry Work Burnt Clay Brick [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm | A04AL074 | 00002 | A04AL074-00002 | AR | A04 | Finishing Work | AL | Masonry Work | 074 | Burnt Clay Brick |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 23 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 23 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL074 | A04AL074-00002
|  |  |  | A04AL074 Finishing Work Masonry Work Burnt Clay Brick | A04AL074-00003 Finishing Work Masonry Work Burnt Clay Brick [1.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 190mm<THK≤290mm | A04AL074 | 00003 | A04AL074-00003 | AR | A04 | Finishing Work | AL | Masonry Work | 074 | Burnt Clay Brick |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 24 | [1.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 24 | 190mm<THK≤290mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL074 | A04AL074-00003
|  |  |  | A04AL074 Finishing Work Masonry Work Burnt Clay Brick | A04AL074-00004 Finishing Work Masonry Work Burnt Clay Brick [2.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 290mm<THK | A04AL074 | 00004 | A04AL074-00004 | AR | A04 | Finishing Work | AL | Masonry Work | 074 | Burnt Clay Brick |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 25 | [2.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 | 25 | 290mm<THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL074 | A04AL074-00004
|  |  |  | A04AL075 Finishing Work Masonry Work Insulated Brick | A04AL075-00001 Finishing Work Masonry Work Insulated Brick w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | A04AL075 | 00001 | A04AL075-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 075 | Insulated Brick |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL075 | A04AL075-00001
|  |  |  | A04AL076 Finishing Work Masonry Work Insulation | A04AL076-00001 Finishing Work Masonry Work Insulation Mineral Wool (Rock Wool) Minimum Density of 50 kg/m3 THK<50mm | A04AL076 | 00001 | A04AL076-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 43 | Mineral Wool (Rock Wool) |  | 0 |  | 0 |  | 0 |  | 0 | 26 | Minimum Density of 50 kg/m3 |  | 0 | 31 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL076 | A04AL076-00001
|  |  |  | A04AL076 Finishing Work Masonry Work Insulation | A04AL076-00002 Finishing Work Masonry Work Insulation Mineral Wool (Rock Wool) Minimum Density of 50 kg/m3 50mm≤THK<75mm | A04AL076 | 00002 | A04AL076-00002 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 43 | Mineral Wool (Rock Wool) |  | 0 |  | 0 |  | 0 |  | 0 | 26 | Minimum Density of 50 kg/m3 |  | 0 | 09 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL076 | A04AL076-00002
|  |  |  | A04AL076 Finishing Work Masonry Work Insulation | A04AL076-00003 Finishing Work Masonry Work Insulation Mineral Wool (Rock Wool) Minimum Density of 50 kg/m3 75mm≤THK<100mm | A04AL076 | 00003 | A04AL076-00003 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 43 | Mineral Wool (Rock Wool) |  | 0 |  | 0 |  | 0 |  | 0 | 26 | Minimum Density of 50 kg/m3 |  | 0 | 10 | 75mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL076 | A04AL076-00003
|  |  |  | A04AL076 Finishing Work Masonry Work Insulation | A04AL076-00004 Finishing Work Masonry Work Insulation Mineral Wool (Rock Wool) Minimum Density of 50 kg/m3 100mm≤THK | A04AL076 | 00004 | A04AL076-00004 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 43 | Mineral Wool (Rock Wool) |  | 0 |  | 0 |  | 0 |  | 0 | 26 | Minimum Density of 50 kg/m3 |  | 0 | 11 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL076 | A04AL076-00004
|  |  |  | A04AL076 Finishing Work Masonry Work Insulation | A04AL076-00005 Finishing Work Masonry Work Insulation Glass Wool (Fiberglass) Minimum Density of 50 kg/m3 THK<50mm | A04AL076 | 00005 | A04AL076-00005 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 44 | Glass Wool (Fiberglass) |  | 0 |  | 0 |  | 0 |  | 0 | 26 | Minimum Density of 50 kg/m3 |  | 0 | 31 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL076 | A04AL076-00005
|  |  |  | A04AL076 Finishing Work Masonry Work Insulation | A04AL076-00006 Finishing Work Masonry Work Insulation Glass Wool (Fiberglass) Minimum Density of 50 kg/m3 50mm≤THK<75mm | A04AL076 | 00006 | A04AL076-00006 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 44 | Glass Wool (Fiberglass) |  | 0 |  | 0 |  | 0 |  | 0 | 26 | Minimum Density of 50 kg/m3 |  | 0 | 09 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL076 | A04AL076-00006
|  |  |  | A04AL076 Finishing Work Masonry Work Insulation | A04AL076-00007 Finishing Work Masonry Work Insulation Glass Wool (Fiberglass) Minimum Density of 50 kg/m3 75mm≤THK<100mm | A04AL076 | 00007 | A04AL076-00007 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 44 | Glass Wool (Fiberglass) |  | 0 |  | 0 |  | 0 |  | 0 | 26 | Minimum Density of 50 kg/m3 |  | 0 | 10 | 75mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL076 | A04AL076-00007
|  |  |  | A04AL076 Finishing Work Masonry Work Insulation | A04AL076-00008 Finishing Work Masonry Work Insulation Glass Wool (Fiberglass) Minimum Density of 50 kg/m3 100mm≤THK | A04AL076 | 00008 | A04AL076-00008 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 44 | Glass Wool (Fiberglass) |  | 0 |  | 0 |  | 0 |  | 0 | 26 | Minimum Density of 50 kg/m3 |  | 0 | 11 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL076 | A04AL076-00008
|  |  |  | A04AL076 Finishing Work Masonry Work Insulation | A04AL076-00009 Finishing Work Masonry Work Insulation Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) Minimum Density of 25 kg/m3 THK<50mm | A04AL076 | 00009 | A04AL076-00009 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 64 | Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) |  | 0 |  | 0 |  | 0 |  | 0 | 57 | Minimum Density of 25 kg/m3 |  | 0 | 31 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL076 | A04AL076-00009
|  |  |  | A04AL076 Finishing Work Masonry Work Insulation | A04AL076-00010 Finishing Work Masonry Work Insulation Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) Minimum Density of 25 kg/m3 50mm≤THK<75mm | A04AL076 | 00010 | A04AL076-00010 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 64 | Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) |  | 0 |  | 0 |  | 0 |  | 0 | 57 | Minimum Density of 25 kg/m3 |  | 0 | 09 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL076 | A04AL076-00010
|  |  |  | A04AL076 Finishing Work Masonry Work Insulation | A04AL076-00011 Finishing Work Masonry Work Insulation Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) Minimum Density of 25 kg/m3 75mm≤THK<100mm | A04AL076 | 00011 | A04AL076-00011 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 64 | Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) |  | 0 |  | 0 |  | 0 |  | 0 | 57 | Minimum Density of 25 kg/m3 |  | 0 | 10 | 75mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL076 | A04AL076-00011
|  |  |  | A04AL076 Finishing Work Masonry Work Insulation | A04AL076-00012 Finishing Work Masonry Work Insulation Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) Minimum Density of 25 kg/m3 100mm≤THK | A04AL076 | 00012 | A04AL076-00012 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 64 | Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) |  | 0 |  | 0 |  | 0 |  | 0 | 57 | Minimum Density of 25 kg/m3 |  | 0 | 11 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AL076 | A04AL076-00012
|  |  |  | A04AM077 Finishing Work Painting Work External Wall Painting | A04AM077-00001 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint | A04AM077 | 00001 | A04AM077-00001 | AR | A04 | Finishing Work | AM | Painting Work | 077 | External Wall Painting | 45 | Acrylic Emulsion Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM077 | A04AM077-00001
|  |  |  | A04AM077 Finishing Work Painting Work External Wall Painting | A04AM077-00002 Finishing Work Painting Work External Wall Painting Acrylic Emulsion Paint (Textured Type) | A04AM077 | 00002 | A04AM077-00002 | AR | A04 | Finishing Work | AM | Painting Work | 077 | External Wall Painting | 46 | Acrylic Emulsion Paint (Textured Type) |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM077 | A04AM077-00002
|  |  |  | A04AM077 Finishing Work Painting Work External Wall Painting | A04AM077-00003 Finishing Work Painting Work External Wall Painting Water Emulsion Paint | A04AM077 | 00003 | A04AM077-00003 | AR | A04 | Finishing Work | AM | Painting Work | 077 | External Wall Painting | 47 | Water Emulsion Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM077 | A04AM077-00003
|  |  |  | A04AM077 Finishing Work Painting Work External Wall Painting | A04AM077-00004 Finishing Work Painting Work External Wall Painting Latex Paint | A04AM077 | 00004 | A04AM077-00004 | AR | A04 | Finishing Work | AM | Painting Work | 077 | External Wall Painting | 48 | Latex Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM077 | A04AM077-00004
|  |  |  | A04AM077 Finishing Work Painting Work External Wall Painting | A04AM077-00005 Finishing Work Painting Work External Wall Painting Latex Paint (Textured Type) | A04AM077 | 00005 | A04AM077-00005 | AR | A04 | Finishing Work | AM | Painting Work | 077 | External Wall Painting | 49 | Latex Paint (Textured Type) |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM077 | A04AM077-00005
|  |  |  | A04AM077 Finishing Work Painting Work External Wall Painting | A04AM077-00006 Finishing Work Painting Work External Wall Painting Epoxy Paint | A04AM077 | 00006 | A04AM077-00006 | AR | A04 | Finishing Work | AM | Painting Work | 077 | External Wall Painting | 50 | Epoxy Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM077 | A04AM077-00006
|  |  |  | A04AM077 Finishing Work Painting Work External Wall Painting | A04AM077-00007 Finishing Work Painting Work External Wall Painting Stucco Finish | A04AM077 | 00007 | A04AM077-00007 | AR | A04 | Finishing Work | AM | Painting Work | 077 | External Wall Painting | 51 | Stucco Finish |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM077 | A04AM077-00007
|  |  |  | A04AM077 Finishing Work Painting Work External Wall Painting | A04AM077-00008 Finishing Work Painting Work External Wall Painting Chemical Resistant Paint | A04AM077 | 00008 | A04AM077-00008 | AR | A04 | Finishing Work | AM | Painting Work | 077 | External Wall Painting | 74 | Chemical Resistant Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM077 | A04AM077-00008
|  |  |  | A04AM078 Finishing Work Painting Work Internal Wall Painting | A04AM078-00001 Finishing Work Painting Work Internal Wall Painting Acrylic Emulsion Paint | A04AM078 | 00001 | A04AM078-00001 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 45 | Acrylic Emulsion Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM078 | A04AM078-00001
|  |  |  | A04AM078 Finishing Work Painting Work Internal Wall Painting | A04AM078-00002 Finishing Work Painting Work Internal Wall Painting Water Emulsion Paint | A04AM078 | 00002 | A04AM078-00002 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 47 | Water Emulsion Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM078 | A04AM078-00002
|  |  |  | A04AM078 Finishing Work Painting Work Internal Wall Painting | A04AM078-00003 Finishing Work Painting Work Internal Wall Painting Latex Paint | A04AM078 | 00003 | A04AM078-00003 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 48 | Latex Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM078 | A04AM078-00003
|  |  |  | A04AM078 Finishing Work Painting Work Internal Wall Painting | A04AM078-00004 Finishing Work Painting Work Internal Wall Painting Acid/Alkaline Resistant Paint | A04AM078 | 00004 | A04AM078-00004 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 52 | Acid/Alkaline Resistant Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM078 | A04AM078-00004
|  |  |  | A04AM078 Finishing Work Painting Work Internal Wall Painting | A04AM078-00005 Finishing Work Painting Work Internal Wall Painting Epoxy Paint | A04AM078 | 00005 | A04AM078-00005 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 50 | Epoxy Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM078 | A04AM078-00005
|  |  |  | A04AM078 Finishing Work Painting Work Internal Wall Painting | A04AM078-00006 Finishing Work Painting Work Internal Wall Painting Stucco Finish | A04AM078 | 00006 | A04AM078-00006 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 51 | Stucco Finish |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM078 | A04AM078-00006
|  |  |  | A04AM078 Finishing Work Painting Work Internal Wall Painting | A04AM078-00007 Finishing Work Painting Work Internal Wall Painting Anti-Dust Paint | A04AM078 | 00007 | A04AM078-00007 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 53 | Anti-Dust Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM078 | A04AM078-00007
|  |  |  | A04AM078 Finishing Work Painting Work Internal Wall Painting | A04AM078-00008 Finishing Work Painting Work Internal Wall Painting Epoxy Based Sealer | A04AM078 | 00008 | A04AM078-00008 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 54 | Epoxy Based Sealer |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM078 | A04AM078-00008
|  |  |  | A04AM078 Finishing Work Painting Work Internal Wall Painting | A04AM078-00009 Finishing Work Painting Work Internal Wall Painting Chemical Resistant Paint | A04AM078 | 00009 | A04AM078-00009 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 74 | Chemical Resistant Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM078 | A04AM078-00009
|  |  |  | A04AM079 Finishing Work Painting Work Ceiling Painting | A04AM079-00001 Finishing Work Painting Work Ceiling Painting Acrylic Emulsion Paint | A04AM079 | 00001 | A04AM079-00001 | AR | A04 | Finishing Work | AM | Painting Work | 079 | Ceiling Painting | 45 | Acrylic Emulsion Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM079 | A04AM079-00001
|  |  |  | A04AM079 Finishing Work Painting Work Ceiling Painting | A04AM079-00002 Finishing Work Painting Work Ceiling Painting Water Emulsion Paint | A04AM079 | 00002 | A04AM079-00002 | AR | A04 | Finishing Work | AM | Painting Work | 079 | Ceiling Painting | 47 | Water Emulsion Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM079 | A04AM079-00002
|  |  |  | A04AM079 Finishing Work Painting Work Ceiling Painting | A04AM079-00003 Finishing Work Painting Work Ceiling Painting Latex Paint | A04AM079 | 00003 | A04AM079-00003 | AR | A04 | Finishing Work | AM | Painting Work | 079 | Ceiling Painting | 48 | Latex Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM079 | A04AM079-00003
|  |  |  | A04AM079 Finishing Work Painting Work Ceiling Painting | A04AM079-00004 Finishing Work Painting Work Ceiling Painting Acid/Alkaline Resistant Paint | A04AM079 | 00004 | A04AM079-00004 | AR | A04 | Finishing Work | AM | Painting Work | 079 | Ceiling Painting | 52 | Acid/Alkaline Resistant Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM079 | A04AM079-00004
|  |  |  | A04AM079 Finishing Work Painting Work Ceiling Painting | A04AM079-00005 Finishing Work Painting Work Ceiling Painting Anti-Dust Paint | A04AM079 | 00005 | A04AM079-00005 | AR | A04 | Finishing Work | AM | Painting Work | 079 | Ceiling Painting | 53 | Anti-Dust Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM079 | A04AM079-00005
|  |  |  | A04AM079 Finishing Work Painting Work Ceiling Painting | A04AM079-00006 Finishing Work Painting Work Ceiling Painting Epoxy Paint | A04AM079 | 00006 | A04AM079-00006 | AR | A04 | Finishing Work | AM | Painting Work | 079 | Ceiling Painting | 50 | Epoxy Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM079 | A04AM079-00006
|  |  |  | A04AM080 Finishing Work Painting Work Floor Painting | A04AM080-00001 Finishing Work Painting Work Floor Painting Acrylic Emulsion Paint | A04AM080 | 00001 | A04AM080-00001 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 45 | Acrylic Emulsion Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM080 | A04AM080-00001
|  |  |  | A04AM080 Finishing Work Painting Work Floor Painting | A04AM080-00002 Finishing Work Painting Work Floor Painting Water Emulsion Paint | A04AM080 | 00002 | A04AM080-00002 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 47 | Water Emulsion Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM080 | A04AM080-00002
|  |  |  | A04AM080 Finishing Work Painting Work Floor Painting | A04AM080-00003 Finishing Work Painting Work Floor Painting Acid/Alkaline Resistant Paint | A04AM080 | 00003 | A04AM080-00003 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 52 | Acid/Alkaline Resistant Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM080 | A04AM080-00003
|  |  |  | A04AM080 Finishing Work Painting Work Floor Painting | A04AM080-00004 Finishing Work Painting Work Floor Painting Oil Based Paint | A04AM080 | 00004 | A04AM080-00004 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 55 | Oil Based Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM080 | A04AM080-00004
|  |  |  | A04AM080 Finishing Work Painting Work Floor Painting | A04AM080-00005 Finishing Work Painting Work Floor Painting Anti-Dust Paint | A04AM080 | 00005 | A04AM080-00005 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 53 | Anti-Dust Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM080 | A04AM080-00005
|  |  |  | A04AM080 Finishing Work Painting Work Floor Painting | A04AM080-00006 Finishing Work Painting Work Floor Painting Epoxy Paint | A04AM080 | 00006 | A04AM080-00006 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 50 | Epoxy Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM080 | A04AM080-00006
|  |  |  | A04AM080 Finishing Work Painting Work Floor Painting | A04AM080-00007 Finishing Work Painting Work Floor Painting Epoxy Based Sealer | A04AM080 | 00007 | A04AM080-00007 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 54 | Epoxy Based Sealer |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM080 | A04AM080-00007
|  |  |  | A04AM080 Finishing Work Painting Work Floor Painting | A04AM080-00008 Finishing Work Painting Work Floor Painting Epoxy Lining | A04AM080 | 00008 | A04AM080-00008 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 56 | Epoxy Lining |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM080 | A04AM080-00008
|  |  |  | A04AM080 Finishing Work Painting Work Floor Painting | A04AM080-00009 Finishing Work Painting Work Floor Painting Road Marker Paint | A04AM080 | 00009 | A04AM080-00009 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 57 | Road Marker Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM080 | A04AM080-00009
|  |  |  | A04AM080 Finishing Work Painting Work Floor Painting | A04AM080-00010 Finishing Work Painting Work Floor Painting White Strips for Parking Place | A04AM080 | 00010 | A04AM080-00010 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 58 | White Strips for Parking Place |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M | A04AM080 | A04AM080-00010
|  |  |  | A04AM080 Finishing Work Painting Work Floor Painting | A04AM080-00011 Finishing Work Painting Work Floor Painting Chemical Resistant Paint | A04AM080 | 00011 | A04AM080-00011 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 74 | Chemical Resistant Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM080 | A04AM080-00011
|  |  |  | A04AM080 Finishing Work Painting Work Floor Painting | A04AM080-00012 Finishing Work Painting Work Floor Painting Polyurethane Coating | A04AM080 | 00012 | A04AM080-00012 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | FT | Polyurethane Coating |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AM080 | A04AM080-00012
|  |  |  | A04AM081 Finishing Work Painting Work Skirt Painting | A04AM081-00001 Finishing Work Painting Work Skirt Painting Acrylic Emulsion Paint H<150mm | A04AM081 | 00001 | A04AM081-00001 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 45 | Acrylic Emulsion Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AM081 | A04AM081-00001
|  |  |  | A04AM081 Finishing Work Painting Work Skirt Painting | A04AM081-00002 Finishing Work Painting Work Skirt Painting Acrylic Emulsion Paint 150mm≤H<200mm | A04AM081 | 00002 | A04AM081-00002 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 45 | Acrylic Emulsion Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AM081 | A04AM081-00002
|  |  |  | A04AM081 Finishing Work Painting Work Skirt Painting | A04AM081-00003 Finishing Work Painting Work Skirt Painting Acrylic Emulsion Paint 200mm≤H | A04AM081 | 00003 | A04AM081-00003 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 45 | Acrylic Emulsion Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AM081 | A04AM081-00003
|  |  |  | A04AM081 Finishing Work Painting Work Skirt Painting | A04AM081-00004 Finishing Work Painting Work Skirt Painting Acid/Alkaline Resistant Paint H<150mm | A04AM081 | 00004 | A04AM081-00004 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 52 | Acid/Alkaline Resistant Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AM081 | A04AM081-00004
|  |  |  | A04AM081 Finishing Work Painting Work Skirt Painting | A04AM081-00005 Finishing Work Painting Work Skirt Painting Acid/Alkaline Resistant Paint 150mm≤H<200mm | A04AM081 | 00005 | A04AM081-00005 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 52 | Acid/Alkaline Resistant Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AM081 | A04AM081-00005
|  |  |  | A04AM081 Finishing Work Painting Work Skirt Painting | A04AM081-00006 Finishing Work Painting Work Skirt Painting Acid/Alkaline Resistant Paint 200mm≤H | A04AM081 | 00006 | A04AM081-00006 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 52 | Acid/Alkaline Resistant Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AM081 | A04AM081-00006
|  |  |  | A04AM081 Finishing Work Painting Work Skirt Painting | A04AM081-00007 Finishing Work Painting Work Skirt Painting Epoxy Paint H<150mm | A04AM081 | 00007 | A04AM081-00007 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 50 | Epoxy Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AM081 | A04AM081-00007
|  |  |  | A04AM081 Finishing Work Painting Work Skirt Painting | A04AM081-00008 Finishing Work Painting Work Skirt Painting Epoxy Paint 150mm≤H<200mm | A04AM081 | 00008 | A04AM081-00008 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 50 | Epoxy Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AM081 | A04AM081-00008
|  |  |  | A04AM081 Finishing Work Painting Work Skirt Painting | A04AM081-00009 Finishing Work Painting Work Skirt Painting Epoxy Paint 200mm≤H | A04AM081 | 00009 | A04AM081-00009 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 50 | Epoxy Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AM081 | A04AM081-00009
|  |  |  | A04AM081 Finishing Work Painting Work Skirt Painting | A04AM081-00010 Finishing Work Painting Work Skirt Painting Chemical Resistant Paint H<150mm | A04AM081 | 00010 | A04AM081-00010 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 74 | Chemical Resistant Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AM081 | A04AM081-00010
|  |  |  | A04AM081 Finishing Work Painting Work Skirt Painting | A04AM081-00011 Finishing Work Painting Work Skirt Painting Chemical Resistant Paint 150mm≤H<200mm | A04AM081 | 00011 | A04AM081-00011 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 74 | Chemical Resistant Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AM081 | A04AM081-00011
|  |  |  | A04AM081 Finishing Work Painting Work Skirt Painting | A04AM081-00012 Finishing Work Painting Work Skirt Painting Chemical Resistant Paint 200mm≤H | A04AM081 | 00012 | A04AM081-00012 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 74 | Chemical Resistant Paint |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AM081 | A04AM081-00012
|  |  |  | A04AM081 Finishing Work Painting Work Skirt Painting | A04AM081-00013 Finishing Work Painting Work Skirt Painting Polyurethane Coating H<150mm | A04AM081 | 00013 | A04AM081-00013 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | FT | Polyurethane Coating |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AM081 | A04AM081-00013
|  |  |  | A04AM081 Finishing Work Painting Work Skirt Painting | A04AM081-00014 Finishing Work Painting Work Skirt Painting Polyurethane Coating 150mm≤H<200mm | A04AM081 | 00014 | A04AM081-00014 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | FT | Polyurethane Coating |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AM081 | A04AM081-00014
|  |  |  | A04AM081 Finishing Work Painting Work Skirt Painting | A04AM081-00015 Finishing Work Painting Work Skirt Painting Polyurethane Coating 200mm≤H | A04AM081 | 00015 | A04AM081-00015 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | FT | Polyurethane Coating |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AM081 | A04AM081-00015
|  |  |  | A04AN082 Finishing Work Tile Work Wall Tile | A04AN082-00001 Finishing Work Tile Work Wall Tile Unglazed Ceramic Tile w/ Mortar Bond Coat or Adhesive | A04AN082 | 00001 | A04AN082-00001 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 59 | Unglazed Ceramic Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN082 | A04AN082-00001
|  |  |  | A04AN082 Finishing Work Tile Work Wall Tile | A04AN082-00002 Finishing Work Tile Work Wall Tile Glazed Ceramic Tile w/ Mortar Bond Coat or Adhesive | A04AN082 | 00002 | A04AN082-00002 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 60 | Glazed Ceramic Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN082 | A04AN082-00002
|  |  |  | A04AN082 Finishing Work Tile Work Wall Tile | A04AN082-00003 Finishing Work Tile Work Wall Tile Acid/Alkaline Resistant Tile w/ Mortar Bond Coat or Adhesive | A04AN082 | 00003 | A04AN082-00003 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 61 | Acid/Alkaline Resistant Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN082 | A04AN082-00003
|  |  |  | A04AN082 Finishing Work Tile Work Wall Tile | A04AN082-00004 Finishing Work Tile Work Wall Tile Granite Tile w/ Wet Method (Mortar Bond Coat or Adhesive) or Dry Method (Steel or SST Frame, Angle, Bolt, etc.) | A04AN082 | 00004 | A04AN082-00004 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 62 | Granite Tile |  | 0 |  | 0 |  | 0 |  | 0 | 28 | w/ Wet Method (Mortar Bond Coat or Adhesive) or Dry Method (Steel or SST Frame, Angle, Bolt, etc.) |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN082 | A04AN082-00004
|  |  |  | A04AN082 Finishing Work Tile Work Wall Tile | A04AN082-00005 Finishing Work Tile Work Wall Tile Marble Tile w/ Wet Method (Mortar Bond Coat or Adhesive) or Dry Method (Steel or SST Frame, Angle, Bolt, etc.) | A04AN082 | 00005 | A04AN082-00005 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 63 | Marble Tile |  | 0 |  | 0 |  | 0 |  | 0 | 28 | w/ Wet Method (Mortar Bond Coat or Adhesive) or Dry Method (Steel or SST Frame, Angle, Bolt, etc.) |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN082 | A04AN082-00005
|  |  |  | A04AN082 Finishing Work Tile Work Wall Tile | A04AN082-00006 Finishing Work Tile Work Wall Tile Stone Tile w/ Mortar Bond Coat or Adhesive | A04AN082 | 00006 | A04AN082-00006 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 72 | Stone Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN082 | A04AN082-00006
|  |  |  | A04AN082 Finishing Work Tile Work Wall Tile | A04AN082-00007 Finishing Work Tile Work Wall Tile Mosaic Tile w/ Mortar Bond Coat or Adhesive | A04AN082 | 00007 | A04AN082-00007 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 65 | Mosaic Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN082 | A04AN082-00007
|  |  |  | A04AN082 Finishing Work Tile Work Wall Tile | A04AN082-00008 Finishing Work Tile Work Wall Tile Acoustic Tile w/ Mortar Bond Coat or Adhesive | A04AN082 | 00008 | A04AN082-00008 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 66 | Acoustic Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN082 | A04AN082-00008
|  |  |  | A04AN082 Finishing Work Tile Work Wall Tile | A04AN082-00009 Finishing Work Tile Work Wall Tile Porcelain Tile w/ Mortar Bond Coat or Adhesive | A04AN082 | 00009 | A04AN082-00009 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 67 | Porcelain Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN082 | A04AN082-00009
|  |  |  | A04AN083 Finishing Work Tile Work Floor Tile | A04AN083-00001 Finishing Work Tile Work Floor Tile Ceramic Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083 | 00001 | A04AN083-00001 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 68 | Ceramic Tile |  | 0 |  | 0 |  | 0 |  | 0 | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN083 | A04AN083-00001
|  |  |  | A04AN083 Finishing Work Tile Work Floor Tile | A04AN083-00002 Finishing Work Tile Work Floor Tile Acid/Alkaline Resistant Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083 | 00002 | A04AN083-00002 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 61 | Acid/Alkaline Resistant Tile |  | 0 |  | 0 |  | 0 |  | 0 | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN083 | A04AN083-00002
|  |  |  | A04AN083 Finishing Work Tile Work Floor Tile | A04AN083-00003 Finishing Work Tile Work Floor Tile Terrazzo Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083 | 00003 | A04AN083-00003 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 69 | Terrazzo Tile |  | 0 |  | 0 |  | 0 |  | 0 | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN083 | A04AN083-00003
|  |  |  | A04AN083 Finishing Work Tile Work Floor Tile | A04AN083-00004 Finishing Work Tile Work Floor Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive | A04AN083 | 00004 | A04AN083-00004 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 70 | Vinyl Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN083 | A04AN083-00004
|  |  |  | A04AN083 Finishing Work Tile Work Floor Tile | A04AN083-00005 Finishing Work Tile Work Floor Tile Anti-Static Vinyl Tile w/ Mortar Bond Coat or Adhesive | A04AN083 | 00005 | A04AN083-00005 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 71 | Anti-Static Vinyl Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN083 | A04AN083-00005
|  |  |  | A04AN083 Finishing Work Tile Work Floor Tile | A04AN083-00006 Finishing Work Tile Work Floor Tile Granite Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083 | 00006 | A04AN083-00006 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 62 | Granite Tile |  | 0 |  | 0 |  | 0 |  | 0 | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN083 | A04AN083-00006
|  |  |  | A04AN083 Finishing Work Tile Work Floor Tile | A04AN083-00007 Finishing Work Tile Work Floor Tile Marble Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083 | 00007 | A04AN083-00007 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 63 | Marble Tile |  | 0 |  | 0 |  | 0 |  | 0 | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN083 | A04AN083-00007
|  |  |  | A04AN083 Finishing Work Tile Work Floor Tile | A04AN083-00008 Finishing Work Tile Work Floor Tile Stone Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083 | 00008 | A04AN083-00008 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 72 | Stone Tile |  | 0 |  | 0 |  | 0 |  | 0 | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN083 | A04AN083-00008
|  |  |  | A04AN083 Finishing Work Tile Work Floor Tile | A04AN083-00009 Finishing Work Tile Work Floor Tile Concrete Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083 | 00009 | A04AN083-00009 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 73 | Concrete Tile |  | 0 |  | 0 |  | 0 |  | 0 | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN083 | A04AN083-00009
|  |  |  | A04AN083 Finishing Work Tile Work Floor Tile | A04AN083-00010 Finishing Work Tile Work Floor Tile Mosaic Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083 | 00010 | A04AN083-00010 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 65 | Mosaic Tile |  | 0 |  | 0 |  | 0 |  | 0 | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN083 | A04AN083-00010
|  |  |  | A04AN083 Finishing Work Tile Work Floor Tile | A04AN083-00011 Finishing Work Tile Work Floor Tile Porcelain Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive | A04AN083 | 00011 | A04AN083-00011 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 67 | Porcelain Tile |  | 0 |  | 0 |  | 0 |  | 0 | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN083 | A04AN083-00011
|  |  |  | A04AN083 Finishing Work Tile Work Floor Tile | A04AN083-00012 Finishing Work Tile Work Floor Tile Rubber Tile w/ Mortar Bond Coat or Adhesive | A04AN083 | 00012 | A04AN083-00012 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | FD | Rubber Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AN083 | A04AN083-00012
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00001 Finishing Work Tile Work Skirt Tile Unglazed Ceramic Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084 | 00001 | A04AN084-00001 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 59 | Unglazed Ceramic Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00001
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00002 Finishing Work Tile Work Skirt Tile Unglazed Ceramic Tile w/ Mortar Bond Coat or Adhesive 150mm≤H<200mm | A04AN084 | 00002 | A04AN084-00002 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 59 | Unglazed Ceramic Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00002
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00003 Finishing Work Tile Work Skirt Tile Unglazed Ceramic Tile w/ Mortar Bond Coat or Adhesive 200mm≤H | A04AN084 | 00003 | A04AN084-00003 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 59 | Unglazed Ceramic Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00003
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00004 Finishing Work Tile Work Skirt Tile Glazed Ceramic Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084 | 00004 | A04AN084-00004 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 60 | Glazed Ceramic Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00004
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00005 Finishing Work Tile Work Skirt Tile Glazed Ceramic Tile w/ Mortar Bond Coat or Adhesive 150mm≤H<200mm | A04AN084 | 00005 | A04AN084-00005 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 60 | Glazed Ceramic Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00005
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00006 Finishing Work Tile Work Skirt Tile Glazed Ceramic Tile w/ Mortar Bond Coat or Adhesive 200mm≤H | A04AN084 | 00006 | A04AN084-00006 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 60 | Glazed Ceramic Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00006
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00007 Finishing Work Tile Work Skirt Tile Acid/Alkaline Resistant Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084 | 00007 | A04AN084-00007 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 61 | Acid/Alkaline Resistant Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00007
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00008 Finishing Work Tile Work Skirt Tile Acid/Alkaline Resistant Tile w/ Mortar Bond Coat or Adhesive 150mm≤H<200mm | A04AN084 | 00008 | A04AN084-00008 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 61 | Acid/Alkaline Resistant Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00008
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00009 Finishing Work Tile Work Skirt Tile Acid/Alkaline Resistant Tile w/ Mortar Bond Coat or Adhesive 200mm≤H | A04AN084 | 00009 | A04AN084-00009 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 61 | Acid/Alkaline Resistant Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00009
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00010 Finishing Work Tile Work Skirt Tile Terrazzo Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084 | 00010 | A04AN084-00010 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 69 | Terrazzo Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00010
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00011 Finishing Work Tile Work Skirt Tile Terrazzo Tile w/ Mortar Bond Coat or Adhesive 150mm≤H<200mm | A04AN084 | 00011 | A04AN084-00011 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 69 | Terrazzo Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00011
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00012 Finishing Work Tile Work Skirt Tile Terrazzo Tile w/ Mortar Bond Coat or Adhesive 200mm≤H | A04AN084 | 00012 | A04AN084-00012 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 69 | Terrazzo Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00012
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00013 Finishing Work Tile Work Skirt Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084 | 00013 | A04AN084-00013 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 70 | Vinyl Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00013
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00014 Finishing Work Tile Work Skirt Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive 150mm≤H<200mm | A04AN084 | 00014 | A04AN084-00014 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 70 | Vinyl Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00014
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00015 Finishing Work Tile Work Skirt Tile Vinyl Tile w/ Mortar Bond Coat or Adhesive 200mm≤H | A04AN084 | 00015 | A04AN084-00015 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 70 | Vinyl Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00015
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00016 Finishing Work Tile Work Skirt Tile Anti-Static Vinyl Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084 | 00016 | A04AN084-00016 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 71 | Anti-Static Vinyl Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00016
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00017 Finishing Work Tile Work Skirt Tile Anti-Static Vinyl Tile w/ Mortar Bond Coat or Adhesive 150mm≤H<200mm | A04AN084 | 00017 | A04AN084-00017 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 71 | Anti-Static Vinyl Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00017
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00018 Finishing Work Tile Work Skirt Tile Anti-Static Vinyl Tile w/ Mortar Bond Coat or Adhesive 200mm≤H | A04AN084 | 00018 | A04AN084-00018 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 71 | Anti-Static Vinyl Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00018
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00019 Finishing Work Tile Work Skirt Tile Granite Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084 | 00019 | A04AN084-00019 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 62 | Granite Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00019
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00020 Finishing Work Tile Work Skirt Tile Granite Tile w/ Mortar Bond Coat or Adhesive 150mm≤H<200mm | A04AN084 | 00020 | A04AN084-00020 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 62 | Granite Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00020
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00021 Finishing Work Tile Work Skirt Tile Granite Tile w/ Mortar Bond Coat or Adhesive 200mm≤H | A04AN084 | 00021 | A04AN084-00021 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 62 | Granite Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00021
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00022 Finishing Work Tile Work Skirt Tile Marble Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084 | 00022 | A04AN084-00022 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 63 | Marble Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00022
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00023 Finishing Work Tile Work Skirt Tile Marble Tile w/ Mortar Bond Coat or Adhesive 150mm≤H<200mm | A04AN084 | 00023 | A04AN084-00023 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 63 | Marble Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00023
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00024 Finishing Work Tile Work Skirt Tile Marble Tile w/ Mortar Bond Coat or Adhesive 200mm≤H | A04AN084 | 00024 | A04AN084-00024 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 63 | Marble Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00024
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00025 Finishing Work Tile Work Skirt Tile Stone Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084 | 00025 | A04AN084-00025 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 72 | Stone Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00025
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00026 Finishing Work Tile Work Skirt Tile Stone Tile w/ Mortar Bond Coat or Adhesive 150mm≤H<200mm | A04AN084 | 00026 | A04AN084-00026 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 72 | Stone Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00026
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00027 Finishing Work Tile Work Skirt Tile Stone Tile w/ Mortar Bond Coat or Adhesive 200mm≤H | A04AN084 | 00027 | A04AN084-00027 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 72 | Stone Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00027
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00028 Finishing Work Tile Work Skirt Tile Concrete Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084 | 00028 | A04AN084-00028 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 73 | Concrete Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00028
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00029 Finishing Work Tile Work Skirt Tile Concrete Tile w/ Mortar Bond Coat or Adhesive 150mm≤H<200mm | A04AN084 | 00029 | A04AN084-00029 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 73 | Concrete Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00029
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00030 Finishing Work Tile Work Skirt Tile Concrete Tile w/ Mortar Bond Coat or Adhesive 200mm≤H | A04AN084 | 00030 | A04AN084-00030 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 73 | Concrete Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00030
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00031 Finishing Work Tile Work Skirt Tile Porcelain Tile w/ Mortar Bond Coat or Adhesive H<150mm | A04AN084 | 00031 | A04AN084-00031 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 67 | Porcelain Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00031
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00032 Finishing Work Tile Work Skirt Tile Porcelain Tile w/ Mortar Bond Coat or Adhesive 150mm≤H<200mm | A04AN084 | 00032 | A04AN084-00032 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 67 | Porcelain Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00032
|  |  |  | A04AN084 Finishing Work Tile Work Skirt Tile | A04AN084-00033 Finishing Work Tile Work Skirt Tile Porcelain Tile w/ Mortar Bond Coat or Adhesive 200mm≤H | A04AN084 | 00033 | A04AN084-00033 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 67 | Porcelain Tile |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AN084 | A04AN084-00033
|  |  |  | A04AP085 Finishing Work Waterproofing Work Liquid Waterproofing | A04AP085-00001 Finishing Work Waterproofing Work Liquid Waterproofing for Internal Floor Area Min. 2 Coats | A04AP085 | 00001 | A04AP085-00001 | AR | A04 | Finishing Work | AP | Waterproofing Work | 085 | Liquid Waterproofing |  | 0 |  | 0 |  | 0 |  | 0 | 02 | for Internal Floor Area | 30 | Min. 2 Coats |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AP085 | A04AP085-00001
|  |  |  | A04AP085 Finishing Work Waterproofing Work Liquid Waterproofing | A04AP085-00002 Finishing Work Waterproofing Work Liquid Waterproofing for Internal Wall Area Min. 2 Coats | A04AP085 | 00002 | A04AP085-00002 | AR | A04 | Finishing Work | AP | Waterproofing Work | 085 | Liquid Waterproofing |  | 0 |  | 0 |  | 0 |  | 0 | 03 | for Internal Wall Area | 30 | Min. 2 Coats |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AP085 | A04AP085-00002
|  |  |  | A04AP310 Finishing Work Waterproofing Work Waterproofing Membrane | A04AP310-00001 Finishing Work Waterproofing Work Waterproofing Membrane for Internal Area | A04AP310 | 00001 | A04AP310-00001 | AR | A04 | Finishing Work | AP | Waterproofing Work | 310 | Waterproofing Membrane |  | 0 |  | 0 |  | 0 |  | 0 | 04 | for Internal Area |  |  |  | 0 |  |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AP310 | A04AP310-00001
|  |  |  | A04AQ012 Finishing Work Roof Work PE Sheet (Vapor Barrier) | A04AQ012-00001 Finishing Work Roof Work PE Sheet (Vapor Barrier) | A04AQ012 | 00001 | A04AQ012-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 012 | PE Sheet (Vapor Barrier) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ012 | A04AQ012-00001
|  |  |  | A04AQ038 Finishing Work Roof Work Welded Wire Fabric | A04AQ038-00001 Finishing Work Roof Work Welded Wire Fabric DIA≤6mm | A04AQ038 | 00001 | A04AQ038-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 038 | Welded Wire Fabric |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 53 | DIA≤6mm | 0 | Mesh Size=DIA( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ038 | A04AQ038-00001
|  |  |  | A04AQ038 Finishing Work Roof Work Welded Wire Fabric | A04AQ038-00002 Finishing Work Roof Work Welded Wire Fabric DIA>6mm | A04AQ038 | 00002 | A04AQ038-00002 | AR | A04 | Finishing Work | AQ | Roof Work | 038 | Welded Wire Fabric |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 54 | DIA>6mm | 0 | Mesh Size=DIA( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ038 | A04AQ038-00002
|  |  |  | A04AQ086 Finishing Work Roof Work Roof Screed | A04AQ086-00001 Finishing Work Roof Work Roof Screed Light-Weight Concrete Screed w/o Welded Wire Fabric 30mm≤Min. THK<50mm | A04AQ086 | 00001 | A04AQ086-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 086 | Roof Screed | 75 | Light-Weight Concrete Screed |  | 0 |  | 0 |  | 0 |  | 0 | 31 | w/o Welded Wire Fabric |  | 0 | 83 | 30mm≤Min. THK<50mm | 0 | Min. THK=( )mm, Slope=( ) | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A04AQ086 | A04AQ086-00001
|  |  |  | A04AQ086 Finishing Work Roof Work Roof Screed | A04AQ086-00002 Finishing Work Roof Work Roof Screed Light-Weight Concrete Screed w/o Welded Wire Fabric 50mm≤Min. THK<75mm | A04AQ086 | 00002 | A04AQ086-00002 | AR | A04 | Finishing Work | AQ | Roof Work | 086 | Roof Screed | 75 | Light-Weight Concrete Screed |  | 0 |  | 0 |  | 0 |  | 0 | 31 | w/o Welded Wire Fabric |  | 0 | 84 | 50mm≤Min. THK<75mm | 0 | Min. THK=( )mm, Slope=( ) | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A04AQ086 | A04AQ086-00002
|  |  |  | A04AQ086 Finishing Work Roof Work Roof Screed | A04AQ086-00003 Finishing Work Roof Work Roof Screed Light-Weight Concrete Screed w/o Welded Wire Fabric 75mm≤Min. THK | A04AQ086 | 00003 | A04AQ086-00003 | AR | A04 | Finishing Work | AQ | Roof Work | 086 | Roof Screed | 75 | Light-Weight Concrete Screed |  | 0 |  | 0 |  | 0 |  | 0 | 31 | w/o Welded Wire Fabric |  | 0 | 85 | 75mm≤Min. THK | 0 | Min. THK=( )mm, Slope=( ) | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A04AQ086 | A04AQ086-00003
|  |  |  | A04AQ086 Finishing Work Roof Work Roof Screed | A04AQ086-00004 Finishing Work Roof Work Roof Screed Bed Mortar Screed w/o Welded Wire Fabric 30mm≤Min. THK<50mm | A04AQ086 | 00004 | A04AQ086-00004 | AR | A04 | Finishing Work | AQ | Roof Work | 086 | Roof Screed | 76 | Bed Mortar Screed |  | 0 |  | 0 |  | 0 |  | 0 | 31 | w/o Welded Wire Fabric |  | 0 | 83 | 30mm≤Min. THK<50mm | 0 | Min. THK=( )mm, Slope=( ) | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A04AQ086 | A04AQ086-00004
|  |  |  | A04AQ086 Finishing Work Roof Work Roof Screed | A04AQ086-00005 Finishing Work Roof Work Roof Screed Bed Mortar Screed w/o Welded Wire Fabric 50mm≤Min. THK<75mm | A04AQ086 | 00005 | A04AQ086-00005 | AR | A04 | Finishing Work | AQ | Roof Work | 086 | Roof Screed | 76 | Bed Mortar Screed |  | 0 |  | 0 |  | 0 |  | 0 | 31 | w/o Welded Wire Fabric |  | 0 | 84 | 50mm≤Min. THK<75mm | 0 | Min. THK=( )mm, Slope=( ) | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A04AQ086 | A04AQ086-00005
|  |  |  | A04AQ086 Finishing Work Roof Work Roof Screed | A04AQ086-00006 Finishing Work Roof Work Roof Screed Bed Mortar Screed w/o Welded Wire Fabric 75mm≤Min. THK | A04AQ086 | 00006 | A04AQ086-00006 | AR | A04 | Finishing Work | AQ | Roof Work | 086 | Roof Screed | 76 | Bed Mortar Screed |  | 0 |  | 0 |  | 0 |  | 0 | 31 | w/o Welded Wire Fabric |  | 0 | 85 | 75mm≤Min. THK | 0 | Min. THK=( )mm, Slope=( ) | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A04AQ086 | A04AQ086-00006
|  |  |  | A04AQ087 Finishing Work Roof Work Waterproofing Coating | A04AQ087-00001 Finishing Work Roof Work Waterproofing Coating Hot Bitumen only for Roof Area | A04AQ087 | 00001 | A04AQ087-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 087 | Waterproofing Coating | 79 | Hot Bitumen |  | 0 |  | 0 |  | 0 | 05 | only for Roof Area |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ087 | A04AQ087-00001
|  |  |  | A04AQ087 Finishing Work Roof Work Waterproofing Coating | A04AQ087-00002 Finishing Work Roof Work Waterproofing Coating Acrylic Polymer Protective Coating only for Roof Area | A04AQ087 | 00002 | A04AQ087-00002 | AR | A04 | Finishing Work | AQ | Roof Work | 087 | Waterproofing Coating | 80 | Acrylic Polymer Protective Coating |  | 0 |  | 0 |  | 0 | 05 | only for Roof Area |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ087 | A04AQ087-00002
|  |  |  | A04AQ088 Finishing Work Roof Work Roof Insulation | A04AQ088-00001 Finishing Work Roof Work Roof Insulation Rigid Extruded Polystyrene Foam Insulation THK<50mm | A04AQ088 | 00001 | A04AQ088-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 088 | Roof Insulation | 81 | Rigid Extruded Polystyrene Foam Insulation |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 31 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ088 | A04AQ088-00001
|  |  |  | A04AQ088 Finishing Work Roof Work Roof Insulation | A04AQ088-00002 Finishing Work Roof Work Roof Insulation Rigid Extruded Polystyrene Foam Insulation 50mm≤THK<75mm | A04AQ088 | 00002 | A04AQ088-00002 | AR | A04 | Finishing Work | AQ | Roof Work | 088 | Roof Insulation | 81 | Rigid Extruded Polystyrene Foam Insulation |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 09 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ088 | A04AQ088-00002
|  |  |  | A04AQ088 Finishing Work Roof Work Roof Insulation | A04AQ088-00003 Finishing Work Roof Work Roof Insulation Rigid Extruded Polystyrene Foam Insulation 75mm≤THK<100mm | A04AQ088 | 00003 | A04AQ088-00003 | AR | A04 | Finishing Work | AQ | Roof Work | 088 | Roof Insulation | 81 | Rigid Extruded Polystyrene Foam Insulation |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 10 | 75mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ088 | A04AQ088-00003
|  |  |  | A04AQ088 Finishing Work Roof Work Roof Insulation | A04AQ088-00004 Finishing Work Roof Work Roof Insulation Rigid Extruded Polystyrene Foam Insulation 100mm≤THK | A04AQ088 | 00004 | A04AQ088-00004 | AR | A04 | Finishing Work | AQ | Roof Work | 088 | Roof Insulation | 81 | Rigid Extruded Polystyrene Foam Insulation |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 11 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ088 | A04AQ088-00004
|  |  |  | A04AQ089 Finishing Work Roof Work Protective Concrete w/ Steel Trowel Finish | A04AQ089-00001 Finishing Work Roof Work Protective Concrete w/ Steel Trowel Finish | A04AQ089 | 00001 | A04AQ089-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 089 | Protective Concrete w/ Steel Trowel Finish |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A04AQ089 | A04AQ089-00001
|  |  |  | A04AQ090 Finishing Work Roof Work Concrete Tile | A04AQ090-00001 Finishing Work Roof Work Concrete Tile w/ Plastic Spacer THK≤50mm | A04AQ090 | 00001 | A04AQ090-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 090 | Concrete Tile |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 33 | w/ Plastic Spacer |  | 0 | 28 | THK≤50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ090 | A04AQ090-00001
|  |  |  | A04AQ090 Finishing Work Roof Work Concrete Tile | A04AQ090-00002 Finishing Work Roof Work Concrete Tile w/ Plastic Spacer 50mm<THK≤75mm | A04AQ090 | 00002 | A04AQ090-00002 | AR | A04 | Finishing Work | AQ | Roof Work | 090 | Concrete Tile |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 33 | w/ Plastic Spacer |  | 0 | 29 | 50mm<THK≤75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ090 | A04AQ090-00002
|  |  |  | A04AQ090 Finishing Work Roof Work Concrete Tile | A04AQ090-00003 Finishing Work Roof Work Concrete Tile w/ Plastic Spacer 75mm<THK≤100mm | A04AQ090 | 00003 | A04AQ090-00003 | AR | A04 | Finishing Work | AQ | Roof Work | 090 | Concrete Tile |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 33 | w/ Plastic Spacer |  | 0 | 30 | 75mm<THK≤100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ090 | A04AQ090-00003
|  |  |  | A04AQ091 Finishing Work Roof Work Gravel for Roof | A04AQ091-00001 Finishing Work Roof Work Gravel for Roof | A04AQ091 | 00001 | A04AQ091-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 091 | Gravel for Roof |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | THK=( )mmDIA=( )mm~( )mm or Max DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ091 | A04AQ091-00001
|  |  |  | A04AQ092 Finishing Work Roof Work Crushed Stone for Roof | A04AQ092-00001 Finishing Work Roof Work Crushed Stone for Roof | A04AQ092 | 00001 | A04AQ092-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 092 | Crushed Stone for Roof |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | THK=( )mmDIA=( )mm~( )mm or Max DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ092 | A04AQ092-00001
|  |  |  | A04AQ093 Finishing Work Roof Work Clean Sand | A04AQ093-00001 Finishing Work Roof Work Clean Sand | A04AQ093 | 00001 | A04AQ093-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 093 | Clean Sand |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ093 | A04AQ093-00001
|  |  |  | A04AQ094 Finishing Work Roof Work Substrate Board | A04AQ094-00001 Finishing Work Roof Work Substrate Board Water-Resistant Gypsum Substrate w/ Fixing Accessories | A04AQ094 | 00001 | A04AQ094-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 094 | Substrate Board | 82 | Water-Resistant Gypsum Substrate |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 |  |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ094 | A04AQ094-00001
|  |  |  | A04AQ095 Finishing Work Roof Work Geotextile | A04AQ095-00001 Finishing Work Roof Work Geotextile w/ Fixing Accessories | A04AQ095 | 00001 | A04AQ095-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 095 | Geotextile |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ095 | A04AQ095-00001
|  |  |  | A04AQ096 Finishing Work Roof Work Metal Coping for Parapet | A04AQ096-00001 Finishing Work Roof Work Metal Coping for Parapet Galvanized Steel Coping w/ Fixing Accessories, Sealant | A04AQ096 | 00001 | A04AQ096-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 096 | Metal Coping for Parapet | 83 | Galvanized Steel Coping |  | 0 |  | 0 |  | 0 |  | 0 | 35 | w/ Fixing Accessories, Sealant |  | 0 |  |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ096 | A04AQ096-00001
|  |  |  | A04AQ096 Finishing Work Roof Work Metal Coping for Parapet | A04AQ096-00002 Finishing Work Roof Work Metal Coping for Parapet Aluminum Coping w/ Fixing Accessories, Sealant | A04AQ096 | 00002 | A04AQ096-00002 | AR | A04 | Finishing Work | AQ | Roof Work | 096 | Metal Coping for Parapet | 84 | Aluminum Coping |  | 0 |  | 0 |  | 0 |  | 0 | 35 | w/ Fixing Accessories, Sealant |  | 0 |  |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ096 | A04AQ096-00002
|  |  |  | A04AQ096 Finishing Work Roof Work Metal Coping for Parapet | A04AQ096-00003 Finishing Work Roof Work Metal Coping for Parapet Stainless Steel Coping w/ Fixing Accessories, Sealant | A04AQ096 | 00003 | A04AQ096-00003 | AR | A04 | Finishing Work | AQ | Roof Work | 096 | Metal Coping for Parapet | 85 | Stainless Steel Coping |  | 0 |  | 0 |  | 0 |  | 0 | 35 | w/ Fixing Accessories, Sealant |  | 0 |  |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ096 | A04AQ096-00003
|  |  |  | A04AQ097 Finishing Work Roof Work Flashing along Roof Corner | A04AQ097-00001 Finishing Work Roof Work Flashing along Roof Corner Galvanized Steel Flashing w/ Fixing Accessories, Sealant | A04AQ097 | 00001 | A04AQ097-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 097 | Flashing along Roof Corner | 86 | Galvanized Steel Flashing |  | 0 |  | 0 |  | 0 |  | 0 | 35 | w/ Fixing Accessories, Sealant |  | 0 |  |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ097 | A04AQ097-00001
|  |  |  | A04AQ097 Finishing Work Roof Work Flashing along Roof Corner | A04AQ097-00002 Finishing Work Roof Work Flashing along Roof Corner Aluminum Flashing w/ Fixing Accessories, Sealant | A04AQ097 | 00002 | A04AQ097-00002 | AR | A04 | Finishing Work | AQ | Roof Work | 097 | Flashing along Roof Corner | 87 | Aluminum Flashing |  | 0 |  | 0 |  | 0 |  | 0 | 35 | w/ Fixing Accessories, Sealant |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ097 | A04AQ097-00002
|  |  |  | A04AQ097 Finishing Work Roof Work Flashing along Roof Corner | A04AQ097-00003 Finishing Work Roof Work Flashing along Roof Corner Stainless Steel Flashing w/ Fixing Accessories, Sealant | A04AQ097 | 00003 | A04AQ097-00003 | AR | A04 | Finishing Work | AQ | Roof Work | 097 | Flashing along Roof Corner | 88 | Stainless Steel Flashing |  | 0 |  | 0 |  | 0 |  | 0 | 35 | w/ Fixing Accessories, Sealant |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ097 | A04AQ097-00003
|  |  |  | A04AQ310 Finishing Work Roof Work Waterproofing Membrane | A04AQ310-00001 Finishing Work Roof Work Waterproofing Membrane EPDM(or Equivalent) w/ Accessories | A04AQ310 | 00001 | A04AQ310-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 310 | Waterproofing Membrane | 77 | EPDM(or Equivalent) |  | 0 |  | 0 |  | 0 |  | 0 | 32 | w/ Accessories |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ310 | A04AQ310-00001
|  |  |  | A04AQ310 Finishing Work Roof Work Waterproofing Membrane | A04AQ310-00002 Finishing Work Roof Work Waterproofing Membrane EPDM(or Equivalent) with Solar Shield w/ Accessories | A04AQ310 | 00002 | A04AQ310-00002 | AR | A04 | Finishing Work | AQ | Roof Work | 310 | Waterproofing Membrane | 78 | EPDM(or Equivalent) with Solar Shield |  | 0 |  | 0 |  | 0 |  | 0 | 32 | w/ Accessories |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AQ310 | A04AQ310-00002
|  |  |  | A04AR098 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: M2) | A04AR098-00001 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: M2) Fire Protective Rating: N/A w/ Hardware & Accessories | A04AR098 | 00001 | A04AR098-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 098 | Steel Door w/ Steel Frame (UoM: M2) | 89 | Fire Protective Rating: N/A |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR098 | A04AR098-00001
|  |  |  | A04AR098 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: M2) | A04AR098-00002 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | A04AR098 | 00002 | A04AR098-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 098 | Steel Door w/ Steel Frame (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR098 | A04AR098-00002
|  |  |  | A04AR098 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: M2) | A04AR098-00003 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 1-hr w/ Hardware & Accessories | A04AR098 | 00003 | A04AR098-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 098 | Steel Door w/ Steel Frame (UoM: M2) | 95 | Fire Protective Rating: 1-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR098 | A04AR098-00003
|  |  |  | A04AR098 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: M2) | A04AR098-00004 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 1.5-hrs w/ Hardware & Accessories | A04AR098 | 00004 | A04AR098-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 098 | Steel Door w/ Steel Frame (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR098 | A04AR098-00004
|  |  |  | A04AR098 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: M2) | A04AR098-00005 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 2-hrs w/ Hardware & Accessories | A04AR098 | 00005 | A04AR098-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 098 | Steel Door w/ Steel Frame (UoM: M2) | AF | Fire Protective Rating: 2-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR098 | A04AR098-00005
|  |  |  | A04AR098 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: M2) | A04AR098-00006 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 3-hrs w/ Hardware & Accessories | A04AR098 | 00006 | A04AR098-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 098 | Steel Door w/ Steel Frame (UoM: M2) | FH | Fire Protective Rating: 3-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR098 | A04AR098-00006
|  | 00001 | Fire Protective Rating: N/A, Single Door | A04AR099 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) | A04AR099-00001 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | A04AR099 | 00001 | A04AR099-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR099 | A04AR099-00001
00002 | Fire Protective Rating: N/A, Double Door |  |  | A04AR099 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) | A04AR099-00002 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | A04AR099 | 00002 | A04AR099-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR099 | A04AR099-00002
|  | 00003 | Fire Protective Rating: 0.5-hr, Single Door | A04AR099 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) | A04AR099-00003 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 0.5-hr, Single Door w/ Hardware & Accessories | A04AR099 | 00003 | A04AR099-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR099 | A04AR099-00003
00004 | Fire Protective Rating: 0.5-hr, Double Door |  |  | A04AR099 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) | A04AR099-00004 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 0.5-hr, Double Door w/ Hardware & Accessories | A04AR099 | 00004 | A04AR099-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR099 | A04AR099-00004
|  | 00005 | Fire Protective Rating: 1-hr, Single Door | A04AR099 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) | A04AR099-00005 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Single Door w/ Hardware & Accessories | A04AR099 | 00005 | A04AR099-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR099 | A04AR099-00005
00006 | Fire Protective Rating: 1-hr, Double Door |  |  | A04AR099 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) | A04AR099-00006 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | A04AR099 | 00006 | A04AR099-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR099 | A04AR099-00006
|  | 00007 | Fire Protective Rating: 1.5-hrs, Single Door | A04AR099 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) | A04AR099-00007 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1.5-hrs, Single Door w/ Hardware & Accessories | A04AR099 | 00007 | A04AR099-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR099 | A04AR099-00007
00008 | Fire Protective Rating: 1.5-hrs, Double Door |  |  | A04AR099 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) | A04AR099-00008 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1.5-hrs, Double Door w/ Hardware & Accessories | A04AR099 | 00008 | A04AR099-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR099 | A04AR099-00008
|  | 00009 | Fire Protective Rating: 2-hrs, Single Door | A04AR099 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) | A04AR099-00009 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 2-hrs, Single Door w/ Hardware & Accessories | A04AR099 | 00009 | A04AR099-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | AG | Fire Protective Rating: 2-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR099 | A04AR099-00009
00010 | Fire Protective Rating: 2-hrs, Double Door |  |  | A04AR099 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) | A04AR099-00010 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 2-hrs, Double Door w/ Hardware & Accessories | A04AR099 | 00010 | A04AR099-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | AH | Fire Protective Rating: 2-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR099 | A04AR099-00010
|  | 00011 | Fire Protective Rating: 3-hrs, Single Door | A04AR099 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) | A04AR099-00011 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 3-hrs, Single Door w/ Hardware & Accessories | A04AR099 | 00011 | A04AR099-00011 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | FJ | Fire Protective Rating: 3-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR099 | A04AR099-00011
00012 | Fire Protective Rating: 3-hrs, Double Door |  |  | A04AR099 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) | A04AR099-00012 Finishing Work Door & Window Work Steel Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 3-hrs, Double Door w/ Hardware & Accessories | A04AR099 | 00012 | A04AR099-00012 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | FK | Fire Protective Rating: 3-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR099 | A04AR099-00012
|  |  |  | A04AR100 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | A04AR100-00001 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) Fire Protective Rating: N/A w/ Hardware & Accessories | A04AR100 | 00001 | A04AR100-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 100 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | 89 | Fire Protective Rating: N/A |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR100 | A04AR100-00001
|  |  |  | A04AR100 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | A04AR100-00002 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | A04AR100 | 00002 | A04AR100-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 100 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR100 | A04AR100-00002
|  |  |  | A04AR100 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | A04AR100-00003 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) Fire Protective Rating: 1-hr w/ Hardware & Accessories | A04AR100 | 00003 | A04AR100-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 100 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | 95 | Fire Protective Rating: 1-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR100 | A04AR100-00003
|  |  |  | A04AR100 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | A04AR100-00004 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) Fire Protective Rating: 1.5-hrs w/ Hardware & Accessories | A04AR100 | 00004 | A04AR100-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 100 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR100 | A04AR100-00004
|  |  |  | A04AR100 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | A04AR100-00005 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) Fire Protective Rating: 2-hrs w/ Hardware & Accessories | A04AR100 | 00005 | A04AR100-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 100 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | AF | Fire Protective Rating: 2-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR100 | A04AR100-00005
|  |  |  | A04AR100 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | A04AR100-00006 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) Fire Protective Rating: 3-hrs w/ Hardware & Accessories | A04AR100 | 00006 | A04AR100-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 100 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | FH | Fire Protective Rating: 3-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR100 | A04AR100-00006
|  | 00001 | Fire Protective Rating: N/A, Single Door | A04AR101 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR101-00001 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | A04AR101 | 00001 | A04AR101-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR101 | A04AR101-00001
00002 | Fire Protective Rating: N/A, Double Door |  |  | A04AR101 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR101-00002 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | A04AR101 | 00002 | A04AR101-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR101 | A04AR101-00002
|  | 00003 | Fire Protective Rating: 0.5-hr, Single Door | A04AR101 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR101-00003 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 0.5-hr, Single Door w/ Hardware & Accessories | A04AR101 | 00003 | A04AR101-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR101 | A04AR101-00003
00004 | Fire Protective Rating: 0.5-hr, Double Door |  |  | A04AR101 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR101-00004 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 0.5-hr, Double Door w/ Hardware & Accessories | A04AR101 | 00004 | A04AR101-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR101 | A04AR101-00004
|  | 00005 | Fire Protective Rating: 1-hr, Single Door | A04AR101 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR101-00005 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1-hr, Single Door w/ Hardware & Accessories | A04AR101 | 00005 | A04AR101-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR101 | A04AR101-00005
00006 | Fire Protective Rating: 1-hr, Double Door |  |  | A04AR101 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR101-00006 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | A04AR101 | 00006 | A04AR101-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR101 | A04AR101-00006
|  | 00007 | Fire Protective Rating: 1.5-hrs, Single Door | A04AR101 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR101-00007 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1.5-hrs, Single Door w/ Hardware & Accessories | A04AR101 | 00007 | A04AR101-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR101 | A04AR101-00007
00008 | Fire Protective Rating: 1.5-hrs, Double Door |  |  | A04AR101 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR101-00008 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1.5-hrs, Double Door w/ Hardware & Accessories | A04AR101 | 00008 | A04AR101-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR101 | A04AR101-00008
|  | 00009 | Fire Protective Rating: 2-hrs, Single Door | A04AR101 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR101-00009 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 2-hrs, Single Door w/ Hardware & Accessories | A04AR101 | 00009 | A04AR101-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | AG | Fire Protective Rating: 2-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR101 | A04AR101-00009
00010 | Fire Protective Rating: 2-hrs, Double Door |  |  | A04AR101 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR101-00010 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 2-hrs, Double Door w/ Hardware & Accessories | A04AR101 | 00010 | A04AR101-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | AH | Fire Protective Rating: 2-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR101 | A04AR101-00010
|  | 00011 | Fire Protective Rating: 3-hrs, Single Door | A04AR101 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR101-00011 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 3-hrs, Single Door w/ Hardware & Accessories | A04AR101 | 00011 | A04AR101-00011 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | FJ | Fire Protective Rating: 3-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR101 | A04AR101-00011
00012 | Fire Protective Rating: 3-hrs, Double Door |  |  | A04AR101 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR101-00012 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 3-hrs, Double Door w/ Hardware & Accessories | A04AR101 | 00012 | A04AR101-00012 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | FK | Fire Protective Rating: 3-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR101 | A04AR101-00012
|  |  |  | A04AR102 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | A04AR102-00001 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: M2) Fire Protective Rating: N/A w/ Hardware & Accessories | A04AR102 | 00001 | A04AR102-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 102 | Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | 89 | Fire Protective Rating: N/A |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR102 | A04AR102-00001
|  |  |  | A04AR102 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | A04AR102-00002 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: M2) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | A04AR102 | 00002 | A04AR102-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 102 | Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR102 | A04AR102-00002
|  |  |  | A04AR102 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | A04AR102-00003 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: M2) Fire Protective Rating: 1-hr w/ Hardware & Accessories | A04AR102 | 00003 | A04AR102-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 102 | Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | 95 | Fire Protective Rating: 1-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR102 | A04AR102-00003
|  |  |  | A04AR102 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | A04AR102-00004 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: M2) Fire Protective Rating: 1.5-hrs w/ Hardware & Accessories | A04AR102 | 00004 | A04AR102-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 102 | Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR102 | A04AR102-00004
|  |  |  | A04AR102 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | A04AR102-00005 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: M2) Fire Protective Rating: 2-hrs w/ Hardware & Accessories | A04AR102 | 00005 | A04AR102-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 102 | Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | AF | Fire Protective Rating: 2-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR102 | A04AR102-00005
|  |  |  | A04AR102 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | A04AR102-00006 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: M2) Fire Protective Rating: 3-hrs w/ Hardware & Accessories | A04AR102 | 00006 | A04AR102-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 102 | Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | FH | Fire Protective Rating: 3-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR102 | A04AR102-00006
|  | 00001 | Fire Protective Rating: N/A, Single Door | A04AR103 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | A04AR103-00001 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | A04AR103 | 00001 | A04AR103-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR103 | A04AR103-00001
00002 | Fire Protective Rating: N/A, Double Door |  |  | A04AR103 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | A04AR103-00002 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | A04AR103 | 00002 | A04AR103-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR103 | A04AR103-00002
|  | 00003 | Fire Protective Rating: 0.5-hr, Single Door | A04AR103 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | A04AR103-00003 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: 0.5-hr, Single Door w/ Hardware & Accessories | A04AR103 | 00003 | A04AR103-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR103 | A04AR103-00003
00004 | Fire Protective Rating: 0.5-hr, Double Door |  |  | A04AR103 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | A04AR103-00004 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: 0.5-hr, Double Door w/ Hardware & Accessories | A04AR103 | 00004 | A04AR103-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR103 | A04AR103-00004
|  | 00005 | Fire Protective Rating: 1-hr, Single Door | A04AR103 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | A04AR103-00005 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: 1-hr, Single Door w/ Hardware & Accessories | A04AR103 | 00005 | A04AR103-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR103 | A04AR103-00005
00006 | Fire Protective Rating: 1-hr, Double Door |  |  | A04AR103 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | A04AR103-00006 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | A04AR103 | 00006 | A04AR103-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR103 | A04AR103-00006
|  | 00007 | Fire Protective Rating: 1.5-hrs, Single Door | A04AR103 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | A04AR103-00007 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: 1.5-hrs, Single Door w/ Hardware & Accessories | A04AR103 | 00007 | A04AR103-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR103 | A04AR103-00007
00008 | Fire Protective Rating: 1.5-hrs, Double Door |  |  | A04AR103 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | A04AR103-00008 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: 1.5-hrs, Double Door w/ Hardware & Accessories | A04AR103 | 00008 | A04AR103-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR103 | A04AR103-00008
|  | 00009 | Fire Protective Rating: 2-hrs, Single Door | A04AR103 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | A04AR103-00009 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: 2-hrs, Single Door w/ Hardware & Accessories | A04AR103 | 00009 | A04AR103-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | AG | Fire Protective Rating: 2-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR103 | A04AR103-00009
00010 | Fire Protective Rating: 2-hrs, Double Door |  |  | A04AR103 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | A04AR103-00010 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: 2-hrs, Double Door w/ Hardware & Accessories | A04AR103 | 00010 | A04AR103-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | AH | Fire Protective Rating: 2-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR103 | A04AR103-00010
|  | 00011 | Fire Protective Rating: 3-hrs, Single Door | A04AR103 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | A04AR103-00011 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: 3-hrs, Single Door w/ Hardware & Accessories | A04AR103 | 00011 | A04AR103-00011 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | FJ | Fire Protective Rating: 3-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR103 | A04AR103-00011
00012 | Fire Protective Rating: 3-hrs, Double Door |  |  | A04AR103 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | A04AR103-00012 Finishing Work Door & Window Work Steel Door w/ Steel Frame & Panic Bar (UoM: EA) Fire Protective Rating: 3-hrs, Double Door w/ Hardware & Accessories | A04AR103 | 00012 | A04AR103-00012 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | FK | Fire Protective Rating: 3-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR103 | A04AR103-00012
|  |  |  | A04AR104 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | A04AR104-00001 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) Fire Protective Rating: N/A w/ Hardware & Accessories | A04AR104 | 00001 | A04AR104-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 104 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | 89 | Fire Protective Rating: N/A |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR104 | A04AR104-00001
|  |  |  | A04AR104 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | A04AR104-00002 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | A04AR104 | 00002 | A04AR104-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 104 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR104 | A04AR104-00002
|  |  |  | A04AR104 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | A04AR104-00003 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) Fire Protective Rating: 1-hr w/ Hardware & Accessories | A04AR104 | 00003 | A04AR104-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 104 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | 95 | Fire Protective Rating: 1-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR104 | A04AR104-00003
|  |  |  | A04AR104 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | A04AR104-00004 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) Fire Protective Rating: 1.5-hrs w/ Hardware & Accessories | A04AR104 | 00004 | A04AR104-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 104 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR104 | A04AR104-00004
|  |  |  | A04AR104 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | A04AR104-00005 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) Fire Protective Rating: 2-hrs w/ Hardware & Accessories | A04AR104 | 00005 | A04AR104-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 104 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | AF | Fire Protective Rating: 2-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR104 | A04AR104-00005
|  | 00001 | Fire Protective Rating: N/A, Single Door | A04AR105 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR105-00001 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | A04AR105 | 00001 | A04AR105-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR105 | A04AR105-00001
00002 | Fire Protective Rating: N/A, Double Door |  |  | A04AR105 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR105-00002 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | A04AR105 | 00002 | A04AR105-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR105 | A04AR105-00002
|  | 00003 | Fire Protective Rating: 0.5-hr, Single Door | A04AR105 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR105-00003 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 0.5-hr, Single Door w/ Hardware & Accessories | A04AR105 | 00003 | A04AR105-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR105 | A04AR105-00003
00004 | Fire Protective Rating: 0.5-hr, Double Door |  |  | A04AR105 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR105-00004 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 0.5-hr, Double Door w/ Hardware & Accessories | A04AR105 | 00004 | A04AR105-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR105 | A04AR105-00004
|  | 00005 | Fire Protective Rating: 1-hr, Single Door | A04AR105 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR105-00005 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1-hr, Single Door w/ Hardware & Accessories | A04AR105 | 00005 | A04AR105-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR105 | A04AR105-00005
00006 | Fire Protective Rating: 1-hr, Double Door |  |  | A04AR105 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR105-00006 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | A04AR105 | 00006 | A04AR105-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR105 | A04AR105-00006
|  | 00007 | Fire Protective Rating: 1.5-hrs, Single Door | A04AR105 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR105-00007 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1.5-hrs, Single Door w/ Hardware & Accessories | A04AR105 | 00007 | A04AR105-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR105 | A04AR105-00007
00008 | Fire Protective Rating: 1.5-hrs, Double Door |  |  | A04AR105 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR105-00008 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1.5-hrs, Double Door w/ Hardware & Accessories | A04AR105 | 00008 | A04AR105-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR105 | A04AR105-00008
|  | 00009 | Fire Protective Rating: 2-hrs, Single Door | A04AR105 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR105-00009 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 2-hrs, Single Door w/ Hardware & Accessories | A04AR105 | 00009 | A04AR105-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AG | Fire Protective Rating: 2-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR105 | A04AR105-00009
00010 | Fire Protective Rating: 2-hrs, Double Door |  |  | A04AR105 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR105-00010 Finishing Work Door & Window Work Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 2-hrs, Double Door w/ Hardware & Accessories | A04AR105 | 00010 | A04AR105-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AH | Fire Protective Rating: 2-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR105 | A04AR105-00010
|  |  |  | A04AR106 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: M2) | A04AR106-00001 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: M2) Fire Protective Rating: N/A w/ Hardware & Accessories | A04AR106 | 00001 | A04AR106-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 106 | Blast Resistant Door w/ Steel Frame (UoM: M2) | 89 | Fire Protective Rating: N/A |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR106 | A04AR106-00001
|  |  |  | A04AR106 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: M2) | A04AR106-00002 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | A04AR106 | 00002 | A04AR106-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 106 | Blast Resistant Door w/ Steel Frame (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR106 | A04AR106-00002
|  |  |  | A04AR106 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: M2) | A04AR106-00003 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 1-hr w/ Hardware & Accessories | A04AR106 | 00003 | A04AR106-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 106 | Blast Resistant Door w/ Steel Frame (UoM: M2) | 95 | Fire Protective Rating: 1-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR106 | A04AR106-00003
|  |  |  | A04AR106 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: M2) | A04AR106-00004 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 1.5-hrs w/ Hardware & Accessories | A04AR106 | 00004 | A04AR106-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 106 | Blast Resistant Door w/ Steel Frame (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR106 | A04AR106-00004
|  |  |  | A04AR106 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: M2) | A04AR106-00005 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 2-hrs w/ Hardware & Accessories | A04AR106 | 00005 | A04AR106-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 106 | Blast Resistant Door w/ Steel Frame (UoM: M2) | AF | Fire Protective Rating: 2-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR106 | A04AR106-00005
|  |  |  | A04AR106 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: M2) | A04AR106-00006 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 3-hrs w/ Hardware & Accessories | A04AR106 | 00006 | A04AR106-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 106 | Blast Resistant Door w/ Steel Frame (UoM: M2) | FH | Fire Protective Rating: 3-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR106 | A04AR106-00006
|  | 00001 | Fire Protective Rating: N/A, Single Door | A04AR107 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) | A04AR107-00001 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | A04AR107 | 00001 | A04AR107-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR107 | A04AR107-00001
00002 | Fire Protective Rating: N/A, Double Door |  |  | A04AR107 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) | A04AR107-00002 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | A04AR107 | 00002 | A04AR107-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR107 | A04AR107-00002
|  | 00003 | Fire Protective Rating: 0.5-hr, Single Door | A04AR107 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) | A04AR107-00003 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 0.5-hr, Single Door w/ Hardware & Accessories | A04AR107 | 00003 | A04AR107-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR107 | A04AR107-00003
00004 | Fire Protective Rating: 0.5-hr, Double Door |  |  | A04AR107 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) | A04AR107-00004 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 0.5-hr, Double Door w/ Hardware & Accessories | A04AR107 | 00004 | A04AR107-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR107 | A04AR107-00004
|  | 00005 | Fire Protective Rating: 1-hr, Single Door | A04AR107 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) | A04AR107-00005 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Single Door w/ Hardware & Accessories | A04AR107 | 00005 | A04AR107-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR107 | A04AR107-00005
00006 | Fire Protective Rating: 1-hr, Double Door |  |  | A04AR107 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) | A04AR107-00006 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | A04AR107 | 00006 | A04AR107-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR107 | A04AR107-00006
|  | 00007 | Fire Protective Rating: 1.5-hrs, Single Door | A04AR107 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) | A04AR107-00007 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1.5-hrs, Single Door w/ Hardware & Accessories | A04AR107 | 00007 | A04AR107-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR107 | A04AR107-00007
00008 | Fire Protective Rating: 1.5-hrs, Double Door |  |  | A04AR107 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) | A04AR107-00008 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1.5-hrs, Double Door w/ Hardware & Accessories | A04AR107 | 00008 | A04AR107-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR107 | A04AR107-00008
|  | 00009 | Fire Protective Rating: 2-hrs, Single Door | A04AR107 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) | A04AR107-00009 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 2-hrs, Single Door w/ Hardware & Accessories | A04AR107 | 00009 | A04AR107-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | AG | Fire Protective Rating: 2-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR107 | A04AR107-00009
00010 | Fire Protective Rating: 2-hrs, Double Door |  |  | A04AR107 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) | A04AR107-00010 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 2-hrs, Double Door w/ Hardware & Accessories | A04AR107 | 00010 | A04AR107-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | AH | Fire Protective Rating: 2-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR107 | A04AR107-00010
|  | 00011 | Fire Protective Rating: 3-hrs, Single Door | A04AR107 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) | A04AR107-00011 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 3-hrs, Single Door w/ Hardware & Accessories | A04AR107 | 00011 | A04AR107-00011 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | FJ | Fire Protective Rating: 3-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR107 | A04AR107-00011
00012 | Fire Protective Rating: 3-hrs, Double Door |  |  | A04AR107 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) | A04AR107-00012 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 3-hrs, Double Door w/ Hardware & Accessories | A04AR107 | 00012 | A04AR107-00012 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | FK | Fire Protective Rating: 3-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR107 | A04AR107-00012
|  |  |  | A04AR108 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | A04AR108-00001 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) Fire Protective Rating: N/A w/ Hardware & Accessories | A04AR108 | 00001 | A04AR108-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 108 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | 89 | Fire Protective Rating: N/A |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR108 | A04AR108-00001
|  |  |  | A04AR108 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | A04AR108-00002 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | A04AR108 | 00002 | A04AR108-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 108 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR108 | A04AR108-00002
|  |  |  | A04AR108 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | A04AR108-00003 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) Fire Protective Rating: 1-hr w/ Hardware & Accessories | A04AR108 | 00003 | A04AR108-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 108 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | 95 | Fire Protective Rating: 1-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR108 | A04AR108-00003
|  |  |  | A04AR108 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | A04AR108-00004 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) Fire Protective Rating: 1.5-hrs w/ Hardware & Accessories | A04AR108 | 00004 | A04AR108-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 108 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR108 | A04AR108-00004
|  |  |  | A04AR108 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | A04AR108-00005 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) Fire Protective Rating: 2-hrs w/ Hardware & Accessories | A04AR108 | 00005 | A04AR108-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 108 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | AF | Fire Protective Rating: 2-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR108 | A04AR108-00005
|  |  |  | A04AR108 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | A04AR108-00006 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) Fire Protective Rating: 3-hrs w/ Hardware & Accessories | A04AR108 | 00006 | A04AR108-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 108 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | FH | Fire Protective Rating: 3-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR108 | A04AR108-00006
|  | 00001 | Fire Protective Rating: N/A, Single Door | A04AR109 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR109-00001 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | A04AR109 | 00001 | A04AR109-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR109 | A04AR109-00001
00002 | Fire Protective Rating: N/A, Double Door |  |  | A04AR109 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR109-00002 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | A04AR109 | 00002 | A04AR109-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR109 | A04AR109-00002
|  | 00003 | Fire Protective Rating: 0.5-hr, Single Door | A04AR109 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR109-00003 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 0.5-hr, Single Door w/ Hardware & Accessories | A04AR109 | 00003 | A04AR109-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR109 | A04AR109-00003
00004 | Fire Protective Rating: 0.5-hr, Double Door |  |  | A04AR109 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR109-00004 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 0.5-hr, Double Door w/ Hardware & Accessories | A04AR109 | 00004 | A04AR109-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR109 | A04AR109-00004
|  | 00005 | Fire Protective Rating: 1-hr, Single Door | A04AR109 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR109-00005 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 1-hr, Single Door w/ Hardware & Accessories | A04AR109 | 00005 | A04AR109-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR109 | A04AR109-00005
00006 | Fire Protective Rating: 1-hr, Double Door |  |  | A04AR109 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR109-00006 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | A04AR109 | 00006 | A04AR109-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR109 | A04AR109-00006
|  | 00007 | Fire Protective Rating: 1.5-hrs, Single Door | A04AR109 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR109-00007 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 1.5-hrs, Single Door w/ Hardware & Accessories | A04AR109 | 00007 | A04AR109-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR109 | A04AR109-00007
00008 | Fire Protective Rating: 1.5-hrs, Double Door |  |  | A04AR109 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR109-00008 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 1.5-hrs, Double Door w/ Hardware & Accessories | A04AR109 | 00008 | A04AR109-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR109 | A04AR109-00008
|  | 00009 | Fire Protective Rating: 2-hrs, Single Door | A04AR109 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR109-00009 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 2-hrs, Single Door w/ Hardware & Accessories | A04AR109 | 00009 | A04AR109-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AG | Fire Protective Rating: 2-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR109 | A04AR109-00009
00010 | Fire Protective Rating: 2-hrs, Double Door |  |  | A04AR109 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR109-00010 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 2-hrs, Double Door w/ Hardware & Accessories | A04AR109 | 00010 | A04AR109-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AH | Fire Protective Rating: 2-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR109 | A04AR109-00010
|  | 00011 | Fire Protective Rating: 3-hrs, Single Door | A04AR109 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR109-00011 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 3-hrs, Single Door w/ Hardware & Accessories | A04AR109 | 00011 | A04AR109-00011 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | FJ | Fire Protective Rating: 3-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR109 | A04AR109-00011
00012 | Fire Protective Rating: 3-hrs, Double Door |  |  | A04AR109 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR109-00012 Finishing Work Door & Window Work Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 3-hrs, Double Door w/ Hardware & Accessories | A04AR109 | 00012 | A04AR109-00012 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | FK | Fire Protective Rating: 3-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR109 | A04AR109-00012
|  |  |  | A04AR110 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: M2) | A04AR110-00001 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: M2) Fire Protective Rating: N/A w/ Hardware & Accessories | A04AR110 | 00001 | A04AR110-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 110 | Aluminum Door w/ Aluminum Frame (UoM: M2) | 89 | Fire Protective Rating: N/A |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR110 | A04AR110-00001
|  |  |  | A04AR110 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: M2) | A04AR110-00002 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: M2) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | A04AR110 | 00002 | A04AR110-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 110 | Aluminum Door w/ Aluminum Frame (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR110 | A04AR110-00002
|  |  |  | A04AR110 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: M2) | A04AR110-00003 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: M2) Fire Protective Rating: 1-hr w/ Hardware & Accessories | A04AR110 | 00003 | A04AR110-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 110 | Aluminum Door w/ Aluminum Frame (UoM: M2) | 95 | Fire Protective Rating: 1-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR110 | A04AR110-00003
|  |  |  | A04AR110 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: M2) | A04AR110-00004 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: M2) Fire Protective Rating: 1.5-hrs w/ Hardware & Accessories | A04AR110 | 00004 | A04AR110-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 110 | Aluminum Door w/ Aluminum Frame (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR110 | A04AR110-00004
|  | 00001 | Fire Protective Rating: N/A, Single Door | A04AR111 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) | A04AR111-00001 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | A04AR111 | 00001 | A04AR111-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 111 | Aluminum Door w/ Aluminum Frame (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR111 | A04AR111-00001
00002 | Fire Protective Rating: N/A, Double Door |  |  | A04AR111 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) | A04AR111-00002 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | A04AR111 | 00002 | A04AR111-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 111 | Aluminum Door w/ Aluminum Frame (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR111 | A04AR111-00002
|  | 00003 | Fire Protective Rating: 0.5-hr, Single Door | A04AR111 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) | A04AR111-00003 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: 0.5-hr, Single Door w/ Hardware & Accessories | A04AR111 | 00003 | A04AR111-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 111 | Aluminum Door w/ Aluminum Frame (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR111 | A04AR111-00003
00004 | Fire Protective Rating: 0.5-hr, Double Door |  |  | A04AR111 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) | A04AR111-00004 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: 0.5-hr, Double Door w/ Hardware & Accessories | A04AR111 | 00004 | A04AR111-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 111 | Aluminum Door w/ Aluminum Frame (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR111 | A04AR111-00004
|  | 00005 | Fire Protective Rating: 1-hr, Single Door | A04AR111 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) | A04AR111-00005 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: 1-hr, Single Door w/ Hardware & Accessories | A04AR111 | 00005 | A04AR111-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 111 | Aluminum Door w/ Aluminum Frame (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR111 | A04AR111-00005
00006 | Fire Protective Rating: 1-hr, Double Door |  |  | A04AR111 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) | A04AR111-00006 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | A04AR111 | 00006 | A04AR111-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 111 | Aluminum Door w/ Aluminum Frame (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR111 | A04AR111-00006
|  | 00007 | Fire Protective Rating: 1.5-hrs, Single Door | A04AR111 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) | A04AR111-00007 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: 1.5-hrs, Single Door w/ Hardware & Accessories | A04AR111 | 00007 | A04AR111-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 111 | Aluminum Door w/ Aluminum Frame (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR111 | A04AR111-00007
00008 | Fire Protective Rating: 1.5-hrs, Double Door |  |  | A04AR111 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) | A04AR111-00008 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: 1.5-hrs, Double Door w/ Hardware & Accessories | A04AR111 | 00008 | A04AR111-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 111 | Aluminum Door w/ Aluminum Frame (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR111 | A04AR111-00008
|  |  |  | A04AR112 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: M2) | A04AR112-00001 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: M2) Fire Protective Rating: N/A w/ Hardware & Accessories | A04AR112 | 00001 | A04AR112-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 112 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: M2) | 89 | Fire Protective Rating: N/A |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR112 | A04AR112-00001
|  |  |  | A04AR112 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: M2) | A04AR112-00002 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: M2) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | A04AR112 | 00002 | A04AR112-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 112 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR112 | A04AR112-00002
|  |  |  | A04AR112 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: M2) | A04AR112-00003 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: M2) Fire Protective Rating: 1-hr w/ Hardware & Accessories | A04AR112 | 00003 | A04AR112-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 112 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: M2) | 95 | Fire Protective Rating: 1-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR112 | A04AR112-00003
|  |  |  | A04AR112 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: M2) | A04AR112-00004 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: M2) Fire Protective Rating: 1.5-hrs w/ Hardware & Accessories | A04AR112 | 00004 | A04AR112-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 112 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR112 | A04AR112-00004
|  | 00001 | Fire Protective Rating: N/A, Single Door | A04AR113 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR113-00001 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | A04AR113 | 00001 | A04AR113-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 113 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR113 | A04AR113-00001
00002 | Fire Protective Rating: N/A, Double Door |  |  | A04AR113 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR113-00002 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | A04AR113 | 00002 | A04AR113-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 113 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR113 | A04AR113-00002
|  | 00003 | Fire Protective Rating: 0.5-hr, Single Door | A04AR113 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR113-00003 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 0.5-hr, Single Door w/ Hardware & Accessories | A04AR113 | 00003 | A04AR113-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 113 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR113 | A04AR113-00003
00004 | Fire Protective Rating: 0.5-hr, Double Door |  |  | A04AR113 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR113-00004 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 0.5-hr, Double Door w/ Hardware & Accessories | A04AR113 | 00004 | A04AR113-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 113 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR113 | A04AR113-00004
|  | 00005 | Fire Protective Rating: 1-hr, Single Door | A04AR113 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR113-00005 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1-hr, Single Door w/ Hardware & Accessories | A04AR113 | 00005 | A04AR113-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 113 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR113 | A04AR113-00005
00006 | Fire Protective Rating: 1-hr, Double Door |  |  | A04AR113 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR113-00006 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | A04AR113 | 00006 | A04AR113-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 113 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR113 | A04AR113-00006
|  | 00007 | Fire Protective Rating: 1.5-hrs, Single Door | A04AR113 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR113-00007 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1.5-hrs, Single Door w/ Hardware & Accessories | A04AR113 | 00007 | A04AR113-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 113 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR113 | A04AR113-00007
00008 | Fire Protective Rating: 1.5-hrs, Double Door |  |  | A04AR113 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR113-00008 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1.5-hrs, Double Door w/ Hardware & Accessories | A04AR113 | 00008 | A04AR113-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 113 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR113 | A04AR113-00008
|  |  |  | A04AR114 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: M2) | A04AR114-00001 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: M2) Fire Protective Rating: N/A w/ Hardware & Accessories | A04AR114 | 00001 | A04AR114-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 114 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: M2) | 89 | Fire Protective Rating: N/A |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR114 | A04AR114-00001
|  |  |  | A04AR114 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: M2) | A04AR114-00002 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: M2) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | A04AR114 | 00002 | A04AR114-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 114 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR114 | A04AR114-00002
|  |  |  | A04AR114 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: M2) | A04AR114-00003 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: M2) Fire Protective Rating: 1-hr w/ Hardware & Accessories | A04AR114 | 00003 | A04AR114-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 114 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: M2) | 95 | Fire Protective Rating: 1-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR114 | A04AR114-00003
|  |  |  | A04AR114 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: M2) | A04AR114-00004 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: M2) Fire Protective Rating: 1.5-hrs w/ Hardware & Accessories | A04AR114 | 00004 | A04AR114-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 114 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR114 | A04AR114-00004
|  | 00001 | Fire Protective Rating: N/A, Single Door | A04AR115 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | A04AR115-00001 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | A04AR115 | 00001 | A04AR115-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 115 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR115 | A04AR115-00001
00002 | Fire Protective Rating: N/A, Double Door |  |  | A04AR115 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | A04AR115-00002 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | A04AR115 | 00002 | A04AR115-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 115 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR115 | A04AR115-00002
|  | 00003 | Fire Protective Rating: 0.5-hr, Single Door | A04AR115 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | A04AR115-00003 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) Fire Protective Rating: 0.5-hr, Single Door w/ Hardware & Accessories | A04AR115 | 00003 | A04AR115-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 115 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR115 | A04AR115-00003
00004 | Fire Protective Rating: 0.5-hr, Double Door |  |  | A04AR115 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | A04AR115-00004 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) Fire Protective Rating: 0.5-hr, Double Door w/ Hardware & Accessories | A04AR115 | 00004 | A04AR115-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 115 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR115 | A04AR115-00004
|  | 00005 | Fire Protective Rating: 1-hr, Single Door | A04AR115 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | A04AR115-00005 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) Fire Protective Rating: 1-hr, Single Door w/ Hardware & Accessories | A04AR115 | 00005 | A04AR115-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 115 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR115 | A04AR115-00005
00006 | Fire Protective Rating: 1-hr, Double Door |  |  | A04AR115 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | A04AR115-00006 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | A04AR115 | 00006 | A04AR115-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 115 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR115 | A04AR115-00006
|  | 00007 | Fire Protective Rating: 1.5-hrs, Single Door | A04AR115 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | A04AR115-00007 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) Fire Protective Rating: 1.5-hrs, Single Door w/ Hardware & Accessories | A04AR115 | 00007 | A04AR115-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 115 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR115 | A04AR115-00007
00008 | Fire Protective Rating: 1.5-hrs, Double Door |  |  | A04AR115 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | A04AR115-00008 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) Fire Protective Rating: 1.5-hrs, Double Door w/ Hardware & Accessories | A04AR115 | 00008 | A04AR115-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 115 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR115 | A04AR115-00008
|  |  |  | A04AR116 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leafr (UoM: M2) | A04AR116-00001 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leafr (UoM: M2) Fire Protective Rating: N/A w/ Hardware & Accessories | A04AR116 | 00001 | A04AR116-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 116 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leafr (UoM: M2) | 89 | Fire Protective Rating: N/A |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR116 | A04AR116-00001
|  |  |  | A04AR116 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leafr (UoM: M2) | A04AR116-00002 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leafr (UoM: M2) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | A04AR116 | 00002 | A04AR116-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 116 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leafr (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR116 | A04AR116-00002
|  |  |  | A04AR116 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leafr (UoM: M2) | A04AR116-00003 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leafr (UoM: M2) Fire Protective Rating: 1-hr w/ Hardware & Accessories | A04AR116 | 00003 | A04AR116-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 116 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leafr (UoM: M2) | 95 | Fire Protective Rating: 1-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR116 | A04AR116-00003
|  |  |  | A04AR116 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leafr (UoM: M2) | A04AR116-00004 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leafr (UoM: M2) Fire Protective Rating: 1.5-hrs w/ Hardware & Accessories | A04AR116 | 00004 | A04AR116-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 116 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leafr (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR116 | A04AR116-00004
|  | 00001 | Fire Protective Rating: N/A, Single Door | A04AR117 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR117-00001 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | A04AR117 | 00001 | A04AR117-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 117 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR117 | A04AR117-00001
00002 | Fire Protective Rating: N/A, Double Door |  |  | A04AR117 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR117-00002 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | A04AR117 | 00002 | A04AR117-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 117 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR117 | A04AR117-00002
|  | 00003 | Fire Protective Rating: 0.5-hr, Single Door | A04AR117 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR117-00003 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 0.5-hr, Single Door w/ Hardware & Accessories | A04AR117 | 00003 | A04AR117-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 117 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR117 | A04AR117-00003
00004 | Fire Protective Rating: 0.5-hr, Double Door |  |  | A04AR117 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR117-00004 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 0.5-hr, Double Door w/ Hardware & Accessories | A04AR117 | 00004 | A04AR117-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 117 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR117 | A04AR117-00004
|  | 00005 | Fire Protective Rating: 1-hr, Single Door | A04AR117 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR117-00005 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1-hr, Single Door w/ Hardware & Accessories | A04AR117 | 00005 | A04AR117-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 117 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR117 | A04AR117-00005
00006 | Fire Protective Rating: 1-hr, Double Door |  |  | A04AR117 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR117-00006 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | A04AR117 | 00006 | A04AR117-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 117 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR117 | A04AR117-00006
|  | 00007 | Fire Protective Rating: 1.5-hrs, Single Door | A04AR117 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR117-00007 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1.5-hrs, Single Door w/ Hardware & Accessories | A04AR117 | 00007 | A04AR117-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 117 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR117 | A04AR117-00007
00008 | Fire Protective Rating: 1.5-hrs, Double Door |  |  | A04AR117 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | A04AR117-00008 Finishing Work Door & Window Work Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) Fire Protective Rating: 1.5-hrs, Double Door w/ Hardware & Accessories | A04AR117 | 00008 | A04AR117-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 117 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR117 | A04AR117-00008
|  |  |  | A04AR118 Finishing Work Door & Window Work Glass Door w/ SST Frame (UoM: M2) | A04AR118-00001 Finishing Work Door & Window Work Glass Door w/ SST Frame (UoM: M2) w/ Hardware & Accessories | A04AR118 | 00001 | A04AR118-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 118 | Glass Door w/ SST Frame (UoM: M2) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR118 | A04AR118-00001
|  | 00001 | Single Door | A04AR119 Finishing Work Door & Window Work Glass Door w/ SST Frame (UoM: EA) | A04AR119-00001 Finishing Work Door & Window Work Glass Door w/ SST Frame (UoM: EA) Single Door w/ Hardware & Accessories | A04AR119 | 00001 | A04AR119-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 119 | Glass Door w/ SST Frame (UoM: EA) | AJ | Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR119 | A04AR119-00001
00002 | Double Door |  |  | A04AR119 Finishing Work Door & Window Work Glass Door w/ SST Frame (UoM: EA) | A04AR119-00002 Finishing Work Door & Window Work Glass Door w/ SST Frame (UoM: EA) Double Door w/ Hardware & Accessories | A04AR119 | 00002 | A04AR119-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 119 | Glass Door w/ SST Frame (UoM: EA) | AK | Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR119 | A04AR119-00002
|  |  |  | A04AR120 Finishing Work Door & Window Work Stainless Steel Door w/ SST Frame (UoM: M2) | A04AR120-00001 Finishing Work Door & Window Work Stainless Steel Door w/ SST Frame (UoM: M2) w/ Hardware & Accessories | A04AR120 | 00001 | A04AR120-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 120 | Stainless Steel Door w/ SST Frame (UoM: M2) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR120 | A04AR120-00001
|  | 00001 | Single Door | A04AR121 Finishing Work Door & Window Work Stainless Steel Door w/ SST Frame (UoM: EA) | A04AR121-00001 Finishing Work Door & Window Work Stainless Steel Door w/ SST Frame (UoM: EA) Single Door w/ Hardware & Accessories | A04AR121 | 00001 | A04AR121-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 121 | Stainless Steel Door w/ SST Frame (UoM: EA) | AJ | Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR121 | A04AR121-00001
00002 | Double Door |  |  | A04AR121 Finishing Work Door & Window Work Stainless Steel Door w/ SST Frame (UoM: EA) | A04AR121-00002 Finishing Work Door & Window Work Stainless Steel Door w/ SST Frame (UoM: EA) Double Door w/ Hardware & Accessories | A04AR121 | 00002 | A04AR121-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 121 | Stainless Steel Door w/ SST Frame (UoM: EA) | AK | Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR121 | A04AR121-00002
|  |  |  | A04AR122 Finishing Work Door & Window Work Wood Door w/ Wood Frame (UoM: M2) | A04AR122-00001 Finishing Work Door & Window Work Wood Door w/ Wood Frame (UoM: M2) w/ Hardware & Accessories | A04AR122 | 00001 | A04AR122-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 122 | Wood Door w/ Wood Frame (UoM: M2) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR122 | A04AR122-00001
|  | 00001 | Single Door | A04AR123 Finishing Work Door & Window Work Wood Door w/ Wood Frame (UoM: EA) | A04AR123-00001 Finishing Work Door & Window Work Wood Door w/ Wood Frame (UoM: EA) Single Door w/ Hardware & Accessories | A04AR123 | 00001 | A04AR123-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 123 | Wood Door w/ Wood Frame (UoM: EA) | AJ | Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR123 | A04AR123-00001
00002 | Double Door |  |  | A04AR123 Finishing Work Door & Window Work Wood Door w/ Wood Frame (UoM: EA) | A04AR123-00002 Finishing Work Door & Window Work Wood Door w/ Wood Frame (UoM: EA) Double Door w/ Hardware & Accessories | A04AR123 | 00002 | A04AR123-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 123 | Wood Door w/ Wood Frame (UoM: EA) | AK | Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR123 | A04AR123-00002
|  |  |  | A04AR124 Finishing Work Door & Window Work Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: M2) | A04AR124-00001 Finishing Work Door & Window Work Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: M2) w/ Hardware & Accessories | A04AR124 | 00001 | A04AR124-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 124 | Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: M2) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR124 | A04AR124-00001
|  | 00001 | Single Door | A04AR125 Finishing Work Door & Window Work Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR125-00001 Finishing Work Door & Window Work Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: EA) Single Door w/ Hardware & Accessories | A04AR125 | 00001 | A04AR125-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 125 | Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: EA) | AJ | Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR125 | A04AR125-00001
00002 | Double Door |  |  | A04AR125 Finishing Work Door & Window Work Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: EA) | A04AR125-00002 Finishing Work Door & Window Work Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: EA) Double Door w/ Hardware & Accessories | A04AR125 | 00002 | A04AR125-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 125 | Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: EA) | AK | Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR125 | A04AR125-00002
|  | 00001 | Fire Protective Rating: N/A, Motorized Type | A04AR126 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) | A04AR126-00001 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) Fire Protective Rating: N/A, Motorized Type w/ Hardware & Accessories | A04AR126 | 00001 | A04AR126-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AL | Fire Protective Rating: N/A, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR126 | A04AR126-00001
00002 | Fire Protective Rating: N/A, Manual Type |  |  | A04AR126 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) | A04AR126-00002 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) Fire Protective Rating: N/A, Manual Type w/ Hardware & Accessories | A04AR126 | 00002 | A04AR126-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AM | Fire Protective Rating: N/A, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR126 | A04AR126-00002
|  | 00003 | Fire Protective Rating: 0.5-hr, Motorized Type | A04AR126 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) | A04AR126-00003 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 0.5-hr, Motorized Type w/ Hardware & Accessories | A04AR126 | 00003 | A04AR126-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AN | Fire Protective Rating: 0.5-hr, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR126 | A04AR126-00003
00004 | Fire Protective Rating: 0.5-hr, Manual Type |  |  | A04AR126 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) | A04AR126-00004 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 0.5-hr, Manual Type w/ Hardware & Accessories | A04AR126 | 00004 | A04AR126-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AP | Fire Protective Rating: 0.5-hr, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR126 | A04AR126-00004
|  | 00005 | Fire Protective Rating: 1-hr, Motorized Type | A04AR126 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) | A04AR126-00005 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 1-hr, Motorized Type w/ Hardware & Accessories | A04AR126 | 00005 | A04AR126-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AQ | Fire Protective Rating: 1-hr, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR126 | A04AR126-00005
00006 | Fire Protective Rating: 1-hr, Manual Type |  |  | A04AR126 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) | A04AR126-00006 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 1-hr, Manual Type w/ Hardware & Accessories | A04AR126 | 00006 | A04AR126-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AR | Fire Protective Rating: 1-hr, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR126 | A04AR126-00006
|  | 00007 | Fire Protective Rating: 1.5-hrs, Motorized Type | A04AR126 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) | A04AR126-00007 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 1.5-hrs, Motorized Type w/ Hardware & Accessories | A04AR126 | 00007 | A04AR126-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AS | Fire Protective Rating: 1.5-hrs, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR126 | A04AR126-00007
00008 | Fire Protective Rating: 1.5-hrs, Manual Type |  |  | A04AR126 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) | A04AR126-00008 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 1.5-hrs, Manual Type w/ Hardware & Accessories | A04AR126 | 00008 | A04AR126-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AT | Fire Protective Rating: 1.5-hrs, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR126 | A04AR126-00008
|  | 00009 | Fire Protective Rating: 2-hrs, Motorized Type | A04AR126 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) | A04AR126-00009 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 2-hrs, Motorized Type w/ Hardware & Accessories | A04AR126 | 00009 | A04AR126-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AU | Fire Protective Rating: 2-hrs, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR126 | A04AR126-00009
00010 | Fire Protective Rating: 2-hrs, Manual Type |  |  | A04AR126 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) | A04AR126-00010 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 2-hrs, Manual Type w/ Hardware & Accessories | A04AR126 | 00010 | A04AR126-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AV | Fire Protective Rating: 2-hrs, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR126 | A04AR126-00010
|  | 00001 | Fire Protective Rating: N/A, Motorized Type | A04AR127 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) | A04AR127-00001 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Motorized Type w/ Hardware & Accessories | A04AR127 | 00001 | A04AR127-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AL | Fire Protective Rating: N/A, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR127 | A04AR127-00001
00002 | Fire Protective Rating: N/A, Manual Type |  |  | A04AR127 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) | A04AR127-00002 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Manual Type w/ Hardware & Accessories | A04AR127 | 00002 | A04AR127-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AM | Fire Protective Rating: N/A, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR127 | A04AR127-00002
|  | 00003 | Fire Protective Rating: 0.5-hr, Motorized Type | A04AR127 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) | A04AR127-00003 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 0.5-hr, Motorized Type w/ Hardware & Accessories | A04AR127 | 00003 | A04AR127-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AN | Fire Protective Rating: 0.5-hr, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR127 | A04AR127-00003
00004 | Fire Protective Rating: 0.5-hr, Manual Type |  |  | A04AR127 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) | A04AR127-00004 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 0.5-hr, Manual Type w/ Hardware & Accessories | A04AR127 | 00004 | A04AR127-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AP | Fire Protective Rating: 0.5-hr, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR127 | A04AR127-00004
|  | 00005 | Fire Protective Rating: 1-hr, Motorized Type | A04AR127 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) | A04AR127-00005 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Motorized Type w/ Hardware & Accessories | A04AR127 | 00005 | A04AR127-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AQ | Fire Protective Rating: 1-hr, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR127 | A04AR127-00005
00006 | Fire Protective Rating: 1-hr, Manual Type |  |  | A04AR127 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) | A04AR127-00006 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Manual Type w/ Hardware & Accessories | A04AR127 | 00006 | A04AR127-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AR | Fire Protective Rating: 1-hr, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR127 | A04AR127-00006
|  | 00007 | Fire Protective Rating: 1.5-hrs, Motorized Type | A04AR127 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) | A04AR127-00007 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1.5-hrs, Motorized Type w/ Hardware & Accessories | A04AR127 | 00007 | A04AR127-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AS | Fire Protective Rating: 1.5-hrs, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR127 | A04AR127-00007
00008 | Fire Protective Rating: 1.5-hrs, Manual Type |  |  | A04AR127 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) | A04AR127-00008 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1.5-hrs, Manual Type w/ Hardware & Accessories | A04AR127 | 00008 | A04AR127-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AT | Fire Protective Rating: 1.5-hrs, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR127 | A04AR127-00008
|  | 00009 | Fire Protective Rating: 2-hrs, Motorized Type | A04AR127 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) | A04AR127-00009 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 2-hrs, Motorized Type w/ Hardware & Accessories | A04AR127 | 00009 | A04AR127-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AU | Fire Protective Rating: 2-hrs, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR127 | A04AR127-00009
00010 | Fire Protective Rating: 2-hrs, Manual Type |  |  | A04AR127 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) | A04AR127-00010 Finishing Work Door & Window Work Steel Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 2-hrs, Manual Type w/ Hardware & Accessories | A04AR127 | 00010 | A04AR127-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AV | Fire Protective Rating: 2-hrs, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR127 | A04AR127-00010
|  | 00001 | Fire Protective Rating: N/A, Motorized Type | A04AR128 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | A04AR128-00001 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) Fire Protective Rating: N/A, Motorized Type w/ Hardware & Accessories | A04AR128 | 00001 | A04AR128-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 128 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | AL | Fire Protective Rating: N/A, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR128 | A04AR128-00001
00002 | Fire Protective Rating: N/A, Manual Type |  |  | A04AR128 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | A04AR128-00002 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) Fire Protective Rating: N/A, Manual Type w/ Hardware & Accessories | A04AR128 | 00002 | A04AR128-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 128 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | AM | Fire Protective Rating: N/A, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR128 | A04AR128-00002
|  | 00003 | Fire Protective Rating: 1-hr, Motorized Type | A04AR128 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | A04AR128-00003 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 1-hr, Motorized Type w/ Hardware & Accessories | A04AR128 | 00003 | A04AR128-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 128 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | AQ | Fire Protective Rating: 1-hr, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR128 | A04AR128-00003
00004 | Fire Protective Rating: 1-hr, Manual Type |  |  | A04AR128 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | A04AR128-00004 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 1-hr, Manual Type w/ Hardware & Accessories | A04AR128 | 00004 | A04AR128-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 128 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | AR | Fire Protective Rating: 1-hr, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR128 | A04AR128-00004
|  | 00005 | Fire Protective Rating: 2-hrs, Motorized Type | A04AR128 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | A04AR128-00005 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 2-hrs, Motorized Type w/ Hardware & Accessories | A04AR128 | 00005 | A04AR128-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 128 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | AU | Fire Protective Rating: 2-hrs, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR128 | A04AR128-00005
00006 | Fire Protective Rating: 2-hrs, Manual Type |  |  | A04AR128 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | A04AR128-00006 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 2-hrs, Manual Type w/ Hardware & Accessories | A04AR128 | 00006 | A04AR128-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 128 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | AV | Fire Protective Rating: 2-hrs, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR128 | A04AR128-00006
|  | 00001 | Fire Protective Rating: N/A, Motorized Type | A04AR129 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | A04AR129-00001 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Motorized Type w/ Hardware & Accessories | A04AR129 | 00001 | A04AR129-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 129 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | AL | Fire Protective Rating: N/A, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR129 | A04AR129-00001
00002 | Fire Protective Rating: N/A, Manual Type |  |  | A04AR129 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | A04AR129-00002 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Manual Type w/ Hardware & Accessories | A04AR129 | 00002 | A04AR129-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 129 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | AM | Fire Protective Rating: N/A, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR129 | A04AR129-00002
|  | 00003 | Fire Protective Rating: 1-hr, Motorized Type | A04AR129 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | A04AR129-00003 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Motorized Type w/ Hardware & Accessories | A04AR129 | 00003 | A04AR129-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 129 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | AQ | Fire Protective Rating: 1-hr, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR129 | A04AR129-00003
00004 | Fire Protective Rating: 1-hr, Manual Type |  |  | A04AR129 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | A04AR129-00004 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Manual Type w/ Hardware & Accessories | A04AR129 | 00004 | A04AR129-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 129 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | AR | Fire Protective Rating: 1-hr, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR129 | A04AR129-00004
|  | 00005 | Fire Protective Rating: 2-hrs, Motorized Type | A04AR129 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | A04AR129-00005 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 2-hrs, Motorized Type w/ Hardware & Accessories | A04AR129 | 00005 | A04AR129-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 129 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | AU | Fire Protective Rating: 2-hrs, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR129 | A04AR129-00005
00006 | Fire Protective Rating: 2-hrs, Manual Type |  |  | A04AR129 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | A04AR129-00006 Finishing Work Door & Window Work Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 2-hrs, Manual Type w/ Hardware & Accessories | A04AR129 | 00006 | A04AR129-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 129 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | AV | Fire Protective Rating: 2-hrs, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR129 | A04AR129-00006
|  | 00001 | Fire Protective Rating: N/A, Motorized Type | A04AR130 Finishing Work Door & Window Work Aluminum Roll Up Door w/ Aluminum Frame (UoM: M2) | A04AR130-00001 Finishing Work Door & Window Work Aluminum Roll Up Door w/ Aluminum Frame (UoM: M2) Fire Protective Rating: N/A, Motorized Type w/ Hardware & Accessories | A04AR130 | 00001 | A04AR130-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 130 | Aluminum Roll Up Door w/ Aluminum Frame (UoM: M2) | AL | Fire Protective Rating: N/A, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR130 | A04AR130-00001
00002 | Fire Protective Rating: N/A, Manual Type |  |  | A04AR130 Finishing Work Door & Window Work Aluminum Roll Up Door w/ Aluminum Frame (UoM: M2) | A04AR130-00002 Finishing Work Door & Window Work Aluminum Roll Up Door w/ Aluminum Frame (UoM: M2) Fire Protective Rating: N/A, Manual Type w/ Hardware & Accessories | A04AR130 | 00002 | A04AR130-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 130 | Aluminum Roll Up Door w/ Aluminum Frame (UoM: M2) | AM | Fire Protective Rating: N/A, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR130 | A04AR130-00002
|  | 00001 | Fire Protective Rating: N/A, Motorized Type | A04AR131 Finishing Work Door & Window Work Aluminum Roll Up Door w/ Aluminum Frame (UoM: EA) | A04AR131-00001 Finishing Work Door & Window Work Aluminum Roll Up Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: N/A, Motorized Type w/ Hardware & Accessories | A04AR131 | 00001 | A04AR131-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 131 | Aluminum Roll Up Door w/ Aluminum Frame (UoM: EA) | AL | Fire Protective Rating: N/A, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR131 | A04AR131-00001
00002 | Fire Protective Rating: N/A, Manual Type |  |  | A04AR131 Finishing Work Door & Window Work Aluminum Roll Up Door w/ Aluminum Frame (UoM: EA) | A04AR131-00002 Finishing Work Door & Window Work Aluminum Roll Up Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: N/A, Manual Type w/ Hardware & Accessories | A04AR131 | 00002 | A04AR131-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 131 | Aluminum Roll Up Door w/ Aluminum Frame (UoM: EA) | AM | Fire Protective Rating: N/A, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR131 | A04AR131-00002
|  | 00001 | Fire Protective Rating: N/A, Motorized Type | A04AR132 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) | A04AR132-00001 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) Fire Protective Rating: N/A, Motorized Type w/ Hardware & Accessories | A04AR132 | 00001 | A04AR132-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AL | Fire Protective Rating: N/A, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR132 | A04AR132-00001
00002 | Fire Protective Rating: N/A, Manual Type |  |  | A04AR132 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) | A04AR132-00002 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) Fire Protective Rating: N/A, Manual Type w/ Hardware & Accessories | A04AR132 | 00002 | A04AR132-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AM | Fire Protective Rating: N/A, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR132 | A04AR132-00002
|  | 00003 | Fire Protective Rating: 0.5-hr, Motorized Type | A04AR132 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) | A04AR132-00003 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 0.5-hr, Motorized Type w/ Hardware & Accessories | A04AR132 | 00003 | A04AR132-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AN | Fire Protective Rating: 0.5-hr, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR132 | A04AR132-00003
00004 | Fire Protective Rating: 0.5-hr, Manual Type |  |  | A04AR132 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) | A04AR132-00004 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 0.5-hr, Manual Type w/ Hardware & Accessories | A04AR132 | 00004 | A04AR132-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AP | Fire Protective Rating: 0.5-hr, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR132 | A04AR132-00004
|  | 00005 | Fire Protective Rating: 1-hr, Motorized Type | A04AR132 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) | A04AR132-00005 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 1-hr, Motorized Type w/ Hardware & Accessories | A04AR132 | 00005 | A04AR132-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AQ | Fire Protective Rating: 1-hr, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR132 | A04AR132-00005
00006 | Fire Protective Rating: 1-hr, Manual Type |  |  | A04AR132 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) | A04AR132-00006 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 1-hr, Manual Type w/ Hardware & Accessories | A04AR132 | 00006 | A04AR132-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AR | Fire Protective Rating: 1-hr, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR132 | A04AR132-00006
|  | 00007 | Fire Protective Rating: 1.5-hrs, Motorized Type | A04AR132 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) | A04AR132-00007 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 1.5-hrs, Motorized Type w/ Hardware & Accessories | A04AR132 | 00007 | A04AR132-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AS | Fire Protective Rating: 1.5-hrs, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR132 | A04AR132-00007
00008 | Fire Protective Rating: 1.5-hrs, Manual Type |  |  | A04AR132 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) | A04AR132-00008 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 1.5-hrs, Manual Type w/ Hardware & Accessories | A04AR132 | 00008 | A04AR132-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AT | Fire Protective Rating: 1.5-hrs, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR132 | A04AR132-00008
|  | 00009 | Fire Protective Rating: 2-hrs, Motorized Type | A04AR132 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) | A04AR132-00009 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 2-hrs, Motorized Type w/ Hardware & Accessories | A04AR132 | 00009 | A04AR132-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AU | Fire Protective Rating: 2-hrs, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR132 | A04AR132-00009
00010 | Fire Protective Rating: 2-hrs, Manual Type |  |  | A04AR132 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) | A04AR132-00010 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 2-hrs, Manual Type w/ Hardware & Accessories | A04AR132 | 00010 | A04AR132-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AV | Fire Protective Rating: 2-hrs, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR132 | A04AR132-00010
|  | 00001 | Fire Protective Rating: N/A, Motorized Type | A04AR133 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) | A04AR133-00001 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Motorized Type w/ Hardware & Accessories | A04AR133 | 00001 | A04AR133-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AL | Fire Protective Rating: N/A, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR133 | A04AR133-00001
00002 | Fire Protective Rating: N/A, Manual Type |  |  | A04AR133 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) | A04AR133-00002 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Manual Type w/ Hardware & Accessories | A04AR133 | 00002 | A04AR133-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AM | Fire Protective Rating: N/A, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR133 | A04AR133-00002
|  | 00003 | Fire Protective Rating: 0.5-hr, Motorized Type | A04AR133 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) | A04AR133-00003 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 0.5-hr, Motorized Type w/ Hardware & Accessories | A04AR133 | 00003 | A04AR133-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AN | Fire Protective Rating: 0.5-hr, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR133 | A04AR133-00003
00004 | Fire Protective Rating: 0.5-hr, Manual Type |  |  | A04AR133 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) | A04AR133-00004 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 0.5-hr, Manual Type w/ Hardware & Accessories | A04AR133 | 00004 | A04AR133-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AP | Fire Protective Rating: 0.5-hr, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR133 | A04AR133-00004
|  | 00005 | Fire Protective Rating: 1-hr, Motorized Type | A04AR133 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) | A04AR133-00005 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Motorized Type w/ Hardware & Accessories | A04AR133 | 00005 | A04AR133-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AQ | Fire Protective Rating: 1-hr, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR133 | A04AR133-00005
00006 | Fire Protective Rating: 1-hr, Manual Type |  |  | A04AR133 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) | A04AR133-00006 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Manual Type w/ Hardware & Accessories | A04AR133 | 00006 | A04AR133-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AR | Fire Protective Rating: 1-hr, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR133 | A04AR133-00006
|  | 00007 | Fire Protective Rating: 1.5-hrs, Motorized Type | A04AR133 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) | A04AR133-00007 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1.5-hrs, Motorized Type w/ Hardware & Accessories | A04AR133 | 00007 | A04AR133-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AS | Fire Protective Rating: 1.5-hrs, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR133 | A04AR133-00007
00008 | Fire Protective Rating: 1.5-hrs, Manual Type |  |  | A04AR133 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) | A04AR133-00008 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1.5-hrs, Manual Type w/ Hardware & Accessories | A04AR133 | 00008 | A04AR133-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AT | Fire Protective Rating: 1.5-hrs, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR133 | A04AR133-00008
|  | 00009 | Fire Protective Rating: 2-hrs, Motorized Type | A04AR133 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) | A04AR133-00009 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 2-hrs, Motorized Type w/ Hardware & Accessories | A04AR133 | 00009 | A04AR133-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AU | Fire Protective Rating: 2-hrs, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR133 | A04AR133-00009
00010 | Fire Protective Rating: 2-hrs, Manual Type |  |  | A04AR133 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) | A04AR133-00010 Finishing Work Door & Window Work Steel Sliding Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 2-hrs, Manual Type w/ Hardware & Accessories | A04AR133 | 00010 | A04AR133-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AV | Fire Protective Rating: 2-hrs, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR133 | A04AR133-00010
|  | 00001 | Fire Protective Rating: N/A, Motorized Type | A04AR134 Finishing Work Door & Window Work Aluminum Sliding Door w/ Aluminum Frame (UoM: M2) | A04AR134-00001 Finishing Work Door & Window Work Aluminum Sliding Door w/ Aluminum Frame (UoM: M2) Fire Protective Rating: N/A, Motorized Type w/ Hardware & Accessories | A04AR134 | 00001 | A04AR134-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 134 | Aluminum Sliding Door w/ Aluminum Frame (UoM: M2) | AL | Fire Protective Rating: N/A, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR134 | A04AR134-00001
00002 | Fire Protective Rating: N/A, Manual Type |  |  | A04AR134 Finishing Work Door & Window Work Aluminum Sliding Door w/ Aluminum Frame (UoM: M2) | A04AR134-00002 Finishing Work Door & Window Work Aluminum Sliding Door w/ Aluminum Frame (UoM: M2) Fire Protective Rating: N/A, Manual Type w/ Hardware & Accessories | A04AR134 | 00002 | A04AR134-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 134 | Aluminum Sliding Door w/ Aluminum Frame (UoM: M2) | AM | Fire Protective Rating: N/A, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR134 | A04AR134-00002
|  | 00001 | Fire Protective Rating: N/A, Motorized Type | A04AR135 Finishing Work Door & Window Work Aluminum Sliding Door w/ Aluminum Frame (UoM: EA) | A04AR135-00001 Finishing Work Door & Window Work Aluminum Sliding Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: N/A, Motorized Type w/ Hardware & Accessories | A04AR135 | 00001 | A04AR135-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 135 | Aluminum Sliding Door w/ Aluminum Frame (UoM: EA) | AL | Fire Protective Rating: N/A, Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR135 | A04AR135-00001
00002 | Fire Protective Rating: N/A, Manual Type |  |  | A04AR135 Finishing Work Door & Window Work Aluminum Sliding Door w/ Aluminum Frame (UoM: EA) | A04AR135-00002 Finishing Work Door & Window Work Aluminum Sliding Door w/ Aluminum Frame (UoM: EA) Fire Protective Rating: N/A, Manual Type w/ Hardware & Accessories | A04AR135 | 00002 | A04AR135-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 135 | Aluminum Sliding Door w/ Aluminum Frame (UoM: EA) | AM | Fire Protective Rating: N/A, Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR135 | A04AR135-00002
|  | 00001 | Steel Hanger Door w/ Steel Frame (UoM: M2) | A04AR136 Finishing Work Door & Window Work Steel Hanger Door w/ Steel Frame (UoM: M2) | A04AR136-00001 Finishing Work Door & Window Work Steel Hanger Door w/ Steel Frame (UoM: M2) w/ Hardware & Accessories | A04AR136 | 00001 | A04AR136-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 136 | Steel Hanger Door w/ Steel Frame (UoM: M2) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR136 | A04AR136-00001
|  | 00001 | Steel Hanger Door w/ Steel Frame (UoM: EA) | A04AR137 Finishing Work Door & Window Work Steel Hanger Door w/ Steel Frame (UoM: EA) | A04AR137-00001 Finishing Work Door & Window Work Steel Hanger Door w/ Steel Frame (UoM: EA) w/ Hardware & Accessories | A04AR137 | 00001 | A04AR137-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 137 | Steel Hanger Door w/ Steel Frame (UoM: EA) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR137 | A04AR137-00001
00001 | Steel Swing Door w/ Steel Frame (UoM: M2) |  |  | A04AR138 Finishing Work Door & Window Work Steel Swing Door w/ Steel Frame (UoM: M2) | A04AR138-00001 Finishing Work Door & Window Work Steel Swing Door w/ Steel Frame (UoM: M2) w/ Hardware & Accessories | A04AR138 | 00001 | A04AR138-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 138 | Steel Swing Door w/ Steel Frame (UoM: M2) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR138 | A04AR138-00001
00001 | Steel Swing Door w/ Steel Frame (UoM: EA) |  |  | A04AR139 Finishing Work Door & Window Work Steel Swing Door w/ Steel Frame (UoM: EA) | A04AR139-00001 Finishing Work Door & Window Work Steel Swing Door w/ Steel Frame (UoM: EA) w/ Hardware & Accessories | A04AR139 | 00001 | A04AR139-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 139 | Steel Swing Door w/ Steel Frame (UoM: EA) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR139 | A04AR139-00001
|  | 00001 | Aluminum Swing Door w/ Aluminum Frame (UoM: M2) | A04AR140 Finishing Work Door & Window Work Aluminum Swing Door w/ Aluminum Frame (UoM: M2) | A04AR140-00001 Finishing Work Door & Window Work Aluminum Swing Door w/ Aluminum Frame (UoM: M2) w/ Hardware & Accessories | A04AR140 | 00001 | A04AR140-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 140 | Aluminum Swing Door w/ Aluminum Frame (UoM: M2) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR140 | A04AR140-00001
|  | 00001 | Aluminum Swing Door w/ Aluminum Frame (UoM: EA) | A04AR141 Finishing Work Door & Window Work Aluminum Swing Door w/ Aluminum Frame (UoM: EA) | A04AR141-00001 Finishing Work Door & Window Work Aluminum Swing Door w/ Aluminum Frame (UoM: EA) w/ Hardware & Accessories | A04AR141 | 00001 | A04AR141-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 141 | Aluminum Swing Door w/ Aluminum Frame (UoM: EA) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR141 | A04AR141-00001
00001 | Revolving Door (UoM: EA) |  |  | A04AR142 Finishing Work Door & Window Work Revolving Door (UoM: EA) | A04AR142-00001 Finishing Work Door & Window Work Revolving Door (UoM: EA) Manual Revolving Door w/ Hardware & Accessories | A04AR142 | 00001 | A04AR142-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 142 | Revolving Door (UoM: EA) | AW | Manual Revolving Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR142 | A04AR142-00001
00002 | Revolving Door (UoM: EA) |  |  | A04AR142 Finishing Work Door & Window Work Revolving Door (UoM: EA) | A04AR142-00002 Finishing Work Door & Window Work Revolving Door (UoM: EA) Auto Revolving Door w/ Hardware & Accessories | A04AR142 | 00002 | A04AR142-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 142 | Revolving Door (UoM: EA) | BA | Auto Revolving Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR142 | A04AR142-00002
|  | 00001 | Motorized Type | A04AR143 Finishing Work Door & Window Work Steel Folding(Accordion) Door w/ Steel Frame (UoM: M2) | A04AR143-00001 Finishing Work Door & Window Work Steel Folding(Accordion) Door w/ Steel Frame (UoM: M2) Motorized Type w/ Hardware & Accessories | A04AR143 | 00001 | A04AR143-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 143 | Steel Folding(Accordion) Door w/ Steel Frame (UoM: M2) | BB | Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR143 | A04AR143-00001
00002 | Manual Type |  |  | A04AR143 Finishing Work Door & Window Work Steel Folding(Accordion) Door w/ Steel Frame (UoM: M2) | A04AR143-00002 Finishing Work Door & Window Work Steel Folding(Accordion) Door w/ Steel Frame (UoM: M2) Manual Type w/ Hardware & Accessories | A04AR143 | 00002 | A04AR143-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 143 | Steel Folding(Accordion) Door w/ Steel Frame (UoM: M2) | BC | Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR143 | A04AR143-00002
|  | 00001 | Motorized Type | A04AR144 Finishing Work Door & Window Work Steel Folding(Accordion) Door w/ Steel Frame (UoM: EA) | A04AR144-00001 Finishing Work Door & Window Work Steel Folding(Accordion) Door w/ Steel Frame (UoM: EA) Motorized Type w/ Hardware & Accessories | A04AR144 | 00001 | A04AR144-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 144 | Steel Folding(Accordion) Door w/ Steel Frame (UoM: EA) | BB | Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR144 | A04AR144-00001
00002 | Manual Type |  |  | A04AR144 Finishing Work Door & Window Work Steel Folding(Accordion) Door w/ Steel Frame (UoM: EA) | A04AR144-00002 Finishing Work Door & Window Work Steel Folding(Accordion) Door w/ Steel Frame (UoM: EA) Manual Type w/ Hardware & Accessories | A04AR144 | 00002 | A04AR144-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 144 | Steel Folding(Accordion) Door w/ Steel Frame (UoM: EA) | BC | Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR144 | A04AR144-00002
|  | 00001 | Motorized Type | A04AR145 Finishing Work Door & Window Work Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: M2) | A04AR145-00001 Finishing Work Door & Window Work Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: M2) Motorized Type w/ Hardware & Accessories | A04AR145 | 00001 | A04AR145-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 145 | Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: M2) | BB | Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR145 | A04AR145-00001
00002 | Manual Type |  |  | A04AR145 Finishing Work Door & Window Work Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: M2) | A04AR145-00002 Finishing Work Door & Window Work Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: M2) Manual Type w/ Hardware & Accessories | A04AR145 | 00002 | A04AR145-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 145 | Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: M2) | BC | Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR145 | A04AR145-00002
|  | 00001 | Motorized Type | A04AR146 Finishing Work Door & Window Work Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: EA) | A04AR146-00001 Finishing Work Door & Window Work Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: EA) Motorized Type w/ Hardware & Accessories | A04AR146 | 00001 | A04AR146-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 146 | Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: EA) | BB | Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR146 | A04AR146-00001
00002 | Manual Type |  |  | A04AR146 Finishing Work Door & Window Work Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: EA) | A04AR146-00002 Finishing Work Door & Window Work Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: EA) Manual Type w/ Hardware & Accessories | A04AR146 | 00002 | A04AR146-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 146 | Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: EA) | BC | Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR146 | A04AR146-00002
00001 | Manual Type |  |  | A04AR147 Finishing Work Door & Window Work PVC Folding(Accordion) Door w/ PVC Frame (UoM: M2) | A04AR147-00001 Finishing Work Door & Window Work PVC Folding(Accordion) Door w/ PVC Frame (UoM: M2) Manual Type w/ Hardware & Accessories | A04AR147 | 00001 | A04AR147-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 147 | PVC Folding(Accordion) Door w/ PVC Frame (UoM: M2) | BC | Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR147 | A04AR147-00001
00001 | Manual Type |  |  | A04AR148 Finishing Work Door & Window Work PVC Folding(Accordion) Door w/ PVC Frame (UoM: EA) | A04AR148-00001 Finishing Work Door & Window Work PVC Folding(Accordion) Door w/ PVC Frame (UoM: EA) Manual Type w/ Hardware & Accessories | A04AR148 | 00001 | A04AR148-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 148 | PVC Folding(Accordion) Door w/ PVC Frame (UoM: EA) | BC | Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR148 | A04AR148-00001
|  |  |  | A04AR149 Finishing Work Door & Window Work uPVC Door w/ uPVC Frame (UoM: M2) | A04AR149-00001 Finishing Work Door & Window Work uPVC Door w/ uPVC Frame (UoM: M2) w/ Hardware & Accessories | A04AR149 | 00001 | A04AR149-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 149 | uPVC Door w/ uPVC Frame (UoM: M2) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR149 | A04AR149-00001
|  |  |  | A04AR150 Finishing Work Door & Window Work uPVC Door w/ uPVC Frame (UoM: EA) | A04AR150-00001 Finishing Work Door & Window Work uPVC Door w/ uPVC Frame (UoM: EA) w/ Hardware & Accessories | A04AR150 | 00001 | A04AR150-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 150 | uPVC Door w/ uPVC Frame (UoM: EA) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR150 | A04AR150-00001
|  |  |  | A04AR151 Finishing Work Door & Window Work Master Key System | A04AR151-00001 Finishing Work Door & Window Work Master Key System Three Levels Master Key w/ Accessories (Key Box, Key Tag and ETC) | A04AR151 | 00001 | A04AR151-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 151 | Master Key System | BD | Three Levels Master Key |  | 0 |  | 0 |  | 0 |  | 0 | 37 | w/ Accessories (Key Box, Key Tag and ETC) |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | SET | SET | A04AR151 | A04AR151-00001
|  |  |  | A04AR152 Finishing Work Door & Window Work Steel Window (UoM: M2) | A04AR152-00001 Finishing Work Door & Window Work Steel Window (UoM: M2) Fire Protective Rating: N/A w/ Hardware & Accessories | A04AR152 | 00001 | A04AR152-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 152 | Steel Window (UoM: M2) | 89 | Fire Protective Rating: N/A |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR152 | A04AR152-00001
|  |  |  | A04AR152 Finishing Work Door & Window Work Steel Window (UoM: M2) | A04AR152-00002 Finishing Work Door & Window Work Steel Window (UoM: M2) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | A04AR152 | 00002 | A04AR152-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 152 | Steel Window (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR152 | A04AR152-00002
|  |  |  | A04AR152 Finishing Work Door & Window Work Steel Window (UoM: M2) | A04AR152-00003 Finishing Work Door & Window Work Steel Window (UoM: M2) Fire Protective Rating: 1-hr w/ Hardware & Accessories | A04AR152 | 00003 | A04AR152-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 152 | Steel Window (UoM: M2) | 95 | Fire Protective Rating: 1-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR152 | A04AR152-00003
|  | 00001 | Fire Protective Rating: N/A | A04AR153 Finishing Work Door & Window Work Steel Window (UoM: EA) | A04AR153-00001 Finishing Work Door & Window Work Steel Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | A04AR153 | 00001 | A04AR153-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 153 | Steel Window (UoM: EA) | 89 | Fire Protective Rating: N/A |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR153 | A04AR153-00001
|  | 00002 | Fire Protective Rating: 0.5-hr | A04AR153 Finishing Work Door & Window Work Steel Window (UoM: EA) | A04AR153-00002 Finishing Work Door & Window Work Steel Window (UoM: EA) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | A04AR153 | 00002 | A04AR153-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 153 | Steel Window (UoM: EA) | 92 | Fire Protective Rating: 0.5-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR153 | A04AR153-00002
|  | 00003 | Fire Protective Rating: 1-hr | A04AR153 Finishing Work Door & Window Work Steel Window (UoM: EA) | A04AR153-00003 Finishing Work Door & Window Work Steel Window (UoM: EA) Fire Protective Rating: 1-hr w/ Hardware & Accessories | A04AR153 | 00003 | A04AR153-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 153 | Steel Window (UoM: EA) | 95 | Fire Protective Rating: 1-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR153 | A04AR153-00003
|  |  |  | A04AR154 Finishing Work Door & Window Work Blast Resistant Steel Window (UoM: M2) | A04AR154-00001 Finishing Work Door & Window Work Blast Resistant Steel Window (UoM: M2) w/ Hardware & Accessories | A04AR154 | 00001 | A04AR154-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 154 | Blast Resistant Steel Window (UoM: M2) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | M2 | M2 | A04AR154 | A04AR154-00001
|  | 00001 | 0 | A04AR155 Finishing Work Door & Window Work Blast Resistant Steel Window (UoM: EA) | A04AR155-00001 Finishing Work Door & Window Work Blast Resistant Steel Window (UoM: EA) w/ Hardware & Accessories | A04AR155 | 00001 | A04AR155-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 155 | Blast Resistant Steel Window (UoM: EA) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | Blast Load: Overpressure ( )psi, Duration ( )ms | 0 |  | EA | EA | A04AR155 | A04AR155-00001
|  |  |  | A04AR156 Finishing Work Door & Window Work Bullet-Proof Steel Window (UoM: M2) | A04AR156-00001 Finishing Work Door & Window Work Bullet-Proof Steel Window (UoM: M2) w/ Hardware & Accessories | A04AR156 | 00001 | A04AR156-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 156 | Bullet-Proof Steel Window (UoM: M2) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR156 | A04AR156-00001
|  | 00001 | 0 | A04AR157 Finishing Work Door & Window Work Bullet-Proof Steel Window (UoM: EA) | A04AR157-00001 Finishing Work Door & Window Work Bullet-Proof Steel Window (UoM: EA) w/ Hardware & Accessories | A04AR157 | 00001 | A04AR157-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 157 | Bullet-Proof Steel Window (UoM: EA) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR157 | A04AR157-00001
|  |  |  | A04AR158 Finishing Work Door & Window Work Aluminum Window (UoM: M2) | A04AR158-00001 Finishing Work Door & Window Work Aluminum Window (UoM: M2) Fire Protective Rating: N/A w/ Hardware & Accessories | A04AR158 | 00001 | A04AR158-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 158 | Aluminum Window (UoM: M2) | 89 | Fire Protective Rating: N/A |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR158 | A04AR158-00001
|  |  |  | A04AR158 Finishing Work Door & Window Work Aluminum Window (UoM: M2) | A04AR158-00002 Finishing Work Door & Window Work Aluminum Window (UoM: M2) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | A04AR158 | 00002 | A04AR158-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 158 | Aluminum Window (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR158 | A04AR158-00002
|  |  |  | A04AR158 Finishing Work Door & Window Work Aluminum Window (UoM: M2) | A04AR158-00003 Finishing Work Door & Window Work Aluminum Window (UoM: M2) Fire Protective Rating: 1-hr w/ Hardware & Accessories | A04AR158 | 00003 | A04AR158-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 158 | Aluminum Window (UoM: M2) | 95 | Fire Protective Rating: 1-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR158 | A04AR158-00003
|  | 00001 | Fire Protective Rating: N/A | A04AR159 Finishing Work Door & Window Work Aluminum Window (UoM: EA) | A04AR159-00001 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: N/A w/ Hardware & Accessories | A04AR159 | 00001 | A04AR159-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 159 | Aluminum Window (UoM: EA) | 89 | Fire Protective Rating: N/A |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR159 | A04AR159-00001
|  | 00002 | Fire Protective Rating: 0.5-hr | A04AR159 Finishing Work Door & Window Work Aluminum Window (UoM: EA) | A04AR159-00002 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | A04AR159 | 00002 | A04AR159-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 159 | Aluminum Window (UoM: EA) | 92 | Fire Protective Rating: 0.5-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR159 | A04AR159-00002
|  | 00003 | Fire Protective Rating: 1-hr | A04AR159 Finishing Work Door & Window Work Aluminum Window (UoM: EA) | A04AR159-00003 Finishing Work Door & Window Work Aluminum Window (UoM: EA) Fire Protective Rating: 1-hr w/ Hardware & Accessories | A04AR159 | 00003 | A04AR159-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 159 | Aluminum Window (UoM: EA) | 95 | Fire Protective Rating: 1-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR159 | A04AR159-00003
|  |  |  | A04AR160 Finishing Work Door & Window Work uPVC Window (UoM: M2) | A04AR160-00001 Finishing Work Door & Window Work uPVC Window (UoM: M2) w/ Hardware & Accessories | A04AR160 | 00001 | A04AR160-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 160 | uPVC Window (UoM: M2) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR160 | A04AR160-00001
|  | 00001 | 0 | A04AR161 Finishing Work Door & Window Work uPVC Window (UoM: EA) | A04AR161-00001 Finishing Work Door & Window Work uPVC Window (UoM: EA) w/ Hardware & Accessories | A04AR161 | 00001 | A04AR161-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 161 | uPVC Window (UoM: EA) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR161 | A04AR161-00001
|  |  |  | A04AR162 Finishing Work Door & Window Work Skylight (UoM: M2) | A04AR162-00001 Finishing Work Door & Window Work Skylight (UoM: M2) FRP(Fiberglass Reinforced Plastics) Skylight | A04AR162 | 00001 | A04AR162-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 162 | Skylight (UoM: M2) | BG | FRP(Fiberglass Reinforced Plastics) Skylight |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR162 | A04AR162-00001
|  |  |  | A04AR162 Finishing Work Door & Window Work Skylight (UoM: M2) | A04AR162-00002 Finishing Work Door & Window Work Skylight (UoM: M2) Acrylic Skylight w/ Ventilation | A04AR162 | 00002 | A04AR162-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 162 | Skylight (UoM: M2) | BH | Acrylic Skylight w/ Ventilation |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR162 | A04AR162-00002
|  |  |  | A04AR163 Finishing Work Door & Window Work Louver (UoM: M2) | A04AR163-00001 Finishing Work Door & Window Work Louver (UoM: M2) Aluminum w/ Hardware & Accessories | A04AR163 | 00001 | A04AR163-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 163 | Louver (UoM: M2) | BJ | Aluminum |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR163 | A04AR163-00001
|  |  |  | A04AR163 Finishing Work Door & Window Work Louver (UoM: M2) | A04AR163-00002 Finishing Work Door & Window Work Louver (UoM: M2) Steel w/ Hardware & Accessories | A04AR163 | 00002 | A04AR163-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 163 | Louver (UoM: M2) | BK | Steel |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR163 | A04AR163-00002
|  | 00001 | Aluminum | A04AR164 Finishing Work Door & Window Work Louver (UoM: EA) | A04AR164-00001 Finishing Work Door & Window Work Louver (UoM: EA) Aluminum w/ Hardware & Accessories | A04AR164 | 00001 | A04AR164-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 164 | Louver (UoM: EA) | BJ | Aluminum |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR164 | A04AR164-00001
|  | 00002 | Steel | A04AR164 Finishing Work Door & Window Work Louver (UoM: EA) | A04AR164-00002 Finishing Work Door & Window Work Louver (UoM: EA) Steel w/ Hardware & Accessories | A04AR164 | 00002 | A04AR164-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 164 | Louver (UoM: EA) | BK | Steel |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR164 | A04AR164-00002
|  |  |  | A04AR165 Finishing Work Door & Window Work Shade (UoM: M2) | A04AR165-00001 Finishing Work Door & Window Work Shade (UoM: M2) Manual Type w/ Hardware & Accessories | A04AR165 | 00001 | A04AR165-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 165 | Shade (UoM: M2) | BC | Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR165 | A04AR165-00001
|  |  |  | A04AR165 Finishing Work Door & Window Work Shade (UoM: M2) | A04AR165-00002 Finishing Work Door & Window Work Shade (UoM: M2) Motorized Type w/ Hardware & Accessories | A04AR165 | 00002 | A04AR165-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 165 | Shade (UoM: M2) | BB | Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR165 | A04AR165-00002
|  | 00001 | Manual Type | A04AR166 Finishing Work Door & Window Work Shade (UoM: EA) | A04AR166-00001 Finishing Work Door & Window Work Shade (UoM: EA) Manual Type w/ Hardware & Accessories | A04AR166 | 00001 | A04AR166-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 166 | Shade (UoM: EA) | BC | Manual Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR166 | A04AR166-00001
|  | 00002 | Motorized Type | A04AR166 Finishing Work Door & Window Work Shade (UoM: EA) | A04AR166-00002 Finishing Work Door & Window Work Shade (UoM: EA) Motorized Type w/ Hardware & Accessories | A04AR166 | 00002 | A04AR166-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 166 | Shade (UoM: EA) | BB | Motorized Type |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR166 | A04AR166-00002
|  |  |  | A04AR315 Finishing Work Door & Window Work Curtain Wall System (UoM: M2) | A04AR315-00001 Finishing Work Door & Window Work Curtain Wall System (UoM: M2) w/ Hardware & Accessories | A04AR315 | 00001 | A04AR315-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 315 | Curtain Wall System (UoM: M2) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR315 | A04AR315-00001
|  | 00001 | 0 | A04AR316 Finishing Work Door & Window Work Curtain Wall System (UoM: EA) | A04AR316-00001 Finishing Work Door & Window Work Curtain Wall System (UoM: EA) w/ Hardware & Accessories | A04AR316 | 00001 | A04AR316-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 316 | Curtain Wall System (UoM: EA) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR316 | A04AR316-00001
|  |  |  | A04AR318 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: M2) | A04AR318-00001 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: M2) Fire Protective Rating: N/A w/ Hardware & Accessories | A04AR318 | 00001 | A04AR318-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 318 | Ballistic Resistant Door w/ Steel Frame (UoM: M2) | 89 | Fire Protective Rating: N/A |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR318 | A04AR318-00001
|  |  |  | A04AR318 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: M2) | A04AR318-00002 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | A04AR318 | 00002 | A04AR318-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 318 | Ballistic Resistant Door w/ Steel Frame (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR318 | A04AR318-00002
|  |  |  | A04AR318 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: M2) | A04AR318-00003 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 1-hr w/ Hardware & Accessories | A04AR318 | 00003 | A04AR318-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 318 | Ballistic Resistant Door w/ Steel Frame (UoM: M2) | 95 | Fire Protective Rating: 1-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR318 | A04AR318-00003
|  |  |  | A04AR318 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: M2) | A04AR318-00004 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 1.5-hrs w/ Hardware & Accessories | A04AR318 | 00004 | A04AR318-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 318 | Ballistic Resistant Door w/ Steel Frame (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR318 | A04AR318-00004
|  |  |  | A04AR318 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: M2) | A04AR318-00005 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 2-hrs w/ Hardware & Accessories | A04AR318 | 00005 | A04AR318-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 318 | Ballistic Resistant Door w/ Steel Frame (UoM: M2) | AF | Fire Protective Rating: 2-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR318 | A04AR318-00005
|  |  |  | A04AR318 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: M2) | A04AR318-00006 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: M2) Fire Protective Rating: 3-hrs w/ Hardware & Accessories | A04AR318 | 00006 | A04AR318-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 318 | Ballistic Resistant Door w/ Steel Frame (UoM: M2) | FH | Fire Protective Rating: 3-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR318 | A04AR318-00006
|  | 00001 | Fire Protective Rating: N/A, Single Door | A04AR319 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) | A04AR319-00001 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | A04AR319 | 00001 | A04AR319-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 319 | Ballistic Resistant Door w/ Steel Frame (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR319 | A04AR319-00001
00002 | Fire Protective Rating: N/A, Double Door |  |  | A04AR319 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) | A04AR319-00002 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | A04AR319 | 00002 | A04AR319-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 319 | Ballistic Resistant Door w/ Steel Frame (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR319 | A04AR319-00002
|  | 00003 | Fire Protective Rating: 0.5-hr, Single Door | A04AR319 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) | A04AR319-00003 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 0.5-hr, Single Door w/ Hardware & Accessories | A04AR319 | 00003 | A04AR319-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 319 | Ballistic Resistant Door w/ Steel Frame (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR319 | A04AR319-00003
00004 | Fire Protective Rating: 0.5-hr, Double Door |  |  | A04AR319 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) | A04AR319-00004 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 0.5-hr, Double Door w/ Hardware & Accessories | A04AR319 | 00004 | A04AR319-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 319 | Ballistic Resistant Door w/ Steel Frame (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR319 | A04AR319-00004
|  | 00005 | Fire Protective Rating: 1-hr, Single Door | A04AR319 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) | A04AR319-00005 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Single Door w/ Hardware & Accessories | A04AR319 | 00005 | A04AR319-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 319 | Ballistic Resistant Door w/ Steel Frame (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR319 | A04AR319-00005
00006 | Fire Protective Rating: 1-hr, Double Door |  |  | A04AR319 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) | A04AR319-00006 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | A04AR319 | 00006 | A04AR319-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 319 | Ballistic Resistant Door w/ Steel Frame (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR319 | A04AR319-00006
|  | 00007 | Fire Protective Rating: 1.5-hrs, Single Door | A04AR319 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) | A04AR319-00007 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1.5-hrs, Single Door w/ Hardware & Accessories | A04AR319 | 00007 | A04AR319-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 319 | Ballistic Resistant Door w/ Steel Frame (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR319 | A04AR319-00007
00008 | Fire Protective Rating: 1.5-hrs, Double Door |  |  | A04AR319 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) | A04AR319-00008 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 1.5-hrs, Double Door w/ Hardware & Accessories | A04AR319 | 00008 | A04AR319-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 319 | Ballistic Resistant Door w/ Steel Frame (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR319 | A04AR319-00008
|  | 00009 | Fire Protective Rating: 2-hrs, Single Door | A04AR319 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) | A04AR319-00009 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 2-hrs, Single Door w/ Hardware & Accessories | A04AR319 | 00009 | A04AR319-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 319 | Ballistic Resistant Door w/ Steel Frame (UoM: EA) | AG | Fire Protective Rating: 2-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR319 | A04AR319-00009
00010 | Fire Protective Rating: 2-hrs, Double Door |  |  | A04AR319 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) | A04AR319-00010 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 2-hrs, Double Door w/ Hardware & Accessories | A04AR319 | 00010 | A04AR319-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 319 | Ballistic Resistant Door w/ Steel Frame (UoM: EA) | AH | Fire Protective Rating: 2-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR319 | A04AR319-00010
|  | 00011 | Fire Protective Rating: 3-hrs, Single Door | A04AR319 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) | A04AR319-00011 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 3-hrs, Single Door w/ Hardware & Accessories | A04AR319 | 00011 | A04AR319-00011 | AR | A04 | Finishing Work | AR | Door & Window Work | 319 | Ballistic Resistant Door w/ Steel Frame (UoM: EA) | FJ | Fire Protective Rating: 3-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR319 | A04AR319-00011
00012 | Fire Protective Rating: 3-hrs, Double Door |  |  | A04AR319 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) | A04AR319-00012 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame (UoM: EA) Fire Protective Rating: 3-hrs, Double Door w/ Hardware & Accessories | A04AR319 | 00012 | A04AR319-00012 | AR | A04 | Finishing Work | AR | Door & Window Work | 319 | Ballistic Resistant Door w/ Steel Frame (UoM: EA) | FK | Fire Protective Rating: 3-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR319 | A04AR319-00012
|  |  |  | A04AR320 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | A04AR320-00001 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) Fire Protective Rating: N/A w/ Hardware & Accessories | A04AR320 | 00001 | A04AR320-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 320 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | 89 | Fire Protective Rating: N/A |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR320 | A04AR320-00001
|  |  |  | A04AR320 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | A04AR320-00002 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) Fire Protective Rating: 0.5-hr w/ Hardware & Accessories | A04AR320 | 00002 | A04AR320-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 320 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR320 | A04AR320-00002
|  |  |  | A04AR320 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | A04AR320-00003 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) Fire Protective Rating: 1-hr w/ Hardware & Accessories | A04AR320 | 00003 | A04AR320-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 320 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | 95 | Fire Protective Rating: 1-hr |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR320 | A04AR320-00003
|  |  |  | A04AR320 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | A04AR320-00004 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) Fire Protective Rating: 1.5-hrs w/ Hardware & Accessories | A04AR320 | 00004 | A04AR320-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 320 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR320 | A04AR320-00004
|  |  |  | A04AR320 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | A04AR320-00005 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) Fire Protective Rating: 2-hrs w/ Hardware & Accessories | A04AR320 | 00005 | A04AR320-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 320 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | AF | Fire Protective Rating: 2-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR320 | A04AR320-00005
|  |  |  | A04AR320 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | A04AR320-00006 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) Fire Protective Rating: 3-hrs w/ Hardware & Accessories | A04AR320 | 00006 | A04AR320-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 320 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | FH | Fire Protective Rating: 3-hrs |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AR320 | A04AR320-00006
|  | 00001 | Fire Protective Rating: N/A, Single Door | A04AR321 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR321-00001 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories | A04AR321 | 00001 | A04AR321-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 321 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR321 | A04AR321-00001
00002 | Fire Protective Rating: N/A, Double Door |  |  | A04AR321 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR321-00002 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories | A04AR321 | 00002 | A04AR321-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 321 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR321 | A04AR321-00002
|  | 00003 | Fire Protective Rating: 0.5-hr, Single Door | A04AR321 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR321-00003 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 0.5-hr, Single Door w/ Hardware & Accessories | A04AR321 | 00003 | A04AR321-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 321 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR321 | A04AR321-00003
00004 | Fire Protective Rating: 0.5-hr, Double Door |  |  | A04AR321 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR321-00004 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 0.5-hr, Double Door w/ Hardware & Accessories | A04AR321 | 00004 | A04AR321-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 321 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR321 | A04AR321-00004
|  | 00005 | Fire Protective Rating: 1-hr, Single Door | A04AR321 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR321-00005 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 1-hr, Single Door w/ Hardware & Accessories | A04AR321 | 00005 | A04AR321-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 321 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR321 | A04AR321-00005
00006 | Fire Protective Rating: 1-hr, Double Door |  |  | A04AR321 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR321-00006 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 1-hr, Double Door w/ Hardware & Accessories | A04AR321 | 00006 | A04AR321-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 321 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR321 | A04AR321-00006
|  | 00007 | Fire Protective Rating: 1.5-hrs, Single Door | A04AR321 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR321-00007 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 1.5-hrs, Single Door w/ Hardware & Accessories | A04AR321 | 00007 | A04AR321-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 321 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR321 | A04AR321-00007
00008 | Fire Protective Rating: 1.5-hrs, Double Door |  |  | A04AR321 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR321-00008 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 1.5-hrs, Double Door w/ Hardware & Accessories | A04AR321 | 00008 | A04AR321-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 321 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR321 | A04AR321-00008
|  | 00009 | Fire Protective Rating: 2-hrs, Single Door | A04AR321 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR321-00009 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 2-hrs, Single Door w/ Hardware & Accessories | A04AR321 | 00009 | A04AR321-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 321 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AG | Fire Protective Rating: 2-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR321 | A04AR321-00009
00010 | Fire Protective Rating: 2-hrs, Double Door |  |  | A04AR321 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR321-00010 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 2-hrs, Double Door w/ Hardware & Accessories | A04AR321 | 00010 | A04AR321-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 321 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AH | Fire Protective Rating: 2-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR321 | A04AR321-00010
|  | 00011 | Fire Protective Rating: 3-hrs, Single Door | A04AR321 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR321-00011 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 3-hrs, Single Door w/ Hardware & Accessories | A04AR321 | 00011 | A04AR321-00011 | AR | A04 | Finishing Work | AR | Door & Window Work | 321 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | FJ | Fire Protective Rating: 3-hrs, Single Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR321 | A04AR321-00011
00012 | Fire Protective Rating: 3-hrs, Double Door |  |  | A04AR321 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | A04AR321-00012 Finishing Work Door & Window Work Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) Fire Protective Rating: 3-hrs, Double Door w/ Hardware & Accessories | A04AR321 | 00012 | A04AR321-00012 | AR | A04 | Finishing Work | AR | Door & Window Work | 321 | Ballistic Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | FK | Fire Protective Rating: 3-hrs, Double Door |  | 0 |  | 0 |  | 0 |  | 0 | 36 | w/ Hardware & Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AR321 | A04AR321-00012
|  |  |  | A04AS038 Finishing Work Exterior/Interior Finish Work Welded Wire Fabric | A04AS038-00001 Finishing Work Exterior/Interior Finish Work Welded Wire Fabric DIA≤6mm | A04AS038 | 00001 | A04AS038-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 038 | Welded Wire Fabric |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 53 | DIA≤6mm | 0 | Mesh Size=DIA( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS038 | A04AS038-00001
|  |  |  | A04AS038 Finishing Work Exterior/Interior Finish Work Welded Wire Fabric | A04AS038-00002 Finishing Work Exterior/Interior Finish Work Welded Wire Fabric DIA>6mm | A04AS038 | 00002 | A04AS038-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 038 | Welded Wire Fabric |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 54 | DIA>6mm | 0 | Mesh Size=DIA( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS038 | A04AS038-00002
|  |  |  | A04AS167 Finishing Work Exterior/Interior Finish Work Marble Window Sill | A04AS167-00001 Finishing Work Exterior/Interior Finish Work Marble Window Sill w/ Mortar Bond Coat or Adhesive | A04AS167 | 00001 | A04AS167-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 167 | Marble Window Sill |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | THK=( )mm / W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AS167 | A04AS167-00001
|  |  |  | A04AS168 Finishing Work Exterior/Interior Finish Work Screed | A04AS168-00001 Finishing Work Exterior/Interior Finish Work Screed w/o Welded Wire Fabric THK<50mm | A04AS168 | 00001 | A04AS168-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 168 | Screed |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 31 | w/o Welded Wire Fabric |  | 0 | 31 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS168 | A04AS168-00001
|  |  |  | A04AS168 Finishing Work Exterior/Interior Finish Work Screed | A04AS168-00002 Finishing Work Exterior/Interior Finish Work Screed w/o Welded Wire Fabric 50mm≤THK<75mm | A04AS168 | 00002 | A04AS168-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 168 | Screed |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 31 | w/o Welded Wire Fabric |  | 0 | 09 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS168 | A04AS168-00002
|  |  |  | A04AS168 Finishing Work Exterior/Interior Finish Work Screed | A04AS168-00003 Finishing Work Exterior/Interior Finish Work Screed w/o Welded Wire Fabric 75mm≤THK | A04AS168 | 00003 | A04AS168-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 168 | Screed |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 31 | w/o Welded Wire Fabric |  | 0 | 27 | 75mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS168 | A04AS168-00003
|  |  |  | A04AS169 Finishing Work Exterior/Interior Finish Work Carpet | A04AS169-00001 Finishing Work Exterior/Interior Finish Work Carpet | A04AS169 | 00001 | A04AS169-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 169 | Carpet |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS169 | A04AS169-00001
|  |  |  | A04AS170 Finishing Work Exterior/Interior Finish Work Carpet Tile | A04AS170-00001 Finishing Work Exterior/Interior Finish Work Carpet Tile | A04AS170 | 00001 | A04AS170-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 170 | Carpet Tile |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | Tile Size=W( )mm x L( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS170 | A04AS170-00001
|  |  |  | A04AS171 Finishing Work Exterior/Interior Finish Work Recess Floor Mat | A04AS171-00001 Finishing Work Exterior/Interior Finish Work Recess Floor Mat | A04AS171 | 00001 | A04AS171-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 171 | Recess Floor Mat |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS171 | A04AS171-00001
|  |  |  | A04AS172 Finishing Work Exterior/Interior Finish Work Entrance Floor Mats and Frame | A04AS172-00001 Finishing Work Exterior/Interior Finish Work Entrance Floor Mats and Frame | A04AS172 | 00001 | A04AS172-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 172 | Entrance Floor Mats and Frame |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS172 | A04AS172-00001
|  |  |  | A04AS172 Finishing Work Exterior/Interior Finish Work Entrance Floor Mats and Frame | A04AS172-00002 Finishing Work Exterior/Interior Finish Work Entrance Floor Mats and Frame Embedded Type | A04AS172 | 00002 | A04AS172-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 172 | Entrance Floor Mats and Frame | BL | Embedded Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS172 | A04AS172-00002
|  |  |  | A04AS173 Finishing Work Exterior/Interior Finish Work Steel Trowel Finish | A04AS173-00001 Finishing Work Exterior/Interior Finish Work Steel Trowel Finish | A04AS173 | 00001 | A04AS173-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 173 | Steel Trowel Finish |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS173 | A04AS173-00001
|  |  |  | A04AS173 Finishing Work Exterior/Interior Finish Work Steel Trowel Finish | A04AS173-00002 Finishing Work Exterior/Interior Finish Work Steel Trowel Finish Brushed(Broom) Finish | A04AS173 | 00002 | A04AS173-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 173 | Steel Trowel Finish | BM | Brushed(Broom) Finish |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS173 | A04AS173-00002
|  |  |  | A04AS173 Finishing Work Exterior/Interior Finish Work Steel Trowel Finish | A04AS173-00003 Finishing Work Exterior/Interior Finish Work Steel Trowel Finish Hardener Finish(Powder Type) | A04AS173 | 00003 | A04AS173-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 173 | Steel Trowel Finish | BN | Hardener Finish(Powder Type) |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS173 | A04AS173-00003
|  |  |  | A04AS173 Finishing Work Exterior/Interior Finish Work Steel Trowel Finish | A04AS173-00004 Finishing Work Exterior/Interior Finish Work Steel Trowel Finish Hardener Finish(Liquid Type) | A04AS173 | 00004 | A04AS173-00004 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 173 | Steel Trowel Finish | BP | Hardener Finish(Liquid Type) |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS173 | A04AS173-00004
|  |  |  | A04AS174 Finishing Work Exterior/Interior Finish Work Raised Floor | A04AS174-00001 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Anti-Static Vinyl Tile 600mm x 600mm / H≤600mm | A04AS174 | 00001 | A04AS174-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BQ | Top Finish: Anti-Static Vinyl Tile |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 73 | 600mm x 600mm / H≤600mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS174 | A04AS174-00001
|  |  |  | A04AS174 Finishing Work Exterior/Interior Finish Work Raised Floor | A04AS174-00002 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Anti-Static Vinyl Tile 600mm x 600mm / 600mm<H≤1000mm | A04AS174 | 00002 | A04AS174-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BQ | Top Finish: Anti-Static Vinyl Tile |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 74 | 600mm x 600mm / 600mm<H≤1000mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS174 | A04AS174-00002
|  |  |  | A04AS174 Finishing Work Exterior/Interior Finish Work Raised Floor | A04AS174-00003 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Anti-Static Vinyl Tile 600mm x 600mm / 1000mm<H≤1500mm | A04AS174 | 00003 | A04AS174-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BQ | Top Finish: Anti-Static Vinyl Tile |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 75 | 600mm x 600mm / 1000mm<H≤1500mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS174 | A04AS174-00003
|  |  |  | A04AS174 Finishing Work Exterior/Interior Finish Work Raised Floor | A04AS174-00004 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Carpet Tile 600mm x 600mm / H≤600mm | A04AS174 | 00004 | A04AS174-00004 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BR | Top Finish: Carpet Tile |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 73 | 600mm x 600mm / H≤600mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS174 | A04AS174-00004
|  |  |  | A04AS174 Finishing Work Exterior/Interior Finish Work Raised Floor | A04AS174-00005 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Carpet Tile 600mm x 600mm / 600mm<H≤1000mm | A04AS174 | 00005 | A04AS174-00005 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BR | Top Finish: Carpet Tile |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 74 | 600mm x 600mm / 600mm<H≤1000mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS174 | A04AS174-00005
|  |  |  | A04AS174 Finishing Work Exterior/Interior Finish Work Raised Floor | A04AS174-00006 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Carpet Tile 600mm x 600mm / 1000mm<H≤1500mm | A04AS174 | 00006 | A04AS174-00006 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BR | Top Finish: Carpet Tile |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 75 | 600mm x 600mm / 1000mm<H≤1500mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS174 | A04AS174-00006
|  |  |  | A04AS174 Finishing Work Exterior/Interior Finish Work Raised Floor | A04AS174-00007 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Marble 600mm x 600mm / H≤600mm | A04AS174 | 00007 | A04AS174-00007 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BS | Top Finish: Marble |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 73 | 600mm x 600mm / H≤600mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS174 | A04AS174-00007
|  |  |  | A04AS174 Finishing Work Exterior/Interior Finish Work Raised Floor | A04AS174-00008 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Marble 600mm x 600mm / 600mm<H≤1000mm | A04AS174 | 00008 | A04AS174-00008 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BS | Top Finish: Marble |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 74 | 600mm x 600mm / 600mm<H≤1000mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS174 | A04AS174-00008
|  |  |  | A04AS174 Finishing Work Exterior/Interior Finish Work Raised Floor | A04AS174-00009 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Marble 600mm x 600mm / 1000mm<H≤1500mm | A04AS174 | 00009 | A04AS174-00009 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BS | Top Finish: Marble |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 75 | 600mm x 600mm / 1000mm<H≤1500mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS174 | A04AS174-00009
|  |  |  | A04AS174 Finishing Work Exterior/Interior Finish Work Raised Floor | A04AS174-00010 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Anti-Static Vinyl Tile 600mm x 600mm / 1500mm≤H | A04AS174 | 00010 | A04AS174-00010 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BQ | Top Finish: Anti-Static Vinyl Tile |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AV | 600mm x 600mm / 1500mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS174 | A04AS174-00010
|  |  |  | A04AS174 Finishing Work Exterior/Interior Finish Work Raised Floor | A04AS174-00011 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Carpet Tile 600mm x 600mm / 1500mm≤H | A04AS174 | 00011 | A04AS174-00011 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BR | Top Finish: Carpet Tile |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AV | 600mm x 600mm / 1500mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS174 | A04AS174-00011
|  |  |  | A04AS174 Finishing Work Exterior/Interior Finish Work Raised Floor | A04AS174-00012 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Marble 600mm x 600mm / 1500mm≤H | A04AS174 | 00012 | A04AS174-00012 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BS | Top Finish: Marble |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AV | 600mm x 600mm / 1500mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS174 | A04AS174-00012
|  |  |  | A04AS174 Finishing Work Exterior/Interior Finish Work Raised Floor | A04AS174-00013 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Anti-Static Vinyl Tile 600mm x 600mm / 1500mm<H | A04AS174 | 00013 | A04AS174-00013 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BQ | Top Finish: Anti-Static Vinyl Tile |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AW | 600mm x 600mm / 1500mm<H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS174 | A04AS174-00013
|  |  |  | A04AS174 Finishing Work Exterior/Interior Finish Work Raised Floor | A04AS174-00014 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Carpet Tile 600mm x 600mm / 1500mm<H | A04AS174 | 00014 | A04AS174-00014 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BR | Top Finish: Carpet Tile |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AW | 600mm x 600mm / 1500mm<H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS174 | A04AS174-00014
|  |  |  | A04AS174 Finishing Work Exterior/Interior Finish Work Raised Floor | A04AS174-00015 Finishing Work Exterior/Interior Finish Work Raised Floor Top Finish: Marble 600mm x 600mm / 1500mm<H | A04AS174 | 00015 | A04AS174-00015 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BS | Top Finish: Marble |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | AW | 600mm x 600mm / 1500mm<H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS174 | A04AS174-00015
|  |  |  | A04AS175 Finishing Work Exterior/Interior Finish Work Material Dividing Strip | A04AS175-00001 Finishing Work Exterior/Interior Finish Work Material Dividing Strip Stainless Steel | A04AS175 | 00001 | A04AS175-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 175 | Material Dividing Strip | BT | Stainless Steel |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AS175 | A04AS175-00001
|  |  |  | A04AS176 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System | A04AS176-00001 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Mineral Wool (Rock Wool) for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS176 | 00001 | A04AS176-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System |  | 0 |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS176 | A04AS176-00001
|  |  |  | A04AS176 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System | A04AS176-00002 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Mineral Wool (Rock Wool) for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS176 | 00002 | A04AS176-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System |  | 0 |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS176 | A04AS176-00002
|  |  |  | A04AS176 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System | A04AS176-00003 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Mineral Wool (Rock Wool) for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=16mm | A04AS176 | 00003 | A04AS176-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System |  | 0 |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS176 | A04AS176-00003
|  |  |  | A04AS176 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System | A04AS176-00004 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Glass Wool (Fiberglass) for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS176 | 00004 | A04AS176-00004 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System |  | 0 |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS176 | A04AS176-00004
|  |  |  | A04AS176 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System | A04AS176-00005 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Glass Wool (Fiberglass) for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS176 | 00005 | A04AS176-00005 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System |  | 0 |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS176 | A04AS176-00005
|  |  |  | A04AS176 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System | A04AS176-00006 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Glass Wool (Fiberglass) for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=16mm | A04AS176 | 00006 | A04AS176-00006 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System |  | 0 |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS176 | A04AS176-00006
|  |  |  | A04AS176 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System | A04AS176-00007 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Rigid Insulation for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS176 | 00007 | A04AS176-00007 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System |  | 0 |  | 0 |  | 0 | 05 | Rigid Insulation | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS176 | A04AS176-00007
|  |  |  | A04AS176 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System | A04AS176-00008 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Rigid Insulation for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS176 | 00008 | A04AS176-00008 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System |  | 0 |  | 0 |  | 0 | 05 | Rigid Insulation | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS176 | A04AS176-00008
|  |  |  | A04AS176 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System | A04AS176-00009 Finishing Work Exterior/Interior Finish Work Plasterboard Dry Liner System Rigid Insulation for Wall To External Side w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories 1-Layer Gypsumboard THK=16mm | A04AS176 | 00009 | A04AS176-00009 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System |  | 0 |  | 0 |  | 0 | 05 | Rigid Insulation | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS176 | A04AS176-00009
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00001 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177 | 00001 | A04AS177-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BU | Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side |  | 0 |  | 0 | 02 | w/o Insulation |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00001
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00002 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177 | 00002 | A04AS177-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BU | Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side |  | 0 |  | 0 | 02 | w/o Insulation |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00002
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00003 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS177 | 00003 | A04AS177-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BU | Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side |  | 0 |  | 0 | 02 | w/o Insulation |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00003
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00004 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177 | 00004 | A04AS177-00004 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BV | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side |  | 0 |  | 0 | 02 | w/o Insulation |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00004
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00005 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177 | 00005 | A04AS177-00005 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BV | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side |  | 0 |  | 0 | 02 | w/o Insulation |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00005
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00006 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS177 | 00006 | A04AS177-00006 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BV | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side |  | 0 |  | 0 | 02 | w/o Insulation |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00006
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00007 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177 | 00007 | A04AS177-00007 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00007
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00008 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177 | 00008 | A04AS177-00008 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00008
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00009 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS177 | 00009 | A04AS177-00009 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00009
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00010 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177 | 00010 | A04AS177-00010 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00010
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00011 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177 | 00011 | A04AS177-00011 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00011
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00012 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS177 | 00012 | A04AS177-00012 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00012
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00013 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177 | 00013 | A04AS177-00013 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 02 | w/o Insulation |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00013
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00014 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177 | 00014 | A04AS177-00014 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 02 | w/o Insulation |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00014
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00015 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS177 | 00015 | A04AS177-00015 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 02 | w/o Insulation |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00015
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00016 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177 | 00016 | A04AS177-00016 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00016
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00017 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177 | 00017 | A04AS177-00017 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00017
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00018 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS177 | 00018 | A04AS177-00018 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00018
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00019 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177 | 00019 | A04AS177-00019 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00019
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00020 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177 | 00020 | A04AS177-00020 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00020
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00021 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS177 | 00021 | A04AS177-00021 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00021
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00022 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177 | 00022 | A04AS177-00022 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 02 | w/o Insulation |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00022
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00023 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177 | 00023 | A04AS177-00023 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 02 | w/o Insulation |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00023
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00024 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS177 | 00024 | A04AS177-00024 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 02 | w/o Insulation |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00024
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00025 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177 | 00025 | A04AS177-00025 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CB | Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00025
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00026 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177 | 00026 | A04AS177-00026 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CB | Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00026
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00027 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS177 | 00027 | A04AS177-00027 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CB | Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00027
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00028 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177 | 00028 | A04AS177-00028 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CB | Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00028
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00029 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177 | 00029 | A04AS177-00029 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CB | Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00029
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00030 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS177 | 00030 | A04AS177-00030 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CB | Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00030
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00031 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177 | 00031 | A04AS177-00031 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CC | Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00031
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00032 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177 | 00032 | A04AS177-00032 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CC | Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00032
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00033 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS177 | 00033 | A04AS177-00033 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CC | Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00033
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00034 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS177 | 00034 | A04AS177-00034 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CC | Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00034
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00035 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS177 | 00035 | A04AS177-00035 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CC | Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00035
|  |  |  | A04AS177 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) | A04AS177-00036 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Fixed Type) Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS177 | 00036 | A04AS177-00036 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CC | Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS177 | A04AS177-00036
|  |  |  | A04AS178 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) | A04AS178-00001 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS178 | 00001 | A04AS178-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS178 | A04AS178-00001
|  |  |  | A04AS178 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) | A04AS178-00002 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS178 | 00002 | A04AS178-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS178 | A04AS178-00002
|  |  |  | A04AS178 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) | A04AS178-00003 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides Mineral Wool (Rock Wool) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS178 | 00003 | A04AS178-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS178 | A04AS178-00003
|  |  |  | A04AS178 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) | A04AS178-00004 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS178 | 00004 | A04AS178-00004 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS178 | A04AS178-00004
|  |  |  | A04AS178 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) | A04AS178-00005 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS178 | 00005 | A04AS178-00005 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS178 | A04AS178-00005
|  |  |  | A04AS178 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) | A04AS178-00006 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides Glass Wool (Fiberglass) Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS178 | 00006 | A04AS178-00006 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 | Insulation THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS178 | A04AS178-00006
|  |  |  | A04AS178 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) | A04AS178-00007 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=9.5mm | A04AS178 | 00007 | A04AS178-00007 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 02 | w/o Insulation |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 76 | 1-Layer Gypsumboard THK=9.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS178 | A04AS178-00007
|  |  |  | A04AS178 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) | A04AS178-00008 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=12.5mm | A04AS178 | 00008 | A04AS178-00008 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 02 | w/o Insulation |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS178 | A04AS178-00008
|  |  |  | A04AS178 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) | A04AS178-00009 Finishing Work Exterior/Interior Finish Work Gypsumboard Partition Wall (Removable Type) Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides w/o Insulation Including Supporting Frame(Stud) & Accessories 1-Layer Gypsumboard THK=16mm | A04AS178 | 00009 | A04AS178-00009 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  | 0 |  | 0 | 02 | w/o Insulation |  | 0 | 39 | Including Supporting Frame(Stud) & Accessories |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS178 | A04AS178-00009
|  |  |  | A04AS179 Finishing Work Exterior/Interior Finish Work Cubicle Partition | A04AS179-00001 Finishing Work Exterior/Interior Finish Work Cubicle Partition for Toilet w/ Accessories | A04AS179 | 00001 | A04AS179-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 179 | Cubicle Partition |  | 0 |  | 0 |  | 0 |  | 0 | 07 | for Toilet | 32 | w/ Accessories |  | 0 |  | 0 | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AS179 | A04AS179-00001
|  |  |  | A04AS180 Finishing Work Exterior/Interior Finish Work Shower Booth Partition | A04AS180-00001 Finishing Work Exterior/Interior Finish Work Shower Booth Partition w/ Accessories | A04AS180 | 00001 | A04AS180-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 180 | Shower Booth Partition |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 32 | w/ Accessories |  | 0 |  | 0 | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AS180 | A04AS180-00001
|  |  |  | A04AS181 Finishing Work Exterior/Interior Finish Work Acoustic Panel | A04AS181-00001 Finishing Work Exterior/Interior Finish Work Acoustic Panel for Wall w/ Accessories (Supporting Frame, Acoustic Insulation, Etc.) | A04AS181 | 00001 | A04AS181-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 181 | Acoustic Panel |  | 0 |  | 0 |  | 0 |  | 0 | 08 | for Wall | 40 | w/ Accessories (Supporting Frame, Acoustic Insulation, Etc.) |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS181 | A04AS181-00001
|  |  |  | A04AS182 Finishing Work Exterior/Interior Finish Work Face Brick | A04AS182-00001 Finishing Work Exterior/Interior Finish Work Face Brick w/ Bedding | A04AS182 | 00001 | A04AS182-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 182 | Face Brick |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 41 | w/ Bedding |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS182 | A04AS182-00001
|  |  |  | A04AS183 Finishing Work Exterior/Interior Finish Work Hard Wood Trim | A04AS183-00001 Finishing Work Exterior/Interior Finish Work Hard Wood Trim for Wall H<150mm | A04AS183 | 00001 | A04AS183-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 183 | Hard Wood Trim |  | 0 |  | 0 |  | 0 |  | 0 | 08 | for Wall |  | 0 |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AS183 | A04AS183-00001
|  |  |  | A04AS183 Finishing Work Exterior/Interior Finish Work Hard Wood Trim | A04AS183-00002 Finishing Work Exterior/Interior Finish Work Hard Wood Trim for Wall 150mm≤H<200mm | A04AS183 | 00002 | A04AS183-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 183 | Hard Wood Trim |  | 0 |  | 0 |  | 0 |  | 0 | 08 | for Wall |  | 0 |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AS183 | A04AS183-00002
|  |  |  | A04AS183 Finishing Work Exterior/Interior Finish Work Hard Wood Trim | A04AS183-00003 Finishing Work Exterior/Interior Finish Work Hard Wood Trim for Wall 200mm≤H | A04AS183 | 00003 | A04AS183-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 183 | Hard Wood Trim |  | 0 |  | 0 |  | 0 |  | 0 | 08 | for Wall |  | 0 |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AS183 | A04AS183-00003
|  |  |  | A04AS184 Finishing Work Exterior/Interior Finish Work Aluminum Baseboard | A04AS184-00001 Finishing Work Exterior/Interior Finish Work Aluminum Baseboard for Skirt w/ Adhesive H<150mm | A04AS184 | 00001 | A04AS184-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 184 | Aluminum Baseboard |  | 0 |  | 0 |  | 0 |  | 0 | 09 | for Skirt | 42 | w/ Adhesive |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AS184 | A04AS184-00001
|  |  |  | A04AS184 Finishing Work Exterior/Interior Finish Work Aluminum Baseboard | A04AS184-00002 Finishing Work Exterior/Interior Finish Work Aluminum Baseboard for Skirt w/ Adhesive 150mm≤H<200mm | A04AS184 | 00002 | A04AS184-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 184 | Aluminum Baseboard |  | 0 |  | 0 |  | 0 |  | 0 | 09 | for Skirt | 42 | w/ Adhesive |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AS184 | A04AS184-00002
|  |  |  | A04AS184 Finishing Work Exterior/Interior Finish Work Aluminum Baseboard | A04AS184-00003 Finishing Work Exterior/Interior Finish Work Aluminum Baseboard for Skirt w/ Adhesive 200mm≤H | A04AS184 | 00003 | A04AS184-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 184 | Aluminum Baseboard |  | 0 |  | 0 |  | 0 |  | 0 | 09 | for Skirt | 42 | w/ Adhesive |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AS184 | A04AS184-00003
|  |  |  | A04AS185 Finishing Work Exterior/Interior Finish Work Coved Rubber Skirting | A04AS185-00001 Finishing Work Exterior/Interior Finish Work Coved Rubber Skirting for Skirt w/ Adhesive H<150mm | A04AS185 | 00001 | A04AS185-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 185 | Coved Rubber Skirting |  | 0 |  | 0 |  | 0 |  | 0 | 09 | for Skirt | 42 | w/ Adhesive |  | 0 | 86 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AS185 | A04AS185-00001
|  |  |  | A04AS185 Finishing Work Exterior/Interior Finish Work Coved Rubber Skirting | A04AS185-00002 Finishing Work Exterior/Interior Finish Work Coved Rubber Skirting for Skirt w/ Adhesive 150mm≤H<200mm | A04AS185 | 00002 | A04AS185-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 185 | Coved Rubber Skirting |  | 0 |  | 0 |  | 0 |  | 0 | 09 | for Skirt | 42 | w/ Adhesive |  | 0 | 67 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AS185 | A04AS185-00002
|  |  |  | A04AS185 Finishing Work Exterior/Interior Finish Work Coved Rubber Skirting | A04AS185-00003 Finishing Work Exterior/Interior Finish Work Coved Rubber Skirting for Skirt w/ Adhesive 200mm≤H | A04AS185 | 00003 | A04AS185-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 185 | Coved Rubber Skirting |  | 0 |  | 0 |  | 0 |  | 0 | 09 | for Skirt | 42 | w/ Adhesive |  | 0 | 68 | 200mm≤H | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AS185 | A04AS185-00003
|  |  |  | A04AS186 Finishing Work Exterior/Interior Finish Work Fiber Board Ceiling System | A04AS186-00001 Finishing Work Exterior/Interior Finish Work Fiber Board Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS186 | 00001 | A04AS186-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 186 | Fiber Board Ceiling System | CD | M-Bar System |  | 0 |  | 0 |  | 0 |  | 0 | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  | 0 |  | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS186 | A04AS186-00001
|  |  |  | A04AS186 Finishing Work Exterior/Interior Finish Work Fiber Board Ceiling System | A04AS186-00002 Finishing Work Exterior/Interior Finish Work Fiber Board Ceiling System T-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS186 | 00002 | A04AS186-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 186 | Fiber Board Ceiling System | CE | T-Bar System |  | 0 |  | 0 |  | 0 |  | 0 | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  | 0 |  | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS186 | A04AS186-00002
|  |  |  | A04AS187 Finishing Work Exterior/Interior Finish Work Gypsum Plaster Board Ceiling System | A04AS187-00001 Finishing Work Exterior/Interior Finish Work Gypsum Plaster Board Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) 1-Layer Gypsumboard THK=12.5mm | A04AS187 | 00001 | A04AS187-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 187 | Gypsum Plaster Board Ceiling System | CD | M-Bar System |  | 0 |  | 0 |  | 0 |  | 0 | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS187 | A04AS187-00001
|  |  |  | A04AS187 Finishing Work Exterior/Interior Finish Work Gypsum Plaster Board Ceiling System | A04AS187-00002 Finishing Work Exterior/Interior Finish Work Gypsum Plaster Board Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) 1-Layer Gypsumboard THK=16mm | A04AS187 | 00002 | A04AS187-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 187 | Gypsum Plaster Board Ceiling System | CD | M-Bar System |  | 0 |  | 0 |  | 0 |  | 0 | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS187 | A04AS187-00002
|  |  |  | A04AS188 Finishing Work Exterior/Interior Finish Work Moisture Resistant Gypsum Plaster Board Ceiling System | A04AS188-00001 Finishing Work Exterior/Interior Finish Work Moisture Resistant Gypsum Plaster Board Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) 1-Layer Gypsumboard THK=12.5mm | A04AS188 | 00001 | A04AS188-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 188 | Moisture Resistant Gypsum Plaster Board Ceiling System | CD | M-Bar System |  | 0 |  | 0 |  | 0 |  | 0 | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  | 0 | 77 | 1-Layer Gypsumboard THK=12.5mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS188 | A04AS188-00001
|  |  |  | A04AS188 Finishing Work Exterior/Interior Finish Work Moisture Resistant Gypsum Plaster Board Ceiling System | A04AS188-00002 Finishing Work Exterior/Interior Finish Work Moisture Resistant Gypsum Plaster Board Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) 1-Layer Gypsumboard THK=16mm | A04AS188 | 00002 | A04AS188-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 188 | Moisture Resistant Gypsum Plaster Board Ceiling System | CD | M-Bar System |  | 0 |  | 0 |  | 0 |  | 0 | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  | 0 | 78 | 1-Layer Gypsumboard THK=16mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS188 | A04AS188-00002
|  |  |  | A04AS189 Finishing Work Exterior/Interior Finish Work Cement Board Ceiling System | A04AS189-00001 Finishing Work Exterior/Interior Finish Work Cement Board Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS189 | 00001 | A04AS189-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 189 | Cement Board Ceiling System | CD | M-Bar System |  | 0 |  | 0 |  | 0 |  | 0 | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  | 0 |  | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS189 | A04AS189-00001
|  |  |  | A04AS189 Finishing Work Exterior/Interior Finish Work Cement Board Ceiling System | A04AS189-00002 Finishing Work Exterior/Interior Finish Work Cement Board Ceiling System T-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS189 | 00002 | A04AS189-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 189 | Cement Board Ceiling System | CE | T-Bar System |  | 0 |  | 0 |  | 0 |  | 0 | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  | 0 |  | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS189 | A04AS189-00002
|  |  |  | A04AS190 Finishing Work Exterior/Interior Finish Work Acoustic Tiled Ceiling System | A04AS190-00001 Finishing Work Exterior/Interior Finish Work Acoustic Tiled Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS190 | 00001 | A04AS190-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 190 | Acoustic Tiled Ceiling System | CD | M-Bar System |  | 0 |  | 0 |  | 0 |  | 0 | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  | 0 |  | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS190 | A04AS190-00001
|  |  |  | A04AS190 Finishing Work Exterior/Interior Finish Work Acoustic Tiled Ceiling System | A04AS190-00002 Finishing Work Exterior/Interior Finish Work Acoustic Tiled Ceiling System T-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS190 | 00002 | A04AS190-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 190 | Acoustic Tiled Ceiling System | CE | T-Bar System |  | 0 |  | 0 |  | 0 |  | 0 | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  | 0 |  | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS190 | A04AS190-00002
|  |  |  | A04AS191 Finishing Work Exterior/Interior Finish Work Moisture Resistant Tiled Ceiling System | A04AS191-00001 Finishing Work Exterior/Interior Finish Work Moisture Resistant Tiled Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS191 | 00001 | A04AS191-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 191 | Moisture Resistant Tiled Ceiling System | CD | M-Bar System |  | 0 |  | 0 |  | 0 |  | 0 | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  | 0 |  | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS191 | A04AS191-00001
|  |  |  | A04AS191 Finishing Work Exterior/Interior Finish Work Moisture Resistant Tiled Ceiling System | A04AS191-00002 Finishing Work Exterior/Interior Finish Work Moisture Resistant Tiled Ceiling System T-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS191 | 00002 | A04AS191-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 191 | Moisture Resistant Tiled Ceiling System | CE | T-Bar System |  | 0 |  | 0 |  | 0 |  | 0 | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  | 0 |  | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS191 | A04AS191-00002
|  |  |  | A04AS192 Finishing Work Exterior/Interior Finish Work Aluminum Spandrel Ceiling System | A04AS192-00001 Finishing Work Exterior/Interior Finish Work Aluminum Spandrel Ceiling System M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS192 | 00001 | A04AS192-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 192 | Aluminum Spandrel Ceiling System | CD | M-Bar System |  | 0 |  | 0 |  | 0 |  | 0 | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS192 | A04AS192-00001
|  |  |  | A04AS193 Finishing Work Exterior/Interior Finish Work Metal Open Cell Ceiling | A04AS193-00001 Finishing Work Exterior/Interior Finish Work Metal Open Cell Ceiling M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | A04AS193 | 00001 | A04AS193-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 193 | Metal Open Cell Ceiling | CD | M-Bar System |  | 0 |  | 0 |  | 0 |  | 0 | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS193 | A04AS193-00001
|  |  |  | A04AS194 Finishing Work Exterior/Interior Finish Work Rigid Insulation | A04AS194-00001 Finishing Work Exterior/Interior Finish Work Rigid Insulation for Exposed Ceiling Structure of Cable Room w/ Accessories THK<50mm | A04AS194 | 00001 | A04AS194-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 194 | Rigid Insulation |  | 0 |  | 0 |  | 0 |  | 0 | 10 | for Exposed Ceiling Structure of Cable Room | 32 | w/ Accessories |  | 0 | 31 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS194 | A04AS194-00001
|  |  |  | A04AS194 Finishing Work Exterior/Interior Finish Work Rigid Insulation | A04AS194-00002 Finishing Work Exterior/Interior Finish Work Rigid Insulation for Exposed Ceiling Structure of Cable Room w/ Accessories 50mm≤THK<75mm | A04AS194 | 00002 | A04AS194-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 194 | Rigid Insulation |  | 0 |  | 0 |  | 0 |  | 0 | 10 | for Exposed Ceiling Structure of Cable Room | 32 | w/ Accessories |  | 0 | 09 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS194 | A04AS194-00002
|  |  |  | A04AS194 Finishing Work Exterior/Interior Finish Work Rigid Insulation | A04AS194-00003 Finishing Work Exterior/Interior Finish Work Rigid Insulation for Exposed Ceiling Structure of Cable Room w/ Accessories 75mm≤THK | A04AS194 | 00003 | A04AS194-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 194 | Rigid Insulation |  | 0 |  | 0 |  | 0 |  | 0 | 10 | for Exposed Ceiling Structure of Cable Room | 32 | w/ Accessories |  | 0 | 27 | 75mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS194 | A04AS194-00003
|  |  |  | A04AS194 Finishing Work Exterior/Interior Finish Work Rigid Insulation | A04AS194-00004 Finishing Work Exterior/Interior Finish Work Rigid Insulation for Exposed Wall Structure of Cable Room w/ Accessories THK<50mm | A04AS194 | 00004 | A04AS194-00004 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 194 | Rigid Insulation |  | 0 |  | 0 |  | 0 |  | 0 | 11 | for Exposed Wall Structure of Cable Room | 32 | w/ Accessories |  | 0 | 31 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS194 | A04AS194-00004
|  |  |  | A04AS194 Finishing Work Exterior/Interior Finish Work Rigid Insulation | A04AS194-00005 Finishing Work Exterior/Interior Finish Work Rigid Insulation for Exposed Wall Structure of Cable Room w/ Accessories 50mm≤THK<75mm | A04AS194 | 00005 | A04AS194-00005 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 194 | Rigid Insulation |  | 0 |  | 0 |  | 0 |  | 0 | 11 | for Exposed Wall Structure of Cable Room | 32 | w/ Accessories |  | 0 | 09 | 50mm≤THK<75mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS194 | A04AS194-00005
|  |  |  | A04AS194 Finishing Work Exterior/Interior Finish Work Rigid Insulation | A04AS194-00006 Finishing Work Exterior/Interior Finish Work Rigid Insulation for Exposed Wall Structure of Cable Room w/ Accessories 75mm≤THK | A04AS194 | 00006 | A04AS194-00006 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 194 | Rigid Insulation |  | 0 |  | 0 |  | 0 |  | 0 | 11 | for Exposed Wall Structure of Cable Room | 32 | w/ Accessories |  | 0 | 27 | 75mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS194 | A04AS194-00006
|  |  |  | A04AS195 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy | A04AS195-00001 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy Steel Canopy w/ Supporting Frame, Accessories | A04AS195 | 00001 | A04AS195-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CF | Steel Canopy |  | 0 |  | 0 |  | 0 |  | 0 | 44 | w/ Supporting Frame, Accessories |  | 0 |  | 0 | 0 | W x L x Min. D=( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AS195 | A04AS195-00001
|  |  |  | A04AS195 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy | A04AS195-00002 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy Stainless Steel Canopy w/ Supporting Frame, Accessories | A04AS195 | 00002 | A04AS195-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CG | Stainless Steel Canopy |  | 0 |  | 0 |  | 0 |  | 0 | 44 | w/ Supporting Frame, Accessories |  | 0 |  | 0 | 0 | W x L x Min. D=( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AS195 | A04AS195-00002
|  |  |  | A04AS195 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy | A04AS195-00003 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy Aluminum Canopy w/ Supporting Frame, Accessories | A04AS195 | 00003 | A04AS195-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CH | Aluminum Canopy |  | 0 |  | 0 |  | 0 |  | 0 | 44 | w/ Supporting Frame, Accessories |  | 0 |  | 0 | 0 | W x L x Min. D=( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AS195 | A04AS195-00003
|  |  |  | A04AS195 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy | A04AS195-00004 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy Polycarbonate Canopy w/ Supporting Frame, Accessories | A04AS195 | 00004 | A04AS195-00004 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CJ | Polycarbonate Canopy |  | 0 |  | 0 |  | 0 |  | 0 | 44 | w/ Supporting Frame, Accessories |  | 0 |  | 0 | 0 | W x L x Min. D=( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AS195 | A04AS195-00004
|  |  |  | A04AS195 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy | A04AS195-00005 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy GRP Canopy w/ Supporting Frame, Accessories | A04AS195 | 00005 | A04AS195-00005 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CK | GRP Canopy |  | 0 |  | 0 |  | 0 |  | 0 | 44 | w/ Supporting Frame, Accessories |  | 0 |  | 0 | 0 | W x L x Min. D=( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AS195 | A04AS195-00005
|  |  |  | A04AS195 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy | A04AS195-00006 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy Steel Canopy (Continuous Type) along Walkway, w/ Supporting Frame, Accessories | A04AS195 | 00006 | A04AS195-00006 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CL | Steel Canopy (Continuous Type) |  | 0 |  | 0 |  | 0 |  | 0 | 45 | along Walkway, w/ Supporting Frame, Accessories |  | 0 |  | 0 | 0 | W x Min. D=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | M | A04AS195 | A04AS195-00006
|  |  |  | A04AS195 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy | A04AS195-00007 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy Polycarbonate Canopy (Continuous Type) along Walkway, w/ Supporting Frame, Accessories | A04AS195 | 00007 | A04AS195-00007 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CM | Polycarbonate Canopy (Continuous Type) |  | 0 |  | 0 |  | 0 |  | 0 | 45 | along Walkway, w/ Supporting Frame, Accessories |  | 0 |  | 0 | 0 | W x Min. D=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | M | A04AS195 | A04AS195-00007
|  |  |  | A04AS195 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy | A04AS195-00008 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy Steel Canopy (Rounded Type) w/ Supporting Frame, Accessories | A04AS195 | 00008 | A04AS195-00008 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CN | Steel Canopy (Rounded Type) |  | 0 |  | 0 |  | 0 |  | 0 | 44 | w/ Supporting Frame, Accessories |  | 0 |  | 0 | 0 | W x H x Min. D=( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AS195 | A04AS195-00008
|  |  |  | A04AS195 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy | A04AS195-00009 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy Stainless Steel Canopy (Rounded Type) w/ Supporting Frame, Accessories | A04AS195 | 00009 | A04AS195-00009 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CP | Stainless Steel Canopy (Rounded Type) |  | 0 |  | 0 |  | 0 |  | 0 | 44 | w/ Supporting Frame, Accessories |  | 0 |  | 0 | 0 | W x H x Min. D=( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AS195 | A04AS195-00009
|  |  |  | A04AS195 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy | A04AS195-00010 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy Aluminum Canopy (Rounded Type) w/ Supporting Frame, Accessories | A04AS195 | 00010 | A04AS195-00010 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CQ | Aluminum Canopy (Rounded Type) |  | 0 |  | 0 |  | 0 |  | 0 | 44 | w/ Supporting Frame, Accessories |  | 0 |  | 0 | 0 | W x H x Min. D=( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AS195 | A04AS195-00010
|  |  |  | A04AS195 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy | A04AS195-00011 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy Polycarbonate Canopy (Rounded Type) w/ Supporting Frame, Accessories | A04AS195 | 00011 | A04AS195-00011 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CR | Polycarbonate Canopy (Rounded Type) |  | 0 |  | 0 |  | 0 |  | 0 | 44 | w/ Supporting Frame, Accessories |  | 0 |  | 0 | 0 | W x H x Min. D=( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AS195 | A04AS195-00011
|  |  |  | A04AS195 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy | A04AS195-00012 Finishing Work Exterior/Interior Finish Work Pre-Fabricated Canopy GRP Canopy (Rounded Type) w/ Supporting Frame, Accessories | A04AS195 | 00012 | A04AS195-00012 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CS | GRP Canopy (Rounded Type) |  | 0 |  | 0 |  | 0 |  | 0 | 44 | w/ Supporting Frame, Accessories |  | 0 |  | 0 | 0 | W x H x Min. D=( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AS195 | A04AS195-00012
|  |  |  | A04AS196 Finishing Work Exterior/Interior Finish Work Custom-Made Canopy for Main Entrance | A04AS196-00001 Finishing Work Exterior/Interior Finish Work Custom-Made Canopy for Main Entrance Steel Canopy w/ Supporting Frame, Accessories, Lighting Fixtures | A04AS196 | 00001 | A04AS196-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 196 | Custom-Made Canopy for Main Entrance | CF | Steel Canopy |  | 0 |  | 0 |  | 0 |  | 0 | 46 | w/ Supporting Frame, Accessories, Lighting Fixtures |  | 0 |  | 0 | 0 | W x H x Min. D=( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | SET | SET | A04AS196 | A04AS196-00001
|  |  |  | A04AS196 Finishing Work Exterior/Interior Finish Work Custom-Made Canopy for Main Entrance | A04AS196-00002 Finishing Work Exterior/Interior Finish Work Custom-Made Canopy for Main Entrance Stainless Steel Canopy w/ Supporting Frame, Accessories, Lighting Fixtures | A04AS196 | 00002 | A04AS196-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 196 | Custom-Made Canopy for Main Entrance | CG | Stainless Steel Canopy |  | 0 |  | 0 |  | 0 |  | 0 | 46 | w/ Supporting Frame, Accessories, Lighting Fixtures |  | 0 |  | 0 | 0 | W x H x Min. D=( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | SET | SET | A04AS196 | A04AS196-00002
|  |  |  | A04AS196 Finishing Work Exterior/Interior Finish Work Custom-Made Canopy for Main Entrance | A04AS196-00003 Finishing Work Exterior/Interior Finish Work Custom-Made Canopy for Main Entrance Aluminum Canopy w/ Supporting Frame, Accessories, Lighting Fixtures | A04AS196 | 00003 | A04AS196-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 196 | Custom-Made Canopy for Main Entrance | CH | Aluminum Canopy |  | 0 |  | 0 |  | 0 |  | 0 | 46 | w/ Supporting Frame, Accessories, Lighting Fixtures |  | 0 |  | 0 | 0 | W x H x Min. D=( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | SET | SET | A04AS196 | A04AS196-00003
|  |  |  | A04AS197 Finishing Work Exterior/Interior Finish Work Roof Tile | A04AS197-00001 Finishing Work Exterior/Interior Finish Work Roof Tile Metallic Tile w/ Insulation w/ Mortar Bond Coat or Adhesive | A04AS197 | 00001 | A04AS197-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 197 | Roof Tile | CT | Metallic Tile w/ Insulation |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS197 | A04AS197-00001
|  |  |  | A04AS197 Finishing Work Exterior/Interior Finish Work Roof Tile | A04AS197-00002 Finishing Work Exterior/Interior Finish Work Roof Tile Metallic Tile w/o Insulation w/ Mortar Bond Coat or Adhesive | A04AS197 | 00002 | A04AS197-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 197 | Roof Tile | CU | Metallic Tile w/o Insulation |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS197 | A04AS197-00002
|  |  |  | A04AS314 Finishing Work Exterior/Interior Finish Work Plywood w/ Fire Retardant Paint | A04AS314-00001 Finishing Work Exterior/Interior Finish Work Plywood w/ Fire Retardant Paint | A04AS314 | 00001 | A04AS314-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 314 | Plywood w/ Fire Retardant Paint |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AS314 | A04AS314-00001
|  |  |  | A04AT198 Finishing Work Plastering Work Plastering | A04AT198-00001 Finishing Work Plastering Work Plastering for External Masonry Wall | A04AT198 | 00001 | A04AT198-00001 | AR | A04 | Finishing Work | AT | Plastering Work | 198 | Plastering |  | 0 |  | 0 |  | 0 |  | 0 | 12 | for External Masonry Wall |  |  |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AT198 | A04AT198-00001
|  |  |  | A04AT198 Finishing Work Plastering Work Plastering | A04AT198-00002 Finishing Work Plastering Work Plastering for Internal Masonry Wall | A04AT198 | 00002 | A04AT198-00002 | AR | A04 | Finishing Work | AT | Plastering Work | 198 | Plastering |  | 0 |  | 0 |  | 0 |  | 0 | 13 | for Internal Masonry Wall |  |  |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AT198 | A04AT198-00002
|  |  |  | A04AT198 Finishing Work Plastering Work Plastering | A04AT198-00003 Finishing Work Plastering Work Plastering for Exposed Conc. Surface | A04AT198 | 00003 | A04AT198-00003 | AR | A04 | Finishing Work | AT | Plastering Work | 198 | Plastering |  | 0 |  | 0 |  | 0 |  | 0 | 14 | for Exposed Conc. Surface |  |  |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AT198 | A04AT198-00003
|  |  |  | A04AV205 Finishing Work Misc. Work Roof Drain (for Building) | A04AV205-00001 Finishing Work Misc. Work Roof Drain (for Building) Cast Iron Type DIA=100mm | A04AV205 | 00001 | A04AV205-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | DQ | Cast Iron Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 56 | DIA=100mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV205 | A04AV205-00001
|  |  |  | A04AV205 Finishing Work Misc. Work Roof Drain (for Building) | A04AV205-00002 Finishing Work Misc. Work Roof Drain (for Building) Cast Iron Type DIA=150mm | A04AV205 | 00002 | A04AV205-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | DQ | Cast Iron Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 57 | DIA=150mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV205 | A04AV205-00002
|  |  |  | A04AV205 Finishing Work Misc. Work Roof Drain (for Building) | A04AV205-00003 Finishing Work Misc. Work Roof Drain (for Building) Cast Iron Type DIA=200mm | A04AV205 | 00003 | A04AV205-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | DQ | Cast Iron Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 58 | DIA=200mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV205 | A04AV205-00003
|  |  |  | A04AV205 Finishing Work Misc. Work Roof Drain (for Building) | A04AV205-00004 Finishing Work Misc. Work Roof Drain (for Building) Cast Iron Type DIA=250mm | A04AV205 | 00004 | A04AV205-00004 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | DQ | Cast Iron Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 59 | DIA=250mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV205 | A04AV205-00004
|  |  |  | A04AV205 Finishing Work Misc. Work Roof Drain (for Building) | A04AV205-00005 Finishing Work Misc. Work Roof Drain (for Building) PVC Type DIA=100mm | A04AV205 | 00005 | A04AV205-00005 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 56 | DIA=100mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV205 | A04AV205-00005
|  |  |  | A04AV205 Finishing Work Misc. Work Roof Drain (for Building) | A04AV205-00006 Finishing Work Misc. Work Roof Drain (for Building) PVC Type DIA=150mm | A04AV205 | 00006 | A04AV205-00006 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 57 | DIA=150mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV205 | A04AV205-00006
|  |  |  | A04AV205 Finishing Work Misc. Work Roof Drain (for Building) | A04AV205-00007 Finishing Work Misc. Work Roof Drain (for Building) PVC Type DIA=200mm | A04AV205 | 00007 | A04AV205-00007 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 58 | DIA=200mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV205 | A04AV205-00007
|  |  |  | A04AV205 Finishing Work Misc. Work Roof Drain (for Building) | A04AV205-00008 Finishing Work Misc. Work Roof Drain (for Building) PVC Type DIA=250mm | A04AV205 | 00008 | A04AV205-00008 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 59 | DIA=250mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV205 | A04AV205-00008
|  |  |  | A04AV205 Finishing Work Misc. Work Roof Drain (for Building) | A04AV205-00009 Finishing Work Misc. Work Roof Drain (for Building) Stainless Steel Type DIA=100mm | A04AV205 | 00009 | A04AV205-00009 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 56 | DIA=100mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV205 | A04AV205-00009
|  |  |  | A04AV205 Finishing Work Misc. Work Roof Drain (for Building) | A04AV205-00010 Finishing Work Misc. Work Roof Drain (for Building) Stainless Steel Type DIA=150mm | A04AV205 | 00010 | A04AV205-00010 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 57 | DIA=150mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV205 | A04AV205-00010
|  |  |  | A04AV205 Finishing Work Misc. Work Roof Drain (for Building) | A04AV205-00011 Finishing Work Misc. Work Roof Drain (for Building) Stainless Steel Type DIA=200mm | A04AV205 | 00011 | A04AV205-00011 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 58 | DIA=200mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV205 | A04AV205-00011
|  |  |  | A04AV205 Finishing Work Misc. Work Roof Drain (for Building) | A04AV205-00012 Finishing Work Misc. Work Roof Drain (for Building) Stainless Steel Type DIA=250mm | A04AV205 | 00012 | A04AV205-00012 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 59 | DIA=250mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV205 | A04AV205-00012
|  |  |  | A04AV206 Finishing Work Misc. Work Roof Drain (for Shelter) | A04AV206-00001 Finishing Work Misc. Work Roof Drain (for Shelter) Cast Iron Type DIA=100mm | A04AV206 | 00001 | A04AV206-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | DQ | Cast Iron Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 56 | DIA=100mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV206 | A04AV206-00001
|  |  |  | A04AV206 Finishing Work Misc. Work Roof Drain (for Shelter) | A04AV206-00002 Finishing Work Misc. Work Roof Drain (for Shelter) Cast Iron Type DIA=150mm | A04AV206 | 00002 | A04AV206-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | DQ | Cast Iron Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 57 | DIA=150mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV206 | A04AV206-00002
|  |  |  | A04AV206 Finishing Work Misc. Work Roof Drain (for Shelter) | A04AV206-00003 Finishing Work Misc. Work Roof Drain (for Shelter) Cast Iron Type DIA=200mm | A04AV206 | 00003 | A04AV206-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | DQ | Cast Iron Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 58 | DIA=200mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV206 | A04AV206-00003
|  |  |  | A04AV206 Finishing Work Misc. Work Roof Drain (for Shelter) | A04AV206-00004 Finishing Work Misc. Work Roof Drain (for Shelter) Cast Iron Type DIA=250mm | A04AV206 | 00004 | A04AV206-00004 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | DQ | Cast Iron Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 59 | DIA=250mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV206 | A04AV206-00004
|  |  |  | A04AV206 Finishing Work Misc. Work Roof Drain (for Shelter) | A04AV206-00005 Finishing Work Misc. Work Roof Drain (for Shelter) PVC Type DIA=100mm | A04AV206 | 00005 | A04AV206-00005 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 56 | DIA=100mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV206 | A04AV206-00005
|  |  |  | A04AV206 Finishing Work Misc. Work Roof Drain (for Shelter) | A04AV206-00006 Finishing Work Misc. Work Roof Drain (for Shelter) PVC Type DIA=150mm | A04AV206 | 00006 | A04AV206-00006 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 57 | DIA=150mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV206 | A04AV206-00006
|  |  |  | A04AV206 Finishing Work Misc. Work Roof Drain (for Shelter) | A04AV206-00007 Finishing Work Misc. Work Roof Drain (for Shelter) PVC Type DIA=200mm | A04AV206 | 00007 | A04AV206-00007 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 58 | DIA=200mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV206 | A04AV206-00007
|  |  |  | A04AV206 Finishing Work Misc. Work Roof Drain (for Shelter) | A04AV206-00008 Finishing Work Misc. Work Roof Drain (for Shelter) PVC Type DIA=250mm | A04AV206 | 00008 | A04AV206-00008 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 59 | DIA=250mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV206 | A04AV206-00008
|  |  |  | A04AV206 Finishing Work Misc. Work Roof Drain (for Shelter) | A04AV206-00009 Finishing Work Misc. Work Roof Drain (for Shelter) Stainless Steel Type DIA=100mm | A04AV206 | 00009 | A04AV206-00009 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 56 | DIA=100mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV206 | A04AV206-00009
|  |  |  | A04AV206 Finishing Work Misc. Work Roof Drain (for Shelter) | A04AV206-00010 Finishing Work Misc. Work Roof Drain (for Shelter) Stainless Steel Type DIA=150mm | A04AV206 | 00010 | A04AV206-00010 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 57 | DIA=150mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV206 | A04AV206-00010
|  |  |  | A04AV206 Finishing Work Misc. Work Roof Drain (for Shelter) | A04AV206-00011 Finishing Work Misc. Work Roof Drain (for Shelter) Stainless Steel Type DIA=200mm | A04AV206 | 00011 | A04AV206-00011 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 58 | DIA=200mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV206 | A04AV206-00011
|  |  |  | A04AV206 Finishing Work Misc. Work Roof Drain (for Shelter) | A04AV206-00012 Finishing Work Misc. Work Roof Drain (for Shelter) Stainless Steel Type DIA=250mm | A04AV206 | 00012 | A04AV206-00012 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 59 | DIA=250mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV206 | A04AV206-00012
|  |  |  | A04AV207 Finishing Work Misc. Work Downspout | A04AV207-00001 Finishing Work Misc. Work Downspout Galvanized Steel Type w/ Fixing Accessories DIA=100mm | A04AV207 | 00001 | A04AV207-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | DR | Galvanized Steel Type |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 56 | DIA=100mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV207 | A04AV207-00001
|  |  |  | A04AV207 Finishing Work Misc. Work Downspout | A04AV207-00002 Finishing Work Misc. Work Downspout Galvanized Steel Type w/ Fixing Accessories DIA=150mm | A04AV207 | 00002 | A04AV207-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | DR | Galvanized Steel Type |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 57 | DIA=150mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV207 | A04AV207-00002
|  |  |  | A04AV207 Finishing Work Misc. Work Downspout | A04AV207-00003 Finishing Work Misc. Work Downspout Galvanized Steel Type w/ Fixing Accessories DIA=200mm | A04AV207 | 00003 | A04AV207-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | DR | Galvanized Steel Type |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 58 | DIA=200mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV207 | A04AV207-00003
|  |  |  | A04AV207 Finishing Work Misc. Work Downspout | A04AV207-00004 Finishing Work Misc. Work Downspout Galvanized Steel Type w/ Fixing Accessories DIA=250mm | A04AV207 | 00004 | A04AV207-00004 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | DR | Galvanized Steel Type |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 59 | DIA=250mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV207 | A04AV207-00004
|  |  |  | A04AV207 Finishing Work Misc. Work Downspout | A04AV207-00005 Finishing Work Misc. Work Downspout PVC Type w/ Fixing Accessories DIA=100mm | A04AV207 | 00005 | A04AV207-00005 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 56 | DIA=100mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV207 | A04AV207-00005
|  |  |  | A04AV207 Finishing Work Misc. Work Downspout | A04AV207-00006 Finishing Work Misc. Work Downspout PVC Type w/ Fixing Accessories DIA=150mm | A04AV207 | 00006 | A04AV207-00006 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 57 | DIA=150mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV207 | A04AV207-00006
|  |  |  | A04AV207 Finishing Work Misc. Work Downspout | A04AV207-00007 Finishing Work Misc. Work Downspout PVC Type w/ Fixing Accessories DIA=200mm | A04AV207 | 00007 | A04AV207-00007 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 58 | DIA=200mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV207 | A04AV207-00007
|  |  |  | A04AV207 Finishing Work Misc. Work Downspout | A04AV207-00008 Finishing Work Misc. Work Downspout PVC Type w/ Fixing Accessories DIA=250mm | A04AV207 | 00008 | A04AV207-00008 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 59 | DIA=250mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV207 | A04AV207-00008
|  |  |  | A04AV207 Finishing Work Misc. Work Downspout | A04AV207-00009 Finishing Work Misc. Work Downspout Stainless Steel Type w/ Fixing Accessories DIA=100mm | A04AV207 | 00009 | A04AV207-00009 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 56 | DIA=100mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV207 | A04AV207-00009
|  |  |  | A04AV207 Finishing Work Misc. Work Downspout | A04AV207-00010 Finishing Work Misc. Work Downspout Stainless Steel Type w/ Fixing Accessories DIA=150mm | A04AV207 | 00010 | A04AV207-00010 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 57 | DIA=150mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV207 | A04AV207-00010
|  |  |  | A04AV207 Finishing Work Misc. Work Downspout | A04AV207-00011 Finishing Work Misc. Work Downspout Stainless Steel Type w/ Fixing Accessories DIA=200mm | A04AV207 | 00011 | A04AV207-00011 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 58 | DIA=200mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV207 | A04AV207-00011
|  |  |  | A04AV207 Finishing Work Misc. Work Downspout | A04AV207-00012 Finishing Work Misc. Work Downspout Stainless Steel Type w/ Fixing Accessories DIA=250mm | A04AV207 | 00012 | A04AV207-00012 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 59 | DIA=250mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV207 | A04AV207-00012
|  |  |  | A04AV208 Finishing Work Misc. Work Water Collection Box | A04AV208-00001 Finishing Work Misc. Work Water Collection Box Galvanized Steel Type w/ Fixing Accessories | A04AV208 | 00001 | A04AV208-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 208 | Water Collection Box | DR | Galvanized Steel Type |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV208 | A04AV208-00001
|  |  |  | A04AV208 Finishing Work Misc. Work Water Collection Box | A04AV208-00002 Finishing Work Misc. Work Water Collection Box PVC Type w/ Fixing Accessories | A04AV208 | 00002 | A04AV208-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 208 | Water Collection Box | 29 | PVC Type |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV208 | A04AV208-00002
|  |  |  | A04AV208 Finishing Work Misc. Work Water Collection Box | A04AV208-00003 Finishing Work Misc. Work Water Collection Box Stainless Steel Type w/ Fixing Accessories | A04AV208 | 00003 | A04AV208-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 208 | Water Collection Box | 30 | Stainless Steel Type |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV208 | A04AV208-00003
|  |  |  | A04AV209 Finishing Work Misc. Work Splash Block | A04AV209-00001 Finishing Work Misc. Work Splash Block Precast Concrete Block Type | A04AV209 | 00001 | A04AV209-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 209 | Splash Block | DS | Precast Concrete Block Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV209 | A04AV209-00001
|  |  |  | A04AV210 Finishing Work Misc. Work Natural Ventilator | A04AV210-00001 Finishing Work Misc. Work Natural Ventilator w/ Fixing Accessories 400mm≤DIA<600mm | A04AV210 | 00001 | A04AV210-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 210 | Natural Ventilator |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 61 | 400mm≤DIA<600mm | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV210 | A04AV210-00001
|  |  |  | A04AV210 Finishing Work Misc. Work Natural Ventilator | A04AV210-00002 Finishing Work Misc. Work Natural Ventilator w/ Fixing Accessories 600mm≤DIA<800mm | A04AV210 | 00002 | A04AV210-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 210 | Natural Ventilator |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 62 | 600mm≤DIA<800mm | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV210 | A04AV210-00002
|  |  |  | A04AV210 Finishing Work Misc. Work Natural Ventilator | A04AV210-00003 Finishing Work Misc. Work Natural Ventilator w/ Fixing Accessories 800mm≤DIA<1000mm | A04AV210 | 00003 | A04AV210-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 210 | Natural Ventilator |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 63 | 800mm≤DIA<1000mm | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV210 | A04AV210-00003
|  |  |  | A04AV210 Finishing Work Misc. Work Natural Ventilator | A04AV210-00004 Finishing Work Misc. Work Natural Ventilator w/ Fixing Accessories 1000mm≤DIA | A04AV210 | 00004 | A04AV210-00004 | AR | A04 | Finishing Work | AV | Misc. Work | 210 | Natural Ventilator |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 64 | 1000mm≤DIA | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV210 | A04AV210-00004
|  |  |  | A04AV211 Finishing Work Misc. Work Manhole Cover | A04AV211-00001 Finishing Work Misc. Work Manhole Cover Round Cast Iron Cover w/Frame Heavy Duty Type DIA=600mm | A04AV211 | 00001 | A04AV211-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 211 | Manhole Cover | DT | Round Cast Iron Cover w/Frame |  | 0 |  | 0 |  | 0 |  | 0 | 49 | Heavy Duty Type |  | 0 | 60 | DIA=600mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV211 | A04AV211-00001
|  |  |  | A04AV211 Finishing Work Misc. Work Manhole Cover | A04AV211-00002 Finishing Work Misc. Work Manhole Cover Round Cast Iron Cover w/Frame Heavy Duty Type DIA=800mm | A04AV211 | 00002 | A04AV211-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 211 | Manhole Cover | DT | Round Cast Iron Cover w/Frame |  | 0 |  | 0 |  | 0 |  | 0 | 49 | Heavy Duty Type |  | 0 | AT | DIA=800mm | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV211 | A04AV211-00002
|  |  |  | A04AV212 Finishing Work Misc. Work Chain Link Fence (Fixed Type) | A04AV212-00001 Finishing Work Misc. Work Chain Link Fence (Fixed Type) Self-Standing Type w/ Steel Frame w/ Fixing Accessories 1500mm≤H<2000mm | A04AV212 | 00001 | A04AV212-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 212 | Chain Link Fence (Fixed Type) | DU | Self-Standing Type w/ Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 69 | 1500mm≤H<2000mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV212 | A04AV212-00001
|  |  |  | A04AV212 Finishing Work Misc. Work Chain Link Fence (Fixed Type) | A04AV212-00002 Finishing Work Misc. Work Chain Link Fence (Fixed Type) Self-Standing Type w/ Steel Frame w/ Fixing Accessories 2000mm≤H<2500mm | A04AV212 | 00002 | A04AV212-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 212 | Chain Link Fence (Fixed Type) | DU | Self-Standing Type w/ Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 70 | 2000mm≤H<2500mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV212 | A04AV212-00002
|  |  |  | A04AV212 Finishing Work Misc. Work Chain Link Fence (Fixed Type) | A04AV212-00003 Finishing Work Misc. Work Chain Link Fence (Fixed Type) Self-Standing Type w/ Steel Frame w/ Fixing Accessories 2500mm≤H<3000mm | A04AV212 | 00003 | A04AV212-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 212 | Chain Link Fence (Fixed Type) | DU | Self-Standing Type w/ Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 71 | 2500mm≤H<3000mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV212 | A04AV212-00003
|  |  |  | A04AV212 Finishing Work Misc. Work Chain Link Fence (Fixed Type) | A04AV212-00004 Finishing Work Misc. Work Chain Link Fence (Fixed Type) Self-Standing Type w/ Steel Frame w/ Fixing Accessories 3000mm≤H<3500mm | A04AV212 | 00004 | A04AV212-00004 | AR | A04 | Finishing Work | AV | Misc. Work | 212 | Chain Link Fence (Fixed Type) | DU | Self-Standing Type w/ Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 72 | 3000mm≤H<3500mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV212 | A04AV212-00004
|  |  |  | A04AV212 Finishing Work Misc. Work Chain Link Fence (Fixed Type) | A04AV212-00005 Finishing Work Misc. Work Chain Link Fence (Fixed Type) Self-Standing Type w/ Stainless Steel Frame w/ Fixing Accessories 1500mm≤H<2000mm | A04AV212 | 00005 | A04AV212-00005 | AR | A04 | Finishing Work | AV | Misc. Work | 212 | Chain Link Fence (Fixed Type) | DV | Self-Standing Type w/ Stainless Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 69 | 1500mm≤H<2000mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV212 | A04AV212-00005
|  |  |  | A04AV212 Finishing Work Misc. Work Chain Link Fence (Fixed Type) | A04AV212-00006 Finishing Work Misc. Work Chain Link Fence (Fixed Type) Self-Standing Type w/ Stainless Steel Frame w/ Fixing Accessories 2000mm≤H<2500mm | A04AV212 | 00006 | A04AV212-00006 | AR | A04 | Finishing Work | AV | Misc. Work | 212 | Chain Link Fence (Fixed Type) | DV | Self-Standing Type w/ Stainless Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 70 | 2000mm≤H<2500mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV212 | A04AV212-00006
|  |  |  | A04AV212 Finishing Work Misc. Work Chain Link Fence (Fixed Type) | A04AV212-00007 Finishing Work Misc. Work Chain Link Fence (Fixed Type) Self-Standing Type w/ Stainless Steel Frame w/ Fixing Accessories 2500mm≤H<3000mm | A04AV212 | 00007 | A04AV212-00007 | AR | A04 | Finishing Work | AV | Misc. Work | 212 | Chain Link Fence (Fixed Type) | DV | Self-Standing Type w/ Stainless Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 71 | 2500mm≤H<3000mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV212 | A04AV212-00007
|  |  |  | A04AV212 Finishing Work Misc. Work Chain Link Fence (Fixed Type) | A04AV212-00008 Finishing Work Misc. Work Chain Link Fence (Fixed Type) Self-Standing Type w/ Stainless Steel Frame w/ Fixing Accessories 3000mm≤H<3500mm | A04AV212 | 00008 | A04AV212-00008 | AR | A04 | Finishing Work | AV | Misc. Work | 212 | Chain Link Fence (Fixed Type) | DV | Self-Standing Type w/ Stainless Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 72 | 3000mm≤H<3500mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV212 | A04AV212-00008
|  |  |  | A04AV213 Finishing Work Misc. Work Chain Link Fence (Removable Type) | A04AV213-00001 Finishing Work Misc. Work Chain Link Fence (Removable Type) Self-Standing Type w/ Steel Frame w/ Fixing Accessories 1500mm≤H<2000mm | A04AV213 | 00001 | A04AV213-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 213 | Chain Link Fence (Removable Type) | DU | Self-Standing Type w/ Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 69 | 1500mm≤H<2000mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV213 | A04AV213-00001
|  |  |  | A04AV213 Finishing Work Misc. Work Chain Link Fence (Removable Type) | A04AV213-00002 Finishing Work Misc. Work Chain Link Fence (Removable Type) Self-Standing Type w/ Steel Frame w/ Fixing Accessories 2000mm≤H<2500mm | A04AV213 | 00002 | A04AV213-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 213 | Chain Link Fence (Removable Type) | DU | Self-Standing Type w/ Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 70 | 2000mm≤H<2500mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV213 | A04AV213-00002
|  |  |  | A04AV213 Finishing Work Misc. Work Chain Link Fence (Removable Type) | A04AV213-00003 Finishing Work Misc. Work Chain Link Fence (Removable Type) Self-Standing Type w/ Steel Frame w/ Fixing Accessories 2500mm≤H<3000mm | A04AV213 | 00003 | A04AV213-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 213 | Chain Link Fence (Removable Type) | DU | Self-Standing Type w/ Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 71 | 2500mm≤H<3000mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV213 | A04AV213-00003
|  |  |  | A04AV213 Finishing Work Misc. Work Chain Link Fence (Removable Type) | A04AV213-00004 Finishing Work Misc. Work Chain Link Fence (Removable Type) Self-Standing Type w/ Steel Frame w/ Fixing Accessories 3000mm≤H<3500mm | A04AV213 | 00004 | A04AV213-00004 | AR | A04 | Finishing Work | AV | Misc. Work | 213 | Chain Link Fence (Removable Type) | DU | Self-Standing Type w/ Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 | 72 | 3000mm≤H<3500mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV213 | A04AV213-00004
|  |  |  | A04AV213 Finishing Work Misc. Work Chain Link Fence (Removable Type) | A04AV213-00005 Finishing Work Misc. Work Chain Link Fence (Removable Type) Frame Type w/ Steel Frame for Cable Room w/ Fixing Accessories 1500mm≤H<2000mm | A04AV213 | 00005 | A04AV213-00005 | AR | A04 | Finishing Work | AV | Misc. Work | 213 | Chain Link Fence (Removable Type) | DW | Frame Type w/ Steel Frame |  | 0 |  | 0 |  | 0 | 17 | for Cable Room | 34 | w/ Fixing Accessories |  | 0 | 69 | 1500mm≤H<2000mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV213 | A04AV213-00005
|  |  |  | A04AV213 Finishing Work Misc. Work Chain Link Fence (Removable Type) | A04AV213-00006 Finishing Work Misc. Work Chain Link Fence (Removable Type) Frame Type w/ Steel Frame for Cable Room w/ Fixing Accessories 2000mm≤H<2500mm | A04AV213 | 00006 | A04AV213-00006 | AR | A04 | Finishing Work | AV | Misc. Work | 213 | Chain Link Fence (Removable Type) | DW | Frame Type w/ Steel Frame |  | 0 |  | 0 |  | 0 | 17 | for Cable Room | 34 | w/ Fixing Accessories |  | 0 | 70 | 2000mm≤H<2500mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV213 | A04AV213-00006
|  |  |  | A04AV213 Finishing Work Misc. Work Chain Link Fence (Removable Type) | A04AV213-00007 Finishing Work Misc. Work Chain Link Fence (Removable Type) Frame Type w/ Steel Frame for Cable Room w/ Fixing Accessories 2500mm≤H<3000mm | A04AV213 | 00007 | A04AV213-00007 | AR | A04 | Finishing Work | AV | Misc. Work | 213 | Chain Link Fence (Removable Type) | DW | Frame Type w/ Steel Frame |  | 0 |  | 0 |  | 0 | 17 | for Cable Room | 34 | w/ Fixing Accessories |  | 0 | 71 | 2500mm≤H<3000mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV213 | A04AV213-00007
|  |  |  | A04AV213 Finishing Work Misc. Work Chain Link Fence (Removable Type) | A04AV213-00008 Finishing Work Misc. Work Chain Link Fence (Removable Type) Frame Type w/ Steel Frame for Cable Room w/ Fixing Accessories 3000mm≤H<3500mm | A04AV213 | 00008 | A04AV213-00008 | AR | A04 | Finishing Work | AV | Misc. Work | 213 | Chain Link Fence (Removable Type) | DW | Frame Type w/ Steel Frame |  | 0 |  | 0 |  | 0 | 17 | for Cable Room | 34 | w/ Fixing Accessories |  | 0 | 72 | 3000mm≤H<3500mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV213 | A04AV213-00008
|  |  |  | A04AV214 Finishing Work Misc. Work Chain Link Fence Single Gate | A04AV214-00001 Finishing Work Misc. Work Chain Link Fence Single Gate Self-Standing Type, Single w/ Frame, Fixing Accessories | A04AV214 | 00001 | A04AV214-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 214 | Chain Link Fence Single Gate | EA | Self-Standing Type, Single |  | 0 |  | 0 |  | 0 |  | 0 | 50 | w/ Frame, Fixing Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV214 | A04AV214-00001
|  |  |  | A04AV214 Finishing Work Misc. Work Chain Link Fence Single Gate | A04AV214-00002 Finishing Work Misc. Work Chain Link Fence Single Gate Frame Type, Single w/ Frame, Fixing Accessories | A04AV214 | 00002 | A04AV214-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 214 | Chain Link Fence Single Gate | EC | Frame Type, Single |  | 0 |  | 0 |  | 0 |  | 0 | 50 | w/ Frame, Fixing Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV214 | A04AV214-00002
|  |  |  | A04AV215 Finishing Work Misc. Work Chain Link Fence Double Gate | A04AV215-00001 Finishing Work Misc. Work Chain Link Fence Double Gate Self-Standing Type, Double w/ Frame, Fixing Accessories | A04AV215 | 00001 | A04AV215-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 215 | Chain Link Fence Double Gate | EB | Self-Standing Type, Double |  | 0 |  | 0 |  | 0 |  | 0 | 50 | w/ Frame, Fixing Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV215 | A04AV215-00001
|  |  |  | A04AV215 Finishing Work Misc. Work Chain Link Fence Double Gate | A04AV215-00002 Finishing Work Misc. Work Chain Link Fence Double Gate Frame Type, Double w/ Frame, Fixing Accessories | A04AV215 | 00002 | A04AV215-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 215 | Chain Link Fence Double Gate | ED | Frame Type, Double |  | 0 |  | 0 |  | 0 |  | 0 | 50 | w/ Frame, Fixing Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV215 | A04AV215-00002
|  |  |  | A04AV216 Finishing Work Misc. Work Metal Louvered Fence | A04AV216-00001 Finishing Work Misc. Work Metal Louvered Fence Self-Standing Type w/ Steel Frame w/ Fixing Accessories | A04AV216 | 00001 | A04AV216-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 216 | Metal Louvered Fence | DU | Self-Standing Type w/ Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 |  | 0 | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV216 | A04AV216-00001
|  |  |  | A04AV216 Finishing Work Misc. Work Metal Louvered Fence | A04AV216-00002 Finishing Work Misc. Work Metal Louvered Fence Self-Standing Type w/ Galv. Steel Frame w/ Fixing Accessories | A04AV216 | 00002 | A04AV216-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 216 | Metal Louvered Fence | EE | Self-Standing Type w/ Galv. Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 |  | 0 | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV216 | A04AV216-00002
|  |  |  | A04AV216 Finishing Work Misc. Work Metal Louvered Fence | A04AV216-00003 Finishing Work Misc. Work Metal Louvered Fence Self-Standing Type w/ Aluminum Frame w/ Fixing Accessories | A04AV216 | 00003 | A04AV216-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 216 | Metal Louvered Fence | EF | Self-Standing Type w/ Aluminum Frame |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 |  | 0 | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV216 | A04AV216-00003
|  |  |  | A04AV217 Finishing Work Misc. Work Metal Louvered Fence Single Gate | A04AV217-00001 Finishing Work Misc. Work Metal Louvered Fence Single Gate Self-Standing Type w/ Steel Frame w/ Frame, Fixing Accessories | A04AV217 | 00001 | A04AV217-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 217 | Metal Louvered Fence Single Gate | DU | Self-Standing Type w/ Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 50 | w/ Frame, Fixing Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV217 | A04AV217-00001
|  |  |  | A04AV217 Finishing Work Misc. Work Metal Louvered Fence Single Gate | A04AV217-00002 Finishing Work Misc. Work Metal Louvered Fence Single Gate Self-Standing Type w/ Galv. Steel Frame w/ Frame, Fixing Accessories | A04AV217 | 00002 | A04AV217-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 217 | Metal Louvered Fence Single Gate | EE | Self-Standing Type w/ Galv. Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 50 | w/ Frame, Fixing Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV217 | A04AV217-00002
|  |  |  | A04AV217 Finishing Work Misc. Work Metal Louvered Fence Single Gate | A04AV217-00003 Finishing Work Misc. Work Metal Louvered Fence Single Gate Self-Standing Type w/ Aluminum Frame w/ Frame, Fixing Accessories | A04AV217 | 00003 | A04AV217-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 217 | Metal Louvered Fence Single Gate | EF | Self-Standing Type w/ Aluminum Frame |  | 0 |  | 0 |  | 0 |  | 0 | 50 | w/ Frame, Fixing Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV217 | A04AV217-00003
|  |  |  | A04AV218 Finishing Work Misc. Work Metal Louvered Fence Double Gate | A04AV218-00001 Finishing Work Misc. Work Metal Louvered Fence Double Gate Self-Standing Type w/ Steel Frame w/ Frame, Fixing Accessories | A04AV218 | 00001 | A04AV218-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 218 | Metal Louvered Fence Double Gate | DU | Self-Standing Type w/ Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 50 | w/ Frame, Fixing Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV218 | A04AV218-00001
|  |  |  | A04AV218 Finishing Work Misc. Work Metal Louvered Fence Double Gate | A04AV218-00002 Finishing Work Misc. Work Metal Louvered Fence Double Gate Self-Standing Type w/ Galv. Steel Frame w/ Frame, Fixing Accessories | A04AV218 | 00002 | A04AV218-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 218 | Metal Louvered Fence Double Gate | EE | Self-Standing Type w/ Galv. Steel Frame |  | 0 |  | 0 |  | 0 |  | 0 | 50 | w/ Frame, Fixing Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV218 | A04AV218-00002
|  |  |  | A04AV218 Finishing Work Misc. Work Metal Louvered Fence Double Gate | A04AV218-00003 Finishing Work Misc. Work Metal Louvered Fence Double Gate Self-Standing Type w/ Aluminum Frame w/ Frame, Fixing Accessories | A04AV218 | 00003 | A04AV218-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 218 | Metal Louvered Fence Double Gate | EF | Self-Standing Type w/ Aluminum Frame |  | 0 |  | 0 |  | 0 |  | 0 | 50 | w/ Frame, Fixing Accessories |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV218 | A04AV218-00003
|  |  |  | A04AV219 Finishing Work Misc. Work Steel Bollard | A04AV219-00001 Finishing Work Misc. Work Steel Bollard Fixed Type w/ Paint, Concrete Fill | A04AV219 | 00001 | A04AV219-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 219 | Steel Bollard | EG | Fixed Type |  | 0 |  | 0 |  | 0 |  | 0 | 51 | w/ Paint, Concrete Fill |  | 0 |  | 0 | 0 | DIA=( )mm / H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV219 | A04AV219-00001
|  |  |  | A04AV219 Finishing Work Misc. Work Steel Bollard | A04AV219-00002 Finishing Work Misc. Work Steel Bollard Removable Type w/ Paint, Concrete Fill | A04AV219 | 00002 | A04AV219-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 219 | Steel Bollard | EH | Removable Type |  | 0 |  | 0 |  | 0 |  | 0 | 51 | w/ Paint, Concrete Fill |  | 0 |  | 0 | 0 | DIA=( )mm / H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV219 | A04AV219-00002
|  |  |  | A04AV220 Finishing Work Misc. Work Building Signage | A04AV220-00001 Finishing Work Misc. Work Building Signage | A04AV220 | 00001 | A04AV220-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 220 | Building Signage |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | SET | SET | A04AV220 | A04AV220-00001
|  |  |  | A04AV221 Finishing Work Misc. Work Room Signage | A04AV221-00001 Finishing Work Misc. Work Room Signage | A04AV221 | 00001 | A04AV221-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 221 | Room Signage |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | SET | SET | A04AV221 | A04AV221-00001
|  |  |  | A04AV222 Finishing Work Misc. Work Turnstile | A04AV222-00001 Finishing Work Misc. Work Turnstile w/ Frame, Fixing Accessories | A04AV222 | 00001 | A04AV222-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 222 | Turnstile |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 50 | w/ Frame, Fixing Accessories |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | SET | SET | A04AV222 | A04AV222-00001
|  |  |  | A04AV223 Finishing Work Misc. Work Wheel Stop | A04AV223-00001 Finishing Work Misc. Work Wheel Stop Concrete Type w/ Painting, Fixing Accessories | A04AV223 | 00001 | A04AV223-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 223 | Wheel Stop | EJ | Concrete Type |  | 0 |  | 0 |  | 0 |  | 0 | 52 | w/ Painting, Fixing Accessories |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV223 | A04AV223-00001
|  |  |  | A04AV223 Finishing Work Misc. Work Wheel Stop | A04AV223-00002 Finishing Work Misc. Work Wheel Stop Rubber Type w/ Fixing Accessories | A04AV223 | 00002 | A04AV223-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 223 | Wheel Stop | EK | Rubber Type |  | 0 |  | 0 |  | 0 |  | 0 | 34 | w/ Fixing Accessories |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV223 | A04AV223-00002
|  |  |  | A04AV224 Finishing Work Misc. Work Mirror | A04AV224-00001 Finishing Work Misc. Work Mirror Stainless Steel, Surface Mounted Type | A04AV224 | 00001 | A04AV224-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 224 | Mirror | EL | Stainless Steel, Surface Mounted Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV224 | A04AV224-00001
|  |  |  | A04AV225 Finishing Work Misc. Work Mirror w/ Shelf | A04AV225-00001 Finishing Work Misc. Work Mirror w/ Shelf Stainless Steel, Surface Mounted Type | A04AV225 | 00001 | A04AV225-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 225 | Mirror w/ Shelf | EL | Stainless Steel, Surface Mounted Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 | W x H=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV225 | A04AV225-00001
|  |  |  | A04AV226 Finishing Work Misc. Work Liquid Soap Dispensers | A04AV226-00001 Finishing Work Misc. Work Liquid Soap Dispensers Stainless Steel, Surface Mounted Type | A04AV226 | 00001 | A04AV226-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 226 | Liquid Soap Dispensers | EL | Stainless Steel, Surface Mounted Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV226 | A04AV226-00001
|  |  |  | A04AV227 Finishing Work Misc. Work Soap Dish | A04AV227-00001 Finishing Work Misc. Work Soap Dish Stainless Steel, Surface Mounted Type | A04AV227 | 00001 | A04AV227-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 227 | Soap Dish | EL | Stainless Steel, Surface Mounted Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV227 | A04AV227-00001
|  |  |  | A04AV228 Finishing Work Misc. Work Towel Bar | A04AV228-00001 Finishing Work Misc. Work Towel Bar Stainless Steel, Surface Mounted Type | A04AV228 | 00001 | A04AV228-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 228 | Towel Bar | EL | Stainless Steel, Surface Mounted Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV228 | A04AV228-00001
|  |  |  | A04AV229 Finishing Work Misc. Work Coat & Hat Hooks | A04AV229-00001 Finishing Work Misc. Work Coat & Hat Hooks Stainless Steel, Surface Mounted Type | A04AV229 | 00001 | A04AV229-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 229 | Coat & Hat Hooks | EL | Stainless Steel, Surface Mounted Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV229 | A04AV229-00001
|  |  |  | A04AV230 Finishing Work Misc. Work Electric Hand Dryer | A04AV230-00001 Finishing Work Misc. Work Electric Hand Dryer Surface Mounted Type | A04AV230 | 00001 | A04AV230-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 230 | Electric Hand Dryer | EM | Surface Mounted Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV230 | A04AV230-00001
|  |  |  | A04AV231 Finishing Work Misc. Work Paper Tower Dispenser | A04AV231-00001 Finishing Work Misc. Work Paper Tower Dispenser Stainless Steel, Surface Mounted Type | A04AV231 | 00001 | A04AV231-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 231 | Paper Tower Dispenser | EL | Stainless Steel, Surface Mounted Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV231 | A04AV231-00001
|  |  |  | A04AV232 Finishing Work Misc. Work Paper Towel Dispenser and Waste Receptacle | A04AV232-00001 Finishing Work Misc. Work Paper Towel Dispenser and Waste Receptacle Stainless Steel, Recessed Type | A04AV232 | 00001 | A04AV232-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 232 | Paper Towel Dispenser and Waste Receptacle | EN | Stainless Steel, Recessed Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV232 | A04AV232-00001
|  |  |  | A04AV233 Finishing Work Misc. Work Toilet Tissue Dispenser | A04AV233-00001 Finishing Work Misc. Work Toilet Tissue Dispenser Stainless Steel, Surface Mounted Type | A04AV233 | 00001 | A04AV233-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 233 | Toilet Tissue Dispenser | EL | Stainless Steel, Surface Mounted Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV233 | A04AV233-00001
|  |  |  | A04AV234 Finishing Work Misc. Work Grease Traps | A04AV234-00001 Finishing Work Misc. Work Grease Traps Stainless Steel, Embedded Type | A04AV234 | 00001 | A04AV234-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 234 | Grease Traps | EP | Stainless Steel, Embedded Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV234 | A04AV234-00001
|  |  |  | A04AV235 Finishing Work Misc. Work Shelves | A04AV235-00001 Finishing Work Misc. Work Shelves Stainless Steel, Surface Mounted Type | A04AV235 | 00001 | A04AV235-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 235 | Shelves | EL | Stainless Steel, Surface Mounted Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV235 | A04AV235-00001
|  |  |  | A04AV236 Finishing Work Misc. Work Shower Curtain and Curtain Rod | A04AV236-00001 Finishing Work Misc. Work Shower Curtain and Curtain Rod | A04AV236 | 00001 | A04AV236-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 236 | Shower Curtain and Curtain Rod |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV236 | A04AV236-00001
|  |  |  | A04AV237 Finishing Work Misc. Work Waste Bin | A04AV237-00001 Finishing Work Misc. Work Waste Bin Stainless Steel | A04AV237 | 00001 | A04AV237-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 237 | Waste Bin | BT | Stainless Steel |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | Capa.=( )L |  | EA | EA | A04AV237 | A04AV237-00001
|  |  |  | A04AV238 Finishing Work Misc. Work Toilet Seat-Cover Dispenser | A04AV238-00001 Finishing Work Misc. Work Toilet Seat-Cover Dispenser Stainless Steel, Surface Mounted Type | A04AV238 | 00001 | A04AV238-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 238 | Toilet Seat-Cover Dispenser | EL | Stainless Steel, Surface Mounted Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV238 | A04AV238-00001
|  |  |  | A04AV239 Finishing Work Misc. Work Ash Tray | A04AV239-00001 Finishing Work Misc. Work Ash Tray Stainless Steel, Surface Mounted Type | A04AV239 | 00001 | A04AV239-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 239 | Ash Tray | EL | Stainless Steel, Surface Mounted Type |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV239 | A04AV239-00001
|  |  |  | A04AV240 Finishing Work Misc. Work Urinal Partition | A04AV240-00001 Finishing Work Misc. Work Urinal Partition | A04AV240 | 00001 | A04AV240-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 240 | Urinal Partition |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV240 | A04AV240-00001
|  |  |  | A04AV241 Finishing Work Misc. Work Septic Tank | A04AV241-00001 Finishing Work Misc. Work Septic Tank FRP Type Including Excatvation, Installation, Backfilling and Any Other Works to Complete the Work 10 People≤Capa.<50 People | A04AV241 | 00001 | A04AV241-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 241 | Septic Tank | EQ | FRP Type |  | 0 |  | 0 |  | 0 |  | 0 | 53 | Including Excatvation, Installation, Backfilling and Any Other Works to Complete the Work |  | 0 | 79 | 10 People≤Capa.<50 People | 0 |  | 0 | 0 | 0 | 0 | 0 | Capa.=( )People |  | EA | EA | A04AV241 | A04AV241-00001
|  |  |  | A04AV241 Finishing Work Misc. Work Septic Tank | A04AV241-00002 Finishing Work Misc. Work Septic Tank FRP Type Including Excatvation, Installation, Backfilling and Any Other Works to Complete the Work 50 People≤Capa.<100 People | A04AV241 | 00002 | A04AV241-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 241 | Septic Tank | EQ | FRP Type |  | 0 |  | 0 |  | 0 |  | 0 | 53 | Including Excatvation, Installation, Backfilling and Any Other Works to Complete the Work |  | 0 | 80 | 50 People≤Capa.<100 People | 0 |  | 0 | 0 | 0 | 0 | 0 | Capa.=( )People |  | EA | EA | A04AV241 | A04AV241-00002
|  |  |  | A04AV241 Finishing Work Misc. Work Septic Tank | A04AV241-00003 Finishing Work Misc. Work Septic Tank FRP Type Including Excatvation, Installation, Backfilling and Any Other Works to Complete the Work 100 People≤Capa.<150 People | A04AV241 | 00003 | A04AV241-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 241 | Septic Tank | EQ | FRP Type |  | 0 |  | 0 |  | 0 |  | 0 | 53 | Including Excatvation, Installation, Backfilling and Any Other Works to Complete the Work |  | 0 | 81 | 100 People≤Capa.<150 People | 0 |  | 0 | 0 | 0 | 0 | 0 | Capa.=( )People |  | EA | EA | A04AV241 | A04AV241-00003
|  |  |  | A04AV241 Finishing Work Misc. Work Septic Tank | A04AV241-00004 Finishing Work Misc. Work Septic Tank FRP Type Including Excatvation, Installation, Backfilling and Any Other Works to Complete the Work 150 People≤Capa. | A04AV241 | 00004 | A04AV241-00004 | AR | A04 | Finishing Work | AV | Misc. Work | 241 | Septic Tank | EQ | FRP Type |  | 0 |  | 0 |  | 0 |  | 0 | 53 | Including Excatvation, Installation, Backfilling and Any Other Works to Complete the Work |  | 0 | 82 | 150 People≤Capa. | 0 |  | 0 | 0 | 0 | 0 | 0 | Capa.=( )People |  | EA | EA | A04AV241 | A04AV241-00004
|  |  |  | A04AV242 Finishing Work Misc. Work Feature Water Wall | A04AV242-00001 Finishing Work Misc. Work Feature Water Wall w/ Water Circulation System, Accessories | A04AV242 | 00001 | A04AV242-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 242 | Feature Water Wall | ER | w/ Water Circulation System, Accessories |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AV242 | A04AV242-00001
|  |  |  | A04AV243 Finishing Work Misc. Work Urinal Sill | A04AV243-00001 Finishing Work Misc. Work Urinal Sill w/ Mortar Bond Coat or Adhesive | A04AV243 | 00001 | A04AV243-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 243 | Urinal Sill |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | THK=( )mm / W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV243 | A04AV243-00001
|  |  |  | A04AV244 Finishing Work Misc. Work Marble Washstand | A04AV244-00001 Finishing Work Misc. Work Marble Washstand w/ Mortar Bond Coat or Adhesive | A04AV244 | 00001 | A04AV244-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 244 | Marble Washstand |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 27 | w/ Mortar Bond Coat or Adhesive |  | 0 |  | 0 | 0 | THK=( )mm / W=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV244 | A04AV244-00001
|  |  |  | A04AV245 Finishing Work Misc. Work Column Guard | A04AV245-00001 Finishing Work Misc. Work Column Guard | A04AV245 | 00001 | A04AV245-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 245 | Column Guard |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV245 | A04AV245-00001
|  |  |  | A04AV246 Finishing Work Misc. Work Non Slip Nosing | A04AV246-00001 Finishing Work Misc. Work Non Slip Nosing Adhesive Vinyl/Rubber Type | A04AV246 | 00001 | A04AV246-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 246 | Non Slip Nosing | ES | Adhesive Vinyl/Rubber Type |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV246 | A04AV246-00001
|  |  |  | A04AV246 Finishing Work Misc. Work Non Slip Nosing | A04AV246-00002 Finishing Work Misc. Work Non Slip Nosing Adhesive PVC Type | A04AV246 | 00002 | A04AV246-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 246 | Non Slip Nosing | ET | Adhesive PVC Type |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV246 | A04AV246-00002
|  |  |  | A04AV247 Finishing Work Misc. Work Flashing Cover for Opening | A04AV247-00001 Finishing Work Misc. Work Flashing Cover for Opening w/ Fixing Accessories | A04AV247 | 00001 | A04AV247-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 247 | Flashing Cover for Opening |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 34 | w/ Fixing Accessories |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AV247 | A04AV247-00001
|  |  |  | A04AV248 Finishing Work Misc. Work Interlocking Block | A04AV248-00001 Finishing Work Misc. Work Interlocking Block w/ Sand Bedding | A04AV248 | 00001 | A04AV248-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 248 | Interlocking Block |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 54 | w/ Sand Bedding |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AV248 | A04AV248-00001
|  |  |  | A04AV249 Finishing Work Misc. Work Plant Box | A04AV249-00001 Finishing Work Misc. Work Plant Box | A04AV249 | 00001 | A04AV249-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 249 | Plant Box |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV249 | A04AV249-00001
|  |  |  | A04AV311 Finishing Work Misc. Work PVC Pipe | A04AV311-00001 Finishing Work Misc. Work PVC Pipe | A04AV311 | 00001 | A04AV311-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 311 | PVC Pipe |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 | DIA=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV311 | A04AV311-00001
|  |  |  | A04AV312 Finishing Work Misc. Work Catch Basin (Ready-made) | A04AV312-00001 Finishing Work Misc. Work Catch Basin (Ready-made) | A04AV312 | 00001 | A04AV312-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 312 | Catch Basin (Ready-made) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | W x L x H=( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04AV312 | A04AV312-00001
|  |  |  | A04AV313 Finishing Work Misc. Work Safety Rope System | A04AV313-00001 Finishing Work Misc. Work Safety Rope System for Roof w/ Rope, Supporting Frame, Accessories | A04AV313 | 00001 | A04AV313-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 313 | Safety Rope System |  | 0 |  | 0 |  | 0 |  | 0 | 15 | for Roof | 58 | w/ Rope, Supporting Frame, Accessories |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A04AV313 | A04AV313-00001
|  |  |  | A04AW250 Finishing Work Landscaping Detail Design | A04AW250-00001 Finishing Work Landscaping Detail Design Comply with local condition | A04AW250 | 00001 | A04AW250-00001 | AR | A04 | Finishing Work | AW | Landscaping | 250 | Detail Design | EU | Comply with local condition |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Lot | Lot | A04AW250 | A04AW250-00001
|  |  |  | A04AW251 Finishing Work Landscaping Soft Landscaping | A04AW251-00001 Finishing Work Landscaping Soft Landscaping w/ Irrigation System Supply and Install Work w/ All Items to Complete the Work | A04AW251 | 00001 | A04AW251-00001 | AR | A04 | Finishing Work | AW | Landscaping | 251 | Soft Landscaping | EV | w/ Irrigation System |  | 0 |  | 0 |  | 0 |  | 0 | 55 | Supply and Install Work w/ All Items to Complete the Work |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AW251 | A04AW251-00001
|  |  |  | A04AW251 Finishing Work Landscaping Soft Landscaping | A04AW251-00002 Finishing Work Landscaping Soft Landscaping w/o Irrigation System Supply and Install Work w/ All Items to Complete the Work | A04AW251 | 00002 | A04AW251-00002 | AR | A04 | Finishing Work | AW | Landscaping | 251 | Soft Landscaping | EW | w/o Irrigation System |  | 0 |  | 0 |  | 0 |  | 0 | 55 | Supply and Install Work w/ All Items to Complete the Work |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AW251 | A04AW251-00002
|  |  |  | A04AW252 Finishing Work Landscaping Hard Landscaping | A04AW252-00001 Finishing Work Landscaping Hard Landscaping Interlocking Paving Block w/ Sand Bedding | A04AW252 | 00001 | A04AW252-00001 | AR | A04 | Finishing Work | AW | Landscaping | 252 | Hard Landscaping | FA | Interlocking Paving Block w/ Sand Bedding |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04AW252 | A04AW252-00001
|  |  |  | A04AW252 Finishing Work Landscaping Hard Landscaping | A04AW252-00002 Finishing Work Landscaping Hard Landscaping Kerbstone | A04AW252 | 00002 | A04AW252-00002 | AR | A04 | Finishing Work | AW | Landscaping | 252 | Hard Landscaping | FB | Kerbstone |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M | A04AW252 | A04AW252-00002
|  |  |  | A04AW252 Finishing Work Landscaping Hard Landscaping | A04AW252-00003 Finishing Work Landscaping Hard Landscaping Bench | A04AW252 | 00003 | A04AW252-00003 | AR | A04 | Finishing Work | AW | Landscaping | 252 | Hard Landscaping | FC | Bench |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | EA | A04AW252 | A04AW252-00003
|  |  |  | A04BA253 Finishing Work Furniture Installation Automatic Counter Top Tea/Coffee Machine | A04BA253-00001 Finishing Work Furniture Installation Automatic Counter Top Tea/Coffee Machine | A04BA253 | 00001 | A04BA253-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 253 | Automatic Counter Top Tea/Coffee Machine |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA253 | A04BA253-00001
|  |  |  | A04BA254 Finishing Work Furniture Installation Benches | A04BA254-00001 Finishing Work Furniture Installation Benches | A04BA254 | 00001 | A04BA254-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 254 | Benches |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA254 | A04BA254-00001
|  |  |  | A04BA255 Finishing Work Furniture Installation Bicycle/ Tricycle Cart Stand | A04BA255-00001 Finishing Work Furniture Installation Bicycle/ Tricycle Cart Stand | A04BA255 | 00001 | A04BA255-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 255 | Bicycle/ Tricycle Cart Stand |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA255 | A04BA255-00001
|  |  |  | A04BA256 Finishing Work Furniture Installation Printer | A04BA256-00001 Finishing Work Furniture Installation Printer | A04BA256 | 00001 | A04BA256-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 256 | Printer |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA256 | A04BA256-00001
|  |  |  | A04BA257 Finishing Work Furniture Installation Bed | A04BA257-00001 Finishing Work Furniture Installation Bed | A04BA257 | 00001 | A04BA257-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 257 | Bed |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA257 | A04BA257-00001
|  |  |  | A04BA258 Finishing Work Furniture Installation Chairs | A04BA258-00001 Finishing Work Furniture Installation Chairs | A04BA258 | 00001 | A04BA258-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 258 | Chairs |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA258 | A04BA258-00001
|  |  |  | A04BA259 Finishing Work Furniture Installation Cloak-Stand | A04BA259-00001 Finishing Work Furniture Installation Cloak-Stand | A04BA259 | 00001 | A04BA259-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 259 | Cloak-Stand |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA259 | A04BA259-00001
|  |  |  | A04BA260 Finishing Work Furniture Installation Desk | A04BA260-00001 Finishing Work Furniture Installation Desk | A04BA260 | 00001 | A04BA260-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 260 | Desk |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA260 | A04BA260-00001
|  |  |  | A04BA261 Finishing Work Furniture Installation Desk Lamp | A04BA261-00001 Finishing Work Furniture Installation Desk Lamp | A04BA261 | 00001 | A04BA261-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 261 | Desk Lamp |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA261 | A04BA261-00001
|  |  |  | A04BA262 Finishing Work Furniture Installation Desk Top Computer & Monitor | A04BA262-00001 Finishing Work Furniture Installation Desk Top Computer & Monitor | A04BA262 | 00001 | A04BA262-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 262 | Desk Top Computer & Monitor |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA262 | A04BA262-00001
|  |  |  | A04BA263 Finishing Work Furniture Installation Dining Chair | A04BA263-00001 Finishing Work Furniture Installation Dining Chair | A04BA263 | 00001 | A04BA263-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 263 | Dining Chair |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA263 | A04BA263-00001
|  |  |  | A04BA264 Finishing Work Furniture Installation Dining Table | A04BA264-00001 Finishing Work Furniture Installation Dining Table | A04BA264 | 00001 | A04BA264-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 264 | Dining Table |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA264 | A04BA264-00001
|  |  |  | A04BA265 Finishing Work Furniture Installation Hanger | A04BA265-00001 Finishing Work Furniture Installation Hanger | A04BA265 | 00001 | A04BA265-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 265 | Hanger |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA265 | A04BA265-00001
|  |  |  | A04BA266 Finishing Work Furniture Installation Executive Chair | A04BA266-00001 Finishing Work Furniture Installation Executive Chair | A04BA266 | 00001 | A04BA266-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 266 | Executive Chair |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA266 | A04BA266-00001
|  |  |  | A04BA267 Finishing Work Furniture Installation Filing Drawers | A04BA267-00001 Finishing Work Furniture Installation Filing Drawers | A04BA267 | 00001 | A04BA267-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 267 | Filing Drawers |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA267 | A04BA267-00001
|  |  |  | A04BA268 Finishing Work Furniture Installation Full Height Locker | A04BA268-00001 Finishing Work Furniture Installation Full Height Locker | A04BA268 | 00001 | A04BA268-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 268 | Full Height Locker |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA268 | A04BA268-00001
|  |  |  | A04BA269 Finishing Work Furniture Installation Half Height Locker | A04BA269-00001 Finishing Work Furniture Installation Half Height Locker | A04BA269 | 00001 | A04BA269-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 269 | Half Height Locker |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA269 | A04BA269-00001
|  |  |  | A04BA270 Finishing Work Furniture Installation Hot Plate | A04BA270-00001 Finishing Work Furniture Installation Hot Plate | A04BA270 | 00001 | A04BA270-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 270 | Hot Plate |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA270 | A04BA270-00001
|  |  |  | A04BA271 Finishing Work Furniture Installation Information Board | A04BA271-00001 Finishing Work Furniture Installation Information Board | A04BA271 | 00001 | A04BA271-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 271 | Information Board |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA271 | A04BA271-00001
|  |  |  | A04BA272 Finishing Work Furniture Installation Key Cabinet | A04BA272-00001 Finishing Work Furniture Installation Key Cabinet | A04BA272 | 00001 | A04BA272-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 272 | Key Cabinet |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA272 | A04BA272-00001
|  |  |  | A04BA273 Finishing Work Furniture Installation Kitchen Sink | A04BA273-00001 Finishing Work Furniture Installation Kitchen Sink | A04BA273 | 00001 | A04BA273-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 273 | Kitchen Sink |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA273 | A04BA273-00001
|  |  |  | A04BA274 Finishing Work Furniture Installation Kitchen Unit | A04BA274-00001 Finishing Work Furniture Installation Kitchen Unit | A04BA274 | 00001 | A04BA274-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 274 | Kitchen Unit |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | LOT | LOT | A04BA274 | A04BA274-00001
|  |  |  | A04BA275 Finishing Work Furniture Installation Metal Cabinet | A04BA275-00001 Finishing Work Furniture Installation Metal Cabinet | A04BA275 | 00001 | A04BA275-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 275 | Metal Cabinet |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA275 | A04BA275-00001
|  |  |  | A04BA276 Finishing Work Furniture Installation Microwave Oven | A04BA276-00001 Finishing Work Furniture Installation Microwave Oven | A04BA276 | 00001 | A04BA276-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 276 | Microwave Oven |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA276 | A04BA276-00001
|  |  |  | A04BA277 Finishing Work Furniture Installation Office Partition | A04BA277-00001 Finishing Work Furniture Installation Office Partition | A04BA277 | 00001 | A04BA277-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 277 | Office Partition |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | LOT | LOT | A04BA277 | A04BA277-00001
|  |  |  | A04BA278 Finishing Work Furniture Installation Printer Table | A04BA278-00001 Finishing Work Furniture Installation Printer Table | A04BA278 | 00001 | A04BA278-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 278 | Printer Table |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA278 | A04BA278-00001
|  |  |  | A04BA279 Finishing Work Furniture Installation Quartz Clock | A04BA279-00001 Finishing Work Furniture Installation Quartz Clock | A04BA279 | 00001 | A04BA279-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 279 | Quartz Clock |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA279 | A04BA279-00001
|  |  |  | A04BA280 Finishing Work Furniture Installation Reception Counter | A04BA280-00001 Finishing Work Furniture Installation Reception Counter | A04BA280 | 00001 | A04BA280-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 280 | Reception Counter |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA280 | A04BA280-00001
|  |  |  | A04BA281 Finishing Work Furniture Installation Refrigerator | A04BA281-00001 Finishing Work Furniture Installation Refrigerator | A04BA281 | 00001 | A04BA281-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 281 | Refrigerator |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA281 | A04BA281-00001
|  |  |  | A04BA282 Finishing Work Furniture Installation Side Chair | A04BA282-00001 Finishing Work Furniture Installation Side Chair | A04BA282 | 00001 | A04BA282-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 282 | Side Chair |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA282 | A04BA282-00001
|  |  |  | A04BA283 Finishing Work Furniture Installation Sofa | A04BA283-00001 Finishing Work Furniture Installation Sofa | A04BA283 | 00001 | A04BA283-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 283 | Sofa |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA283 | A04BA283-00001
|  |  |  | A04BA284 Finishing Work Furniture Installation Storage Cabinets(Bookcase) | A04BA284-00001 Finishing Work Furniture Installation Storage Cabinets(Bookcase) | A04BA284 | 00001 | A04BA284-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 284 | Storage Cabinets(Bookcase) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA284 | A04BA284-00001
|  |  |  | A04BA285 Finishing Work Furniture Installation Strip Curtain | A04BA285-00001 Finishing Work Furniture Installation Strip Curtain | A04BA285 | 00001 | A04BA285-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 285 | Strip Curtain |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA285 | A04BA285-00001
|  |  |  | A04BA286 Finishing Work Furniture Installation Table | A04BA286-00001 Finishing Work Furniture Installation Table | A04BA286 | 00001 | A04BA286-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 286 | Table |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA286 | A04BA286-00001
|  |  |  | A04BA287 Finishing Work Furniture Installation Tall Storage Cupboard | A04BA287-00001 Finishing Work Furniture Installation Tall Storage Cupboard | A04BA287 | 00001 | A04BA287-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 287 | Tall Storage Cupboard |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA287 | A04BA287-00001
|  |  |  | A04BA288 Finishing Work Furniture Installation Umbrella's Holder | A04BA288-00001 Finishing Work Furniture Installation Umbrella's Holder | A04BA288 | 00001 | A04BA288-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 288 | Umbrella's Holder |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA288 | A04BA288-00001
|  |  |  | A04BA289 Finishing Work Furniture Installation Visitors Chairs | A04BA289-00001 Finishing Work Furniture Installation Visitors Chairs | A04BA289 | 00001 | A04BA289-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 289 | Visitors Chairs |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA289 | A04BA289-00001
|  |  |  | A04BA290 Finishing Work Furniture Installation Wall Cupboard | A04BA290-00001 Finishing Work Furniture Installation Wall Cupboard | A04BA290 | 00001 | A04BA290-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 290 | Wall Cupboard |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA290 | A04BA290-00001
|  |  |  | A04BA291 Finishing Work Furniture Installation Washing Unit | A04BA291-00001 Finishing Work Furniture Installation Washing Unit | A04BA291 | 00001 | A04BA291-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 291 | Washing Unit |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | LOT | LOT | A04BA291 | A04BA291-00001
|  |  |  | A04BA292 Finishing Work Furniture Installation Water Cooler | A04BA292-00001 Finishing Work Furniture Installation Water Cooler | A04BA292 | 00001 | A04BA292-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 292 | Water Cooler |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA292 | A04BA292-00001
|  |  |  | A04BA293 Finishing Work Furniture Installation White Board | A04BA293-00001 Finishing Work Furniture Installation White Board | A04BA293 | 00001 | A04BA293-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 293 | White Board |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA293 | A04BA293-00001
|  |  |  | A04BA294 Finishing Work Furniture Installation Rack | A04BA294-00001 Finishing Work Furniture Installation Rack | A04BA294 | 00001 | A04BA294-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 294 | Rack |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA294 | A04BA294-00001
|  |  |  | A04BA295 Finishing Work Furniture Installation Medicine Cabinet | A04BA295-00001 Finishing Work Furniture Installation Medicine Cabinet | A04BA295 | 00001 | A04BA295-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 295 | Medicine Cabinet |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA295 | A04BA295-00001
|  |  |  | A04BA296 Finishing Work Furniture Installation Others | A04BA296-00001 Finishing Work Furniture Installation Others | A04BA296 | 00001 | A04BA296-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 296 | Others |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A04BA296 | A04BA296-00001
|  |  |  | A04BD308 Finishing Work Work for Ergonomic/Sustainable Design Ergonomic Designed Area | A04BD308-00001 Finishing Work Work for Ergonomic/Sustainable Design Ergonomic Designed Area for Floor | A04BD308 | 00001 | A04BD308-00001 | AR | A04 | Finishing Work | BD | Work for Ergonomic/Sustainable Design | 308 | Ergonomic Designed Area |  | 0 |  | 0 |  | 0 |  | 0 | 29 | for Floor |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04BD308 | A04BD308-00001
|  |  |  | A04BD308 Finishing Work Work for Ergonomic/Sustainable Design Ergonomic Designed Area | A04BD308-00002 Finishing Work Work for Ergonomic/Sustainable Design Ergonomic Designed Area for Wall | A04BD308 | 00002 | A04BD308-00002 | AR | A04 | Finishing Work | BD | Work for Ergonomic/Sustainable Design | 308 | Ergonomic Designed Area |  | 0 |  | 0 |  | 0 |  | 0 | 08 | for Wall |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04BD308 | A04BD308-00002
|  |  |  | A04BD308 Finishing Work Work for Ergonomic/Sustainable Design Ergonomic Designed Area | A04BD308-00003 Finishing Work Work for Ergonomic/Sustainable Design Ergonomic Designed Area for Ceiling | A04BD308 | 00003 | A04BD308-00003 | AR | A04 | Finishing Work | BD | Work for Ergonomic/Sustainable Design | 308 | Ergonomic Designed Area |  | 0 |  | 0 |  | 0 |  | 0 | 30 | for Ceiling |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04BD308 | A04BD308-00003
|  |  |  | A04BD309 Finishing Work Work for Ergonomic/Sustainable Design Sustainable Designed Area | A04BD309-00001 Finishing Work Work for Ergonomic/Sustainable Design Sustainable Designed Area | A04BD309 | 00001 | A04BD309-00001 | AR | A04 | Finishing Work | BD | Work for Ergonomic/Sustainable Design | 309 | Sustainable Designed Area |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A04BD309 | A04BD309-00001
|  |  |  | A05ZZ199 Cladding Work - Single Metal Sheet | A05ZZ199-00001 Cladding Work - Single Metal Sheet Stainless Steel Sheet for Wall w/ Accessories, Flashing | A05ZZ199 | 00001 | A05ZZ199-00001 | AR | A05 | Cladding Work | ZZ | - | 199 | Single Metal Sheet | CV | Stainless Steel Sheet |  | 0 |  | 0 |  | 0 | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ199 | A05ZZ199-00001
|  |  |  | A05ZZ199 Cladding Work - Single Metal Sheet | A05ZZ199-00002 Cladding Work - Single Metal Sheet Stainless Steel Sheet for Roof w/ Accessories, Flashing | A05ZZ199 | 00002 | A05ZZ199-00002 | AR | A05 | Cladding Work | ZZ | - | 199 | Single Metal Sheet | CV | Stainless Steel Sheet |  | 0 |  | 0 |  | 0 | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ199 | A05ZZ199-00002
|  |  |  | A05ZZ199 Cladding Work - Single Metal Sheet | A05ZZ199-00003 Cladding Work - Single Metal Sheet Corrugated Aluminum Sheet for Wall w/ Accessories, Flashing | A05ZZ199 | 00003 | A05ZZ199-00003 | AR | A05 | Cladding Work | ZZ | - | 199 | Single Metal Sheet | CW | Corrugated Aluminum Sheet |  | 0 |  | 0 |  | 0 | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ199 | A05ZZ199-00003
|  |  |  | A05ZZ199 Cladding Work - Single Metal Sheet | A05ZZ199-00004 Cladding Work - Single Metal Sheet Corrugated Aluminum Sheet for Roof w/ Accessories, Flashing | A05ZZ199 | 00004 | A05ZZ199-00004 | AR | A05 | Cladding Work | ZZ | - | 199 | Single Metal Sheet | CW | Corrugated Aluminum Sheet |  | 0 |  | 0 |  | 0 | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ199 | A05ZZ199-00004
|  |  |  | A05ZZ199 Cladding Work - Single Metal Sheet | A05ZZ199-00005 Cladding Work - Single Metal Sheet Corrugated Galvanized Steel Sheet for Wall w/ Accessories, Flashing | A05ZZ199 | 00005 | A05ZZ199-00005 | AR | A05 | Cladding Work | ZZ | - | 199 | Single Metal Sheet | DA | Corrugated Galvanized Steel Sheet |  | 0 |  | 0 |  | 0 | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ199 | A05ZZ199-00005
|  |  |  | A05ZZ199 Cladding Work - Single Metal Sheet | A05ZZ199-00006 Cladding Work - Single Metal Sheet Corrugated Galvanized Steel Sheet for Roof w/ Accessories, Flashing | A05ZZ199 | 00006 | A05ZZ199-00006 | AR | A05 | Cladding Work | ZZ | - | 199 | Single Metal Sheet | DA | Corrugated Galvanized Steel Sheet |  | 0 |  | 0 |  | 0 | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 |  | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ199 | A05ZZ199-00006
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00001 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00001 | A05ZZ200-00001 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00001
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00002 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00002 | A05ZZ200-00002 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00002
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00003 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00003 | A05ZZ200-00003 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00003
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00004 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00004 | A05ZZ200-00004 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00004
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00005 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00005 | A05ZZ200-00005 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00005
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00006 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00006 | A05ZZ200-00006 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00006
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00007 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00007 | A05ZZ200-00007 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00007
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00008 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00008 | A05ZZ200-00008 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00008
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00009 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00009 | A05ZZ200-00009 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00009
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00010 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00010 | A05ZZ200-00010 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00010
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00011 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00011 | A05ZZ200-00011 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00011
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00012 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00012 | A05ZZ200-00012 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00012
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00013 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00013 | A05ZZ200-00013 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00013
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00014 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00014 | A05ZZ200-00014 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00014
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00015 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00015 | A05ZZ200-00015 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00015
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00016 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00016 | A05ZZ200-00016 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00016
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00017 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00017 | A05ZZ200-00017 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00017
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00018 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00018 | A05ZZ200-00018 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00018
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00019 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00019 | A05ZZ200-00019 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00019
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00020 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00020 | A05ZZ200-00020 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00020
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00021 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00021 | A05ZZ200-00021 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00021
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00022 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00022 | A05ZZ200-00022 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00022
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00023 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00023 | A05ZZ200-00023 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00023
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00024 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00024 | A05ZZ200-00024 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00024
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00025 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00025 | A05ZZ200-00025 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00025
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00026 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00026 | A05ZZ200-00026 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00026
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00027 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00027 | A05ZZ200-00027 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00027
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00028 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00028 | A05ZZ200-00028 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00028
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00029 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00029 | A05ZZ200-00029 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00029
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00030 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00030 | A05ZZ200-00030 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00030
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00031 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00031 | A05ZZ200-00031 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00031
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00032 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00032 | A05ZZ200-00032 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00032
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00033 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00033 | A05ZZ200-00033 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00033
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00034 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00034 | A05ZZ200-00034 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00034
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00035 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00035 | A05ZZ200-00035 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00035
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00036 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00036 | A05ZZ200-00036 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00036
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00037 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00037 | A05ZZ200-00037 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00037
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00038 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00038 | A05ZZ200-00038 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00038
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00039 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00039 | A05ZZ200-00039 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00039
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00040 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00040 | A05ZZ200-00040 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00040
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00041 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00041 | A05ZZ200-00041 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00041
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00042 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00042 | A05ZZ200-00042 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00042
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00043 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00043 | A05ZZ200-00043 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00043
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00044 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00044 | A05ZZ200-00044 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00044
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00045 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00045 | A05ZZ200-00045 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00045
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00046 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00046 | A05ZZ200-00046 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00046
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00047 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00047 | A05ZZ200-00047 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00047
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00048 Cladding Work - Sandwich Panel Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00048 | A05ZZ200-00048 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00048
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00049 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00049 | A05ZZ200-00049 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00049
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00050 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00050 | A05ZZ200-00050 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00050
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00051 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00051 | A05ZZ200-00051 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00051
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00052 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00052 | A05ZZ200-00052 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00052
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00053 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00053 | A05ZZ200-00053 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00053
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00054 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00054 | A05ZZ200-00054 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00054
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00055 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00055 | A05ZZ200-00055 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00055
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00056 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00056 | A05ZZ200-00056 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00056
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00057 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00057 | A05ZZ200-00057 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00057
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00058 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00058 | A05ZZ200-00058 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00058
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00059 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00059 | A05ZZ200-00059 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00059
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00060 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00060 | A05ZZ200-00060 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00060
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00061 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00061 | A05ZZ200-00061 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00061
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00062 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00062 | A05ZZ200-00062 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00062
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00063 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00063 | A05ZZ200-00063 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00063
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00064 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00064 | A05ZZ200-00064 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00064
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00065 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00065 | A05ZZ200-00065 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00065
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00066 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00066 | A05ZZ200-00066 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00066
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00067 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00067 | A05ZZ200-00067 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00067
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00068 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00068 | A05ZZ200-00068 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00068
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00069 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00069 | A05ZZ200-00069 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00069
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00070 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00070 | A05ZZ200-00070 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00070
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00071 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00071 | A05ZZ200-00071 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00071
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00072 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00072 | A05ZZ200-00072 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00072
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00073 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00073 | A05ZZ200-00073 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00073
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00074 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00074 | A05ZZ200-00074 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00074
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00075 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00075 | A05ZZ200-00075 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00075
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00076 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00076 | A05ZZ200-00076 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00076
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00077 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00077 | A05ZZ200-00077 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00077
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00078 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00078 | A05ZZ200-00078 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00078
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00079 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00079 | A05ZZ200-00079 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00079
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00080 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00080 | A05ZZ200-00080 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00080
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00081 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00081 | A05ZZ200-00081 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00081
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00082 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00082 | A05ZZ200-00082 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00082
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00083 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00083 | A05ZZ200-00083 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00083
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00084 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00084 | A05ZZ200-00084 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00084
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00085 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00085 | A05ZZ200-00085 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00085
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00086 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00086 | A05ZZ200-00086 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00086
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00087 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00087 | A05ZZ200-00087 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00087
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00088 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00088 | A05ZZ200-00088 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00088
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00089 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00089 | A05ZZ200-00089 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00089
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00090 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00090 | A05ZZ200-00090 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00090
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00091 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00091 | A05ZZ200-00091 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00091
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00092 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00092 | A05ZZ200-00092 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00092
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00093 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00093 | A05ZZ200-00093 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00093
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00094 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00094 | A05ZZ200-00094 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00094
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00095 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00095 | A05ZZ200-00095 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00095
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00096 Cladding Work - Sandwich Panel Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00096 | A05ZZ200-00096 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00096
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00097 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00097 | A05ZZ200-00097 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00097
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00098 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00098 | A05ZZ200-00098 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00098
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00099 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00099 | A05ZZ200-00099 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00099
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00100 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00100 | A05ZZ200-00100 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00100
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00101 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00101 | A05ZZ200-00101 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00101
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00102 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00102 | A05ZZ200-00102 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00102
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00103 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00103 | A05ZZ200-00103 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00103
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00104 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00104 | A05ZZ200-00104 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00104
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00105 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00105 | A05ZZ200-00105 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00105
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00106 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00106 | A05ZZ200-00106 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00106
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00107 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00107 | A05ZZ200-00107 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00107
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00108 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00108 | A05ZZ200-00108 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00108
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00109 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00109 | A05ZZ200-00109 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00109
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00110 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00110 | A05ZZ200-00110 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00110
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00111 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00111 | A05ZZ200-00111 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00111
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00112 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00112 | A05ZZ200-00112 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00112
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00113 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00113 | A05ZZ200-00113 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00113
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00114 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00114 | A05ZZ200-00114 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00114
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00115 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00115 | A05ZZ200-00115 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00115
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00116 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00116 | A05ZZ200-00116 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00116
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00117 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00117 | A05ZZ200-00117 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00117
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00118 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00118 | A05ZZ200-00118 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00118
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00119 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00119 | A05ZZ200-00119 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00119
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00120 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00120 | A05ZZ200-00120 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00120
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00121 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00121 | A05ZZ200-00121 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00121
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00122 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00122 | A05ZZ200-00122 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00122
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00123 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00123 | A05ZZ200-00123 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00123
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00124 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00124 | A05ZZ200-00124 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00124
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00125 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00125 | A05ZZ200-00125 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00125
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00126 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00126 | A05ZZ200-00126 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00126
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00127 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00127 | A05ZZ200-00127 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00127
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00128 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00128 | A05ZZ200-00128 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00128
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00129 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00129 | A05ZZ200-00129 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00129
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00130 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00130 | A05ZZ200-00130 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00130
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00131 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00131 | A05ZZ200-00131 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00131
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00132 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00132 | A05ZZ200-00132 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00132
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00133 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00133 | A05ZZ200-00133 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00133
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00134 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00134 | A05ZZ200-00134 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00134
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00135 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00135 | A05ZZ200-00135 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00135
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00136 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00136 | A05ZZ200-00136 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00136
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00137 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00137 | A05ZZ200-00137 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00137
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00138 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00138 | A05ZZ200-00138 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00138
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00139 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00139 | A05ZZ200-00139 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00139
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00140 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Wall w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00140 | A05ZZ200-00140 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00140
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00141 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 50mm≤THK<70mm | A05ZZ200 | 00141 | A05ZZ200-00141 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 32 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00141
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00142 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 70mm≤THK<100mm | A05ZZ200 | 00142 | A05ZZ200-00142 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 33 | 70mm≤THK<100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00142
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00143 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 100mm≤THK<150mm | A05ZZ200 | 00143 | A05ZZ200-00143 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 34 | 100mm≤THK<150mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00143
|  |  |  | A05ZZ200 Cladding Work - Sandwich Panel | A05ZZ200-00144 Cladding Work - Sandwich Panel Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 150mm≤THK | A05ZZ200 | 00144 | A05ZZ200-00144 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  | 0 |  | 0 | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  | 0 | 35 | 150mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ200 | A05ZZ200-00144
|  |  |  | A05ZZ201 Cladding Work - FRP Translucent Panel w/ Accessories | A05ZZ201-00001 Cladding Work - FRP Translucent Panel w/ Accessories for Wall w/ Accessories | A05ZZ201 | 00001 | A05ZZ201-00001 | AR | A05 | Cladding Work | ZZ | - | 201 | FRP Translucent Panel w/ Accessories |  | 0 |  | 0 |  | 0 |  | 0 | 08 | for Wall | 32 | w/ Accessories |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ201 | A05ZZ201-00001
|  |  |  | A05ZZ201 Cladding Work - FRP Translucent Panel w/ Accessories | A05ZZ201-00002 Cladding Work - FRP Translucent Panel w/ Accessories for Roof w/ Accessories | A05ZZ201 | 00002 | A05ZZ201-00002 | AR | A05 | Cladding Work | ZZ | - | 201 | FRP Translucent Panel w/ Accessories |  | 0 |  | 0 |  | 0 |  | 0 | 15 | for Roof | 32 | w/ Accessories |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ201 | A05ZZ201-00002
|  |  |  | A05ZZ202 Cladding Work - Glass Panel | A05ZZ202-00001 Cladding Work - Glass Panel Straight Type w/ Frame, Accessories | A05ZZ202 | 00001 | A05ZZ202-00001 | AR | A05 | Cladding Work | ZZ | - | 202 | Glass Panel | DH | Straight Type |  | 0 |  | 0 |  | 0 |  | 0 | 48 | w/ Frame, Accessories |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ202 | A05ZZ202-00001
|  |  |  | A05ZZ202 Cladding Work - Glass Panel | A05ZZ202-00002 Cladding Work - Glass Panel Curved Type w/ Frame, Accessories | A05ZZ202 | 00002 | A05ZZ202-00002 | AR | A05 | Cladding Work | ZZ | - | 202 | Glass Panel | DJ | Curved Type |  | 0 |  | 0 |  | 0 |  | 0 | 48 | w/ Frame, Accessories |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ202 | A05ZZ202-00002
|  |  |  | A05ZZ203 Cladding Work - Fabric Roof | A05ZZ203-00001 Cladding Work - Fabric Roof Fabric Type for Car Parking Shelter w/ Accessories | A05ZZ203 | 00001 | A05ZZ203-00001 | AR | A05 | Cladding Work | ZZ | - | 203 | Fabric Roof | DK | Fabric Type |  | 0 |  | 0 |  | 0 | 16 | for Car Parking Shelter | 32 | w/ Accessories |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A05ZZ203 | A05ZZ203-00001
|  |  |  | A05ZZ204 Cladding Work - Gutter | A05ZZ204-00001 Cladding Work - Gutter Galvanized Steel Eave Gutter w/ Coating w/ Accessories | A05ZZ204 | 00001 | A05ZZ204-00001 | AR | A05 | Cladding Work | ZZ | - | 204 | Gutter | DL | Galvanized Steel Eave Gutter w/ Coating |  | 0 |  | 0 |  | 0 |  | 0 | 32 | w/ Accessories |  | 0 |  |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A05ZZ204 | A05ZZ204-00001
|  |  |  | A05ZZ204 Cladding Work - Gutter | A05ZZ204-00002 Cladding Work - Gutter Galvanized Steel Valley Gutter w/ Coating w/ Accessories | A05ZZ204 | 00002 | A05ZZ204-00002 | AR | A05 | Cladding Work | ZZ | - | 204 | Gutter | DM | Galvanized Steel Valley Gutter w/ Coating |  | 0 |  | 0 |  | 0 |  | 0 | 32 | w/ Accessories |  | 0 |  |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A05ZZ204 | A05ZZ204-00002
|  |  |  | A05ZZ204 Cladding Work - Gutter | A05ZZ204-00003 Cladding Work - Gutter Aluminum Eave Gutter w/ Coating w/ Accessories | A05ZZ204 | 00003 | A05ZZ204-00003 | AR | A05 | Cladding Work | ZZ | - | 204 | Gutter | DN | Aluminum Eave Gutter w/ Coating |  | 0 |  | 0 |  | 0 |  | 0 | 32 | w/ Accessories |  | 0 |  |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A05ZZ204 | A05ZZ204-00003
|  |  |  | A05ZZ204 Cladding Work - Gutter | A05ZZ204-00004 Cladding Work - Gutter Aluminum Valley Gutter w/ Coating w/ Accessories | A05ZZ204 | 00004 | A05ZZ204-00004 | AR | A05 | Cladding Work | ZZ | - | 204 | Gutter | DP | Aluminum Valley Gutter w/ Coating |  | 0 |  | 0 |  | 0 |  | 0 | 32 | w/ Accessories |  | 0 |  |  | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 |  | M | M | A05ZZ204 | A05ZZ204-00004
|  |  |  | A06BB297 Demolition Work Revamping Work Demolition Work of Concrete Structure | A06BB297-00001 Demolition Work Revamping Work Demolition Work of Concrete Structure for Foundation & Structure(Reinforced) Demoliton Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | A06BB297 | 00001 | A06BB297-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 297 | Demolition Work of Concrete Structure |  | 0 |  | 0 |  | 0 |  | 0 | 18 | for Foundation & Structure(Reinforced) Demoliton | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M3 | M3 | A06BB297 | A06BB297-00001
|  |  |  | A06BB298 Demolition Work Revamping Work Cutting and Breaking Reinforced Conc. | A06BB298-00001 Demolition Work Revamping Work Cutting and Breaking Reinforced Conc. for Floor Openings Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | A06BB298 | 00001 | A06BB298-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 298 | Cutting and Breaking Reinforced Conc. |  | 0 |  | 0 |  | 0 |  | 0 | 19 | for Floor Openings | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A06BB298 | A06BB298-00001
|  |  |  | A06BB298 Demolition Work Revamping Work Cutting and Breaking Reinforced Conc. | A06BB298-00002 Demolition Work Revamping Work Cutting and Breaking Reinforced Conc. for Wall Openings Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | A06BB298 | 00002 | A06BB298-00002 | AR | A06 | Demolition Work | BB | Revamping Work | 298 | Cutting and Breaking Reinforced Conc. |  | 0 |  | 0 |  | 0 |  | 0 | 20 | for Wall Openings | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A06BB298 | A06BB298-00002
|  |  |  | A06BB299 Demolition Work Revamping Work Demolition Work of Masonry | A06BB299-00001 Demolition Work Revamping Work Demolition Work of Masonry for Masonry Wall incl. Plastering, Any Type of Lining and etc. Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | A06BB299 | 00001 | A06BB299-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 299 | Demolition Work of Masonry |  | 0 |  | 0 |  | 0 |  | 0 | 21 | for Masonry Wall incl. Plastering, Any Type of Lining and etc. | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A06BB299 | A06BB299-00001
|  |  |  | A06BB300 Demolition Work Revamping Work Demolition Work of Roof Waterproofing System | A06BB300-00001 Demolition Work Revamping Work Demolition Work of Roof Waterproofing System for Roof Waterproofing System incl. Conc. Tile, Conc. Screed for Protection, Waterproofing Membrane, Rigid Insulation and etc. Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | A06BB300 | 00001 | A06BB300-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 300 | Demolition Work of Roof Waterproofing System |  | 0 |  | 0 |  | 0 |  | 0 | 22 | for Roof Waterproofing System incl. Conc. Tile, Conc. Screed for Protection, Waterproofing Membrane, Rigid Insulation and etc. | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A06BB300 | A06BB300-00001
|  |  |  | A06BB301 Demolition Work Revamping Work Demolition Work of Finishing Material | A06BB301-00001 Demolition Work Revamping Work Demolition Work of Finishing Material for Existing Floor Finish incl. Flooring Tile, Mortar Bed and etc. Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | A06BB301 | 00001 | A06BB301-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 301 | Demolition Work of Finishing Material |  | 0 |  | 0 |  | 0 |  | 0 | 23 | for Existing Floor Finish incl. Flooring Tile, Mortar Bed and etc. | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A06BB301 | A06BB301-00001
|  |  |  | A06BB301 Demolition Work Revamping Work Demolition Work of Finishing Material | A06BB301-00002 Demolition Work Revamping Work Demolition Work of Finishing Material for Existing Wall Finish incl. Wall Tile, Plastering and etc. Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | A06BB301 | 00002 | A06BB301-00002 | AR | A06 | Demolition Work | BB | Revamping Work | 301 | Demolition Work of Finishing Material |  | 0 |  | 0 |  | 0 |  | 0 | 24 | for Existing Wall Finish incl. Wall Tile, Plastering and etc. | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A06BB301 | A06BB301-00002
|  |  |  | A06BB301 Demolition Work Revamping Work Demolition Work of Finishing Material | A06BB301-00003 Demolition Work Revamping Work Demolition Work of Finishing Material for Existing False Ceiling System incl. Any Material of False Ceiling System Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | A06BB301 | 00003 | A06BB301-00003 | AR | A06 | Demolition Work | BB | Revamping Work | 301 | Demolition Work of Finishing Material |  | 0 |  | 0 |  | 0 |  | 0 | 25 | for Existing False Ceiling System incl. Any Material of False Ceiling System | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A06BB301 | A06BB301-00003
|  |  |  | A06BB302 Demolition Work Revamping Work Demolition Work of Door | A06BB302-00001 Demolition Work Revamping Work Demolition Work of Door Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | A06BB302 | 00001 | A06BB302-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 302 | Demolition Work of Door |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A06BB302 | A06BB302-00001
|  |  |  | A06BB303 Demolition Work Revamping Work Demolition Work of Window | A06BB303-00001 Demolition Work Revamping Work Demolition Work of Window Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | A06BB303 | 00001 | A06BB303-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 303 | Demolition Work of Window |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | EA | EA | A06BB303 | A06BB303-00001
|  |  |  | A06BB304 Demolition Work Revamping Work Demolition Work of Cladding | A06BB304-00001 Demolition Work Revamping Work Demolition Work of Cladding for Existing Roof Cladding Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | A06BB304 | 00001 | A06BB304-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 304 | Demolition Work of Cladding |  | 0 |  | 0 |  | 0 |  | 0 | 26 | for Existing Roof Cladding | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A06BB304 | A06BB304-00001
|  |  |  | A06BB304 Demolition Work Revamping Work Demolition Work of Cladding | A06BB304-00002 Demolition Work Revamping Work Demolition Work of Cladding for Existing Wall Cladding Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | A06BB304 | 00002 | A06BB304-00002 | AR | A06 | Demolition Work | BB | Revamping Work | 304 | Demolition Work of Cladding |  | 0 |  | 0 |  | 0 |  | 0 | 27 | for Existing Wall Cladding | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A06BB304 | A06BB304-00002
|  |  |  | A06BB305 Demolition Work Revamping Work Demolition Work of Fence & Gates | A06BB305-00001 Demolition Work Revamping Work Demolition Work of Fence & Gates Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | A06BB305 | 00001 | A06BB305-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 305 | Demolition Work of Fence & Gates |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | M2 | M2 | A06BB305 | A06BB305-00001
|  |  |  | A06BC306 Demolition Work Demolition Work Demolition Work of RC Structure Building | A06BC306-00001 Demolition Work Demolition Work Demolition Work of RC Structure Building for All Structural and Architectural Components Below and Above Ground Level Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | A06BC306 | 00001 | A06BC306-00001 | AR | A06 | Demolition Work | BC | Demolition Work | 306 | Demolition Work of RC Structure Building |  | 0 |  | 0 |  | 0 |  | 0 | 28 | for All Structural and Architectural Components Below and Above Ground Level | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | LOT | LOT | A06BC306 | A06BC306-00001
|  |  |  | A06BC307 Demolition Work Demolition Work Demolition Work of Steel Structure Shelter | A06BC307-00001 Demolition Work Demolition Work Demolition Work of Steel Structure Shelter for All Structural and Architectural Components Below and Above Ground Level Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | A06BC307 | 00001 | A06BC307-00001 | AR | A06 | Demolition Work | BC | Demolition Work | 307 | Demolition Work of Steel Structure Shelter |  | 0 |  | 0 |  | 0 |  | 0 | 28 | for All Structural and Architectural Components Below and Above Ground Level | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | LOT | LOT | A06BC307 | A06BC307-00001
|  |  |  | A10SA000 Site Instruction General / Common Work (Other Work) - | A10SA000-00001 Site Instruction General / Common Work (Other Work) - | A10SA000 | 00001 | A10SA000-00001 | AR | A10 | Site Instruction | SA | General / Common Work (Other Work) | 000 | - |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LOT | LOT | A10SA000 | A10SA000-00001
|  |  |  | A10SB000 Site Instruction Incentive of Subcontractor (Progress Expediting) - | A10SB000-00001 Site Instruction Incentive of Subcontractor (Progress Expediting) - | A10SB000 | 00001 | A10SB000-00001 | AR | A10 | Site Instruction | SB | Incentive of Subcontractor (Progress Expediting) | 000 | - |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LOT | LOT | A10SB000 | A10SB000-00001
|  |  |  | A10SC000 Site Instruction Claim of Subcontractor - | A10SC000-00001 Site Instruction Claim of Subcontractor - | A10SC000 | 00001 | A10SC000-00001 | AR | A10 | Site Instruction | SC | Claim of Subcontractor | 000 | - |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LOT | LOT | A10SC000 | A10SC000-00001
|  |  |  | #VALUE! |  | #VALUE!
|  |  |  | S01AA007 Main Steel Structure Fabrication Work Shelter/Building Girth & Purlin | S01AA007-00001 Main Steel Structure Fabrication Work Shelter/Building Girth & Purlin | S01AA007 | 00001 | S01AA007-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 007 | Girth & Purlin |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S01AA007 | S01AA007-00001
|  |  |  | S01AA008 Main Steel Structure Fabrication Work Shelter/Building P.E.B. (Pre-Engineered Building) | S01AA008-00001 Main Steel Structure Fabrication Work Shelter/Building P.E.B. (Pre-Engineered Building) | S01AA008 | 00001 | S01AA008-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 008 | P.E.B. (Pre-Engineered Building) |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S01AA008 | S01AA008-00001
|  |  |  | S01AA009 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009-00001 Main Steel Structure Fabrication Work Shelter/Building Plates - Gusset, Stiffener, ETC | S01AA009 | 00001 | S01AA009-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 009 | Plates - Gusset, Stiffener, ETC |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S01AA009 | S01AA009-00001
|  |  |  | S01AA011 Main Steel Structure Fabrication Work Shelter/Building High Strength Bolts&Nuts | S01AA011-00001 Main Steel Structure Fabrication Work Shelter/Building High Strength Bolts&Nuts | S01AA011 | 00001 | S01AA011-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 011 | High Strength Bolts&Nuts |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S01AA011 | S01AA011-00001
|  |  |  | S01AA012 Main Steel Structure Fabrication Work Shelter/Building Common Bolts&Nuts | S01AA012-00001 Main Steel Structure Fabrication Work Shelter/Building Common Bolts&Nuts | S01AA012 | 00001 | S01AA012-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 012 | Common Bolts&Nuts |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S01AA012 | S01AA012-00001
|  |  |  | S01AA071 Main Steel Structure Fabrication Work Shelter/Building Extra Heavy Steel - Standard | S01AA071-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Heavy Steel - Standard | S01AA071 | 00001 | S01AA071-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 071 | Extra Heavy Steel - Standard |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥( )KG/M | TON | TON | S01AA071 | S01AA071-00001
|  |  |  | S01AA072 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Standard | S01AA072 | 00001 | S01AA072-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 072 | Heavy Steel - Standard |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | TON | TON | S01AA072 | S01AA072-00001
|  |  |  | S01AA073 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Standard | S01AA073 | 00001 | S01AA073-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 073 | Medium Steel - Standard |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | TON | TON | S01AA073 | S01AA073-00001
|  |  |  | S01AA074 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Standard | S01AA074 | 00001 | S01AA074-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 074 | Light Steel - Standard |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | TON | TON | S01AA074 | S01AA074-00001
|  |  |  | S01AA075 Main Steel Structure Fabrication Work Shelter/Building Extra Light Steel - Standard | S01AA075-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Light Steel - Standard | S01AA075 | 00001 | S01AA075-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 075 | Extra Light Steel - Standard |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | ( )KG/M>Weight | TON | TON | S01AA075 | S01AA075-00001
|  |  |  | S01AA076 Main Steel Structure Fabrication Work Shelter/Building Extra Heavy Steel - Built up | S01AA076-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Heavy Steel - Built up | S01AA076 | 00001 | S01AA076-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 076 | Extra Heavy Steel - Built up |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥( )KG/M | TON | TON | S01AA076 | S01AA076-00001
|  |  |  | S01AA077 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Built up | S01AA077-00001 Main Steel Structure Fabrication Work Shelter/Building Heavy Steel - Built up | S01AA077 | 00001 | S01AA077-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 077 | Heavy Steel - Built up |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | TON | TON | S01AA077 | S01AA077-00001
|  |  |  | S01AA078 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Built up | S01AA078-00001 Main Steel Structure Fabrication Work Shelter/Building Medium Steel - Built up | S01AA078 | 00001 | S01AA078-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 078 | Medium Steel - Built up |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | TON | TON | S01AA078 | S01AA078-00001
|  |  |  | S01AA079 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Built up | S01AA079-00001 Main Steel Structure Fabrication Work Shelter/Building Light Steel - Built up | S01AA079 | 00001 | S01AA079-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 079 | Light Steel - Built up |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | TON | TON | S01AA079 | S01AA079-00001
|  |  |  | S01AA080 Main Steel Structure Fabrication Work Shelter/Building Extra Light Steel - Built up | S01AA080-00001 Main Steel Structure Fabrication Work Shelter/Building Extra Light Steel - Built up | S01AA080 | 00001 | S01AA080-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 080 | Extra Light Steel - Built up |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | ( )KG/M>Weight | TON | TON | S01AA080 | S01AA080-00001
|  |  |  | S02AA017 Miscellaneous Steel Fabrication Work Shelter/Building Checkered/Flooring Plate | S02AA017-00002 Miscellaneous Steel Fabrication Work Shelter/Building Checkered/Flooring Plate SUS Checkered plate | S02AA017 | 00002 | S02AA017-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 017 | Checkered/Flooring Plate | 07 | SUS Checkered plate |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | THK=( )mm | 0 | 0 | M2 | M2 | S02AA017 | S02AA017-00002
|  |  |  | S02AA017 Miscellaneous Steel Fabrication Work Shelter/Building Checkered/Flooring Plate | S02AA017-00003 Miscellaneous Steel Fabrication Work Shelter/Building Checkered/Flooring Plate Galvanized Steel THK ≤ 6mm | S02AA017 | 00003 | S02AA017-00003 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 017 | Checkered/Flooring Plate | 09 | Galvanized Steel | 18 | THK ≤ 6mm | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S02AA017 | S02AA017-00003
|  |  |  | S02AA017 Miscellaneous Steel Fabrication Work Shelter/Building Checkered/Flooring Plate | S02AA017-00004 Miscellaneous Steel Fabrication Work Shelter/Building Checkered/Flooring Plate Galvanized Steel THK > 6mm | S02AA017 | 00004 | S02AA017-00004 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 017 | Checkered/Flooring Plate | 09 | Galvanized Steel | 19 | THK > 6mm | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S02AA017 | S02AA017-00004
|  |  |  | S02AA017 Miscellaneous Steel Fabrication Work Shelter/Building Checkered/Flooring Plate | S02AA017-00005 Miscellaneous Steel Fabrication Work Shelter/Building Checkered/Flooring Plate Galvanized Steel W/Painting THK ≤ 6mm | S02AA017 | 00005 | S02AA017-00005 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 017 | Checkered/Flooring Plate | 10 | Galvanized Steel W/Painting | 18 | THK ≤ 6mm | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S02AA017 | S02AA017-00005
|  |  |  | S02AA017 Miscellaneous Steel Fabrication Work Shelter/Building Checkered/Flooring Plate | S02AA017-00006 Miscellaneous Steel Fabrication Work Shelter/Building Checkered/Flooring Plate Galvanized Steel W/Painting THK > 6mm | S02AA017 | 00006 | S02AA017-00006 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 017 | Checkered/Flooring Plate | 10 | Galvanized Steel W/Painting | 19 | THK > 6mm | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S02AA017 | S02AA017-00006
|  |  |  | S02AA018 Miscellaneous Steel Fabrication Work Shelter/Building Grating | S02AA018-00002 Miscellaneous Steel Fabrication Work Shelter/Building Grating Hot-Dip Galvanized Steel, (I=25) | S02AA018 | 00002 | S02AA018-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 018 | Grating | 11 | Hot-Dip Galvanized Steel, (I=25) |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S02AA018 | S02AA018-00002
|  |  |  | S02AA018 Miscellaneous Steel Fabrication Work Shelter/Building Grating | S02AA018-00003 Miscellaneous Steel Fabrication Work Shelter/Building Grating Hot-Dip Galvanized Steel, (I=32) | S02AA018 | 00003 | S02AA018-00003 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 018 | Grating | 12 | Hot-Dip Galvanized Steel, (I=32) |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S02AA018 | S02AA018-00003
|  |  |  | S02AA018 Miscellaneous Steel Fabrication Work Shelter/Building Grating | S02AA018-00004 Miscellaneous Steel Fabrication Work Shelter/Building Grating Hot-Dip Galvanized Steel, (I=50) | S02AA018 | 00004 | S02AA018-00004 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 018 | Grating | 13 | Hot-Dip Galvanized Steel, (I=50) |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S02AA018 | S02AA018-00004
|  |  |  | S02AA018 Miscellaneous Steel Fabrication Work Shelter/Building Grating | S02AA018-00005 Miscellaneous Steel Fabrication Work Shelter/Building Grating Hot-Dip Galvanized Steel, (I=75) | S02AA018 | 00005 | S02AA018-00005 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 018 | Grating | 14 | Hot-Dip Galvanized Steel, (I=75) |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S02AA018 | S02AA018-00005
|  |  |  | S02AA019 Miscellaneous Steel Fabrication Work Shelter/Building Steel Stairs | S02AA019-00002 Miscellaneous Steel Fabrication Work Shelter/Building Steel Stairs Galvanized Steel | S02AA019 | 00002 | S02AA019-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 019 | Steel Stairs | 09 | Galvanized Steel |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S02AA019 | S02AA019-00002
|  |  |  | S02AA019 Miscellaneous Steel Fabrication Work Shelter/Building Steel Stairs | S02AA019-00003 Miscellaneous Steel Fabrication Work Shelter/Building Steel Stairs Galvanized Steel W/Painting | S02AA019 | 00003 | S02AA019-00003 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 019 | Steel Stairs | 10 | Galvanized Steel W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S02AA019 | S02AA019-00003
|  |  |  | S02AA020 Miscellaneous Steel Fabrication Work Shelter/Building Steel Handrails | S02AA020-00002 Miscellaneous Steel Fabrication Work Shelter/Building Steel Handrails W/Painting | S02AA020 | 00002 | S02AA020-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 020 | Steel Handrails | 08 | W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S02AA020 | S02AA020-00002
|  |  |  | S02AA020 Miscellaneous Steel Fabrication Work Shelter/Building Steel Handrails | S02AA020-00003 Miscellaneous Steel Fabrication Work Shelter/Building Steel Handrails Galvanized Steel | S02AA020 | 00003 | S02AA020-00003 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 020 | Steel Handrails | 09 | Galvanized Steel |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S02AA020 | S02AA020-00003
|  |  |  | S02AA020 Miscellaneous Steel Fabrication Work Shelter/Building Steel Handrails | S02AA020-00004 Miscellaneous Steel Fabrication Work Shelter/Building Steel Handrails Galvanized Steel W/Painting | S02AA020 | 00004 | S02AA020-00004 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 020 | Steel Handrails | 10 | Galvanized Steel W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S02AA020 | S02AA020-00004
|  |  |  | S02AA021 Miscellaneous Steel Fabrication Work Shelter/Building Steel Handrails - Removable | S02AA021-00002 Miscellaneous Steel Fabrication Work Shelter/Building Steel Handrails - Removable W/Painting | S02AA021 | 00002 | S02AA021-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 021 | Steel Handrails - Removable | 08 | W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S02AA021 | S02AA021-00002
|  |  |  | S02AA021 Miscellaneous Steel Fabrication Work Shelter/Building Steel Handrails - Removable | S02AA021-00003 Miscellaneous Steel Fabrication Work Shelter/Building Steel Handrails - Removable Galvanized Steel | S02AA021 | 00003 | S02AA021-00003 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 021 | Steel Handrails - Removable | 09 | Galvanized Steel |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S02AA021 | S02AA021-00003
|  |  |  | S02AA021 Miscellaneous Steel Fabrication Work Shelter/Building Steel Handrails - Removable | S02AA021-00004 Miscellaneous Steel Fabrication Work Shelter/Building Steel Handrails - Removable Galvanized Steel W/Painting | S02AA021 | 00004 | S02AA021-00004 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 021 | Steel Handrails - Removable | 10 | Galvanized Steel W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S02AA021 | S02AA021-00004
|  |  |  | S02AA022 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Handrail | S02AA022-00002 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Handrail SUS 304 | S02AA022 | 00002 | S02AA022-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 022 | Stainless Steel Handrail | 15 | SUS 304 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S02AA022 | S02AA022-00002
|  |  |  | S02AA022 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Handrail | S02AA022-00003 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Handrail SUS 316L | S02AA022 | 00003 | S02AA022-00003 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 022 | Stainless Steel Handrail | 16 | SUS 316L |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S02AA022 | S02AA022-00003
|  |  |  | S02AA022 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Handrail | S02AA022-00004 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Handrail SUS Duplex | S02AA022 | 00004 | S02AA022-00004 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 022 | Stainless Steel Handrail | 17 | SUS Duplex |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S02AA022 | S02AA022-00004
|  |  |  | S02AA024 Miscellaneous Steel Fabrication Work Shelter/Building Galvanized Steel Deck Plate | S02AA024-00001 Miscellaneous Steel Fabrication Work Shelter/Building Galvanized Steel Deck Plate | S02AA024 | 00001 | S02AA024-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 024 | Galvanized Steel Deck Plate |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | M2 | M2 | S02AA024 | S02AA024-00001
|  |  |  | S02AA037 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Handrail - Removable | S02AA037-00001 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Handrail - Removable SUS 304 | S02AA037 | 00001 | S02AA037-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 037 | Stainless Steel Handrail - Removable | 15 | SUS 304 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S02AA037 | S02AA037-00001
|  |  |  | S02AA037 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Handrail - Removable | S02AA037-00002 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Handrail - Removable SUS 316L | S02AA037 | 00002 | S02AA037-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 037 | Stainless Steel Handrail - Removable | 16 | SUS 316L |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S02AA037 | S02AA037-00002
|  |  |  | S02AA037 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Handrail - Removable | S02AA037-00003 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Handrail - Removable SUS Duplex | S02AA037 | 00003 | S02AA037-00003 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 037 | Stainless Steel Handrail - Removable | 17 | SUS Duplex |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S02AA037 | S02AA037-00003
|  |  |  | S02AA038 Miscellaneous Steel Fabrication Work Shelter/Building FRP Grating | S02AA038-00001 Miscellaneous Steel Fabrication Work Shelter/Building FRP Grating | S02AA038 | 00001 | S02AA038-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 038 | FRP Grating |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | M2 | M2 | S02AA038 | S02AA038-00001
|  |  |  | S02AA039 Miscellaneous Steel Fabrication Work Shelter/Building FRP Handrail | S02AA039-00001 Miscellaneous Steel Fabrication Work Shelter/Building FRP Handrail | S02AA039 | 00001 | S02AA039-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 039 | FRP Handrail |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S02AA039 | S02AA039-00001
|  |  |  | S02AA040 Miscellaneous Steel Fabrication Work Shelter/Building FRP Handrail - Removable | S02AA040-00001 Miscellaneous Steel Fabrication Work Shelter/Building FRP Handrail - Removable | S02AA040 | 00001 | S02AA040-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 040 | FRP Handrail - Removable |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S02AA040 | S02AA040-00001
|  |  |  | S02AA041 Miscellaneous Steel Fabrication Work Shelter/Building Steel Ladder w/ Cage | S02AA041-00001 Miscellaneous Steel Fabrication Work Shelter/Building Steel Ladder w/ Cage W/Painting | S02AA041 | 00001 | S02AA041-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 041 | Steel Ladder w/ Cage | 08 | W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S02AA041 | S02AA041-00001
|  |  |  | S02AA041 Miscellaneous Steel Fabrication Work Shelter/Building Steel Ladder w/ Cage | S02AA041-00002 Miscellaneous Steel Fabrication Work Shelter/Building Steel Ladder w/ Cage Galvanized Steel | S02AA041 | 00002 | S02AA041-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 041 | Steel Ladder w/ Cage | 09 | Galvanized Steel |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S02AA041 | S02AA041-00002
|  |  |  | S02AA041 Miscellaneous Steel Fabrication Work Shelter/Building Steel Ladder w/ Cage | S02AA041-00003 Miscellaneous Steel Fabrication Work Shelter/Building Steel Ladder w/ Cage Galvanized Steel W/Painting | S02AA041 | 00003 | S02AA041-00003 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 041 | Steel Ladder w/ Cage | 10 | Galvanized Steel W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S02AA041 | S02AA041-00003
|  |  |  | S02AA042 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Ladder w/ Cage | S02AA042-00001 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Ladder w/ Cage SUS 304 | S02AA042 | 00001 | S02AA042-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 042 | Stainless Steel Ladder w/ Cage | 15 | SUS 304 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S02AA042 | S02AA042-00001
|  |  |  | S02AA042 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Ladder w/ Cage | S02AA042-00002 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Ladder w/ Cage SUS 316L | S02AA042 | 00002 | S02AA042-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 042 | Stainless Steel Ladder w/ Cage | 16 | SUS 316L |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S02AA042 | S02AA042-00002
|  |  |  | S02AA042 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Ladder w/ Cage | S02AA042-00003 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Ladder w/ Cage SUS Duplex | S02AA042 | 00003 | S02AA042-00003 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 042 | Stainless Steel Ladder w/ Cage | 17 | SUS Duplex |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S02AA042 | S02AA042-00003
|  |  |  | S02AA043 Miscellaneous Steel Fabrication Work Shelter/Building FRP Ladder w/ Cage | S02AA043-00001 Miscellaneous Steel Fabrication Work Shelter/Building FRP Ladder w/ Cage | S02AA043 | 00001 | S02AA043-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 043 | FRP Ladder w/ Cage |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S02AA043 | S02AA043-00001
|  |  |  | S02AA044 Miscellaneous Steel Fabrication Work Shelter/Building Steel Ladder w/o Cage | S02AA044-00001 Miscellaneous Steel Fabrication Work Shelter/Building Steel Ladder w/o Cage W/Painting | S02AA044 | 00001 | S02AA044-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 044 | Steel Ladder w/o Cage | 08 | W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S02AA044 | S02AA044-00001
|  |  |  | S02AA044 Miscellaneous Steel Fabrication Work Shelter/Building Steel Ladder w/o Cage | S02AA044-00002 Miscellaneous Steel Fabrication Work Shelter/Building Steel Ladder w/o Cage Galvanized Steel | S02AA044 | 00002 | S02AA044-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 044 | Steel Ladder w/o Cage | 09 | Galvanized Steel |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S02AA044 | S02AA044-00002
|  |  |  | S02AA044 Miscellaneous Steel Fabrication Work Shelter/Building Steel Ladder w/o Cage | S02AA044-00003 Miscellaneous Steel Fabrication Work Shelter/Building Steel Ladder w/o Cage Galvanized Steel W/Painting | S02AA044 | 00003 | S02AA044-00003 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 044 | Steel Ladder w/o Cage | 10 | Galvanized Steel W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S02AA044 | S02AA044-00003
|  |  |  | S02AA045 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Ladder w/o Cage | S02AA045-00001 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Ladder w/o Cage SUS 304 | S02AA045 | 00001 | S02AA045-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 045 | Stainless Steel Ladder w/o Cage | 15 | SUS 304 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S02AA045 | S02AA045-00001
|  |  |  | S02AA045 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Ladder w/o Cage | S02AA045-00002 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Ladder w/o Cage SUS 316L | S02AA045 | 00002 | S02AA045-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 045 | Stainless Steel Ladder w/o Cage | 16 | SUS 316L |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S02AA045 | S02AA045-00002
|  |  |  | S02AA045 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Ladder w/o Cage | S02AA045-00003 Miscellaneous Steel Fabrication Work Shelter/Building Stainless Steel Ladder w/o Cage SUS Duplex | S02AA045 | 00003 | S02AA045-00003 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 045 | Stainless Steel Ladder w/o Cage | 17 | SUS Duplex |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S02AA045 | S02AA045-00003
|  |  |  | S02AA046 Miscellaneous Steel Fabrication Work Shelter/Building FRP Ladder w/o Cage | S02AA046-00001 Miscellaneous Steel Fabrication Work Shelter/Building FRP Ladder w/o Cage | S02AA046 | 00001 | S02AA046-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 046 | FRP Ladder w/o Cage |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S02AA046 | S02AA046-00001
|  |  |  | S03AA007 Main Steel Structure Erection Work Shelter/Building Girth & Purlin | S03AA007-00001 Main Steel Structure Erection Work Shelter/Building Girth & Purlin | S03AA007 | 00001 | S03AA007-00001 | SS | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 007 | Girth & Purlin |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S03AA007 | S03AA007-00001
|  |  |  | S03AA008 Main Steel Structure Erection Work Shelter/Building P.E.B. (Pre-Engineered Building) | S03AA008-00001 Main Steel Structure Erection Work Shelter/Building P.E.B. (Pre-Engineered Building) | S03AA008 | 00001 | S03AA008-00001 | SS | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 008 | P.E.B. (Pre-Engineered Building) |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S03AA008 | S03AA008-00001
|  |  |  | S03AA030 Main Steel Structure Erection Work Shelter/Building Non-Shrink Grouting | S03AA030-00001 Main Steel Structure Erection Work Shelter/Building Non-Shrink Grouting | S03AA030 | 00001 | S03AA030-00001 | SS | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 030 | Non-Shrink Grouting |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | THK=( )mm | 0 | 0 | M3 | M3 | S03AA030 | S03AA030-00001
|  |  |  | S03AA031 Main Steel Structure Erection Work Shelter/Building Epoxy Grouting | S03AA031-00001 Main Steel Structure Erection Work Shelter/Building Epoxy Grouting | S03AA031 | 00001 | S03AA031-00001 | SS | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 031 | Epoxy Grouting |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | THK=( )mm | 0 | 0 | M3 | M3 | S03AA031 | S03AA031-00001
|  |  |  | S03AA081 Main Steel Structure Erection Work Shelter/Building Extra Heavy Steel | S03AA081-00001 Main Steel Structure Erection Work Shelter/Building Extra Heavy Steel | S03AA081 | 00001 | S03AA081-00001 | SS | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 081 | Extra Heavy Steel |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S03AA081 | S03AA081-00001
|  |  |  | S03AA082 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082-00001 Main Steel Structure Erection Work Shelter/Building Heavy Steel | S03AA082 | 00001 | S03AA082-00001 | SS | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 082 | Heavy Steel |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S03AA082 | S03AA082-00001
|  |  |  | S03AA083 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083-00001 Main Steel Structure Erection Work Shelter/Building Medium Steel | S03AA083 | 00001 | S03AA083-00001 | SS | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 083 | Medium Steel |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S03AA083 | S03AA083-00001
|  |  |  | S03AA084 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084-00001 Main Steel Structure Erection Work Shelter/Building Light Steel | S03AA084 | 00001 | S03AA084-00001 | SS | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 084 | Light Steel |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S03AA084 | S03AA084-00001
|  |  |  | S03AA085 Main Steel Structure Erection Work Shelter/Building Extra Light Steel | S03AA085-00001 Main Steel Structure Erection Work Shelter/Building Extra Light Steel | S03AA085 | 00001 | S03AA085-00001 | SS | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 085 | Extra Light Steel |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S03AA085 | S03AA085-00001
|  |  |  | S04AA017 Miscellaneous Steel Erection Work Shelter/Building Checkered/Flooring Plate | S04AA017-00001 Miscellaneous Steel Erection Work Shelter/Building Checkered/Flooring Plate | S04AA017 | 00001 | S04AA017-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 017 | Checkered/Flooring Plate |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | THK=( )mm | 0 | 0 | M2 | M2 | S04AA017 | S04AA017-00001
|  |  |  | S04AA018 Miscellaneous Steel Erection Work Shelter/Building Grating | S04AA018-00002 Miscellaneous Steel Erection Work Shelter/Building Grating Hot-Dip Galvanized Steel, (I=25) | S04AA018 | 00002 | S04AA018-00002 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 018 | Grating | 11 | Hot-Dip Galvanized Steel, (I=25) |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S04AA018 | S04AA018-00002
|  |  |  | S04AA018 Miscellaneous Steel Erection Work Shelter/Building Grating | S04AA018-00003 Miscellaneous Steel Erection Work Shelter/Building Grating Hot-Dip Galvanized Steel, (I=32) | S04AA018 | 00003 | S04AA018-00003 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 018 | Grating | 12 | Hot-Dip Galvanized Steel, (I=32) |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S04AA018 | S04AA018-00003
|  |  |  | S04AA018 Miscellaneous Steel Erection Work Shelter/Building Grating | S04AA018-00004 Miscellaneous Steel Erection Work Shelter/Building Grating Hot-Dip Galvanized Steel, (I=50) | S04AA018 | 00004 | S04AA018-00004 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 018 | Grating | 13 | Hot-Dip Galvanized Steel, (I=50) |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S04AA018 | S04AA018-00004
|  |  |  | S04AA018 Miscellaneous Steel Erection Work Shelter/Building Grating | S04AA018-00005 Miscellaneous Steel Erection Work Shelter/Building Grating Hot-Dip Galvanized Steel, (I=75) | S04AA018 | 00005 | S04AA018-00005 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 018 | Grating | 14 | Hot-Dip Galvanized Steel, (I=75) |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S04AA018 | S04AA018-00005
|  |  |  | S04AA019 Miscellaneous Steel Erection Work Shelter/Building Steel Stairs | S04AA019-00001 Miscellaneous Steel Erection Work Shelter/Building Steel Stairs | S04AA019 | 00001 | S04AA019-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 019 | Steel Stairs |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | M | M | S04AA019 | S04AA019-00001
|  |  |  | S04AA020 Miscellaneous Steel Erection Work Shelter/Building Steel Handrails | S04AA020-00001 Miscellaneous Steel Erection Work Shelter/Building Steel Handrails | S04AA020 | 00001 | S04AA020-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 020 | Steel Handrails |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | H=( )mm | 0 | M | M | S04AA020 | S04AA020-00001
|  |  |  | S04AA021 Miscellaneous Steel Erection Work Shelter/Building Steel Handrails - Removable | S04AA021-00001 Miscellaneous Steel Erection Work Shelter/Building Steel Handrails - Removable | S04AA021 | 00001 | S04AA021-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 021 | Steel Handrails - Removable |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | H=( )mm | 0 | M | M | S04AA021 | S04AA021-00001
|  |  |  | S04AA022 Miscellaneous Steel Erection Work Shelter/Building Stainless Steel Handrail | S04AA022-00001 Miscellaneous Steel Erection Work Shelter/Building Stainless Steel Handrail | S04AA022 | 00001 | S04AA022-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 022 | Stainless Steel Handrail |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S04AA022 | S04AA022-00001
|  |  |  | S04AA024 Miscellaneous Steel Erection Work Shelter/Building Galvanized Steel Deck Plate | S04AA024-00001 Miscellaneous Steel Erection Work Shelter/Building Galvanized Steel Deck Plate | S04AA024 | 00001 | S04AA024-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 024 | Galvanized Steel Deck Plate |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | M2 | M2 | S04AA024 | S04AA024-00001
|  |  |  | S04AA037 Miscellaneous Steel Erection Work Shelter/Building Stainless Steel Handrail - Removable | S04AA037-00001 Miscellaneous Steel Erection Work Shelter/Building Stainless Steel Handrail - Removable | S04AA037 | 00001 | S04AA037-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 037 | Stainless Steel Handrail - Removable |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S04AA037 | S04AA037-00001
|  |  |  | S04AA038 Miscellaneous Steel Erection Work Shelter/Building FRP Grating | S04AA038-00001 Miscellaneous Steel Erection Work Shelter/Building FRP Grating | S04AA038 | 00001 | S04AA038-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 038 | FRP Grating |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | M2 | M2 | S04AA038 | S04AA038-00001
|  |  |  | S04AA039 Miscellaneous Steel Erection Work Shelter/Building FRP Handrail | S04AA039-00001 Miscellaneous Steel Erection Work Shelter/Building FRP Handrail | S04AA039 | 00001 | S04AA039-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 039 | FRP Handrail |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S04AA039 | S04AA039-00001
|  |  |  | S04AA040 Miscellaneous Steel Erection Work Shelter/Building FRP Handrail - Removable | S04AA040-00001 Miscellaneous Steel Erection Work Shelter/Building FRP Handrail - Removable | S04AA040 | 00001 | S04AA040-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 040 | FRP Handrail - Removable |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S04AA040 | S04AA040-00001
|  |  |  | S04AA041 Miscellaneous Steel Erection Work Shelter/Building Steel Ladder w/ Cage | S04AA041-00001 Miscellaneous Steel Erection Work Shelter/Building Steel Ladder w/ Cage | S04AA041 | 00001 | S04AA041-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 041 | Steel Ladder w/ Cage |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S04AA041 | S04AA041-00001
|  |  |  | S04AA042 Miscellaneous Steel Erection Work Shelter/Building Stainless Steel Ladder w/ Cage | S04AA042-00001 Miscellaneous Steel Erection Work Shelter/Building Stainless Steel Ladder w/ Cage | S04AA042 | 00001 | S04AA042-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 042 | Stainless Steel Ladder w/ Cage |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S04AA042 | S04AA042-00001
|  |  |  | S04AA043 Miscellaneous Steel Erection Work Shelter/Building FRP Ladder w/ Cage | S04AA043-00001 Miscellaneous Steel Erection Work Shelter/Building FRP Ladder w/ Cage | S04AA043 | 00001 | S04AA043-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 043 | FRP Ladder w/ Cage |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S04AA043 | S04AA043-00001
|  |  |  | S04AA044 Miscellaneous Steel Erection Work Shelter/Building Steel Ladder w/o Cage | S04AA044-00001 Miscellaneous Steel Erection Work Shelter/Building Steel Ladder w/o Cage | S04AA044 | 00001 | S04AA044-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 044 | Steel Ladder w/o Cage |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S04AA044 | S04AA044-00001
|  |  |  | S04AA045 Miscellaneous Steel Erection Work Shelter/Building Stainless Steel Ladder w/o Cage | S04AA045-00001 Miscellaneous Steel Erection Work Shelter/Building Stainless Steel Ladder w/o Cage | S04AA045 | 00001 | S04AA045-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 045 | Stainless Steel Ladder w/o Cage |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S04AA045 | S04AA045-00001
|  |  |  | S04AA046 Miscellaneous Steel Erection Work Shelter/Building FRP Ladder w/o Cage | S04AA046-00001 Miscellaneous Steel Erection Work Shelter/Building FRP Ladder w/o Cage | S04AA046 | 00001 | S04AA046-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 046 | FRP Ladder w/o Cage |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S04AA046 | S04AA046-00001
|  |  |  | S05AF032 Demolition Work Revamping Work (Shelter/Building) Demolition Work of Steel for Building/Shelter | S05AF032-00001 Demolition Work Revamping Work (Shelter/Building) Demolition Work of Steel for Building/Shelter | S05AF032 | 00001 | S05AF032-00001 | SS | S05 | Demolition Work | AF | Revamping Work (Shelter/Building) | 032 | Demolition Work of Steel for Building/Shelter |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TON | TON | S05AF032 | S05AF032-00001
|  |  |  | S11AA007 Main Steel Structure Fabrication Work for Revamping Shelter/Building Girth & Purlin | S11AA007-00001 Main Steel Structure Fabrication Work for Revamping Shelter/Building Girth & Purlin | S11AA007 | 00001 | S11AA007-00001 | SS | S11 | Main Steel Structure Fabrication Work for Revamping | AA | Shelter/Building | 007 | Girth & Purlin |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S11AA007 | S11AA007-00001
|  |  |  | S11AA008 Main Steel Structure Fabrication Work for Revamping Shelter/Building P.E.B. (Pre-Engineered Building) | S11AA008-00001 Main Steel Structure Fabrication Work for Revamping Shelter/Building P.E.B. (Pre-Engineered Building) | S11AA008 | 00001 | S11AA008-00001 | SS | S11 | Main Steel Structure Fabrication Work for Revamping | AA | Shelter/Building | 008 | P.E.B. (Pre-Engineered Building) |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S11AA008 | S11AA008-00001
|  |  |  | S11AA009 Main Steel Structure Fabrication Work for Revamping Shelter/Building Plates - Gusset, Stiffener, ETC | S11AA009-00001 Main Steel Structure Fabrication Work for Revamping Shelter/Building Plates - Gusset, Stiffener, ETC | S11AA009 | 00001 | S11AA009-00001 | SS | S11 | Main Steel Structure Fabrication Work for Revamping | AA | Shelter/Building | 009 | Plates - Gusset, Stiffener, ETC |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S11AA009 | S11AA009-00001
|  |  |  | S11AA011 Main Steel Structure Fabrication Work for Revamping Shelter/Building High Strength Bolts&Nuts | S11AA011-00001 Main Steel Structure Fabrication Work for Revamping Shelter/Building High Strength Bolts&Nuts | S11AA011 | 00001 | S11AA011-00001 | SS | S11 | Main Steel Structure Fabrication Work for Revamping | AA | Shelter/Building | 011 | High Strength Bolts&Nuts |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S11AA011 | S11AA011-00001
|  |  |  | S11AA012 Main Steel Structure Fabrication Work for Revamping Shelter/Building Common Bolts&Nuts | S11AA012-00001 Main Steel Structure Fabrication Work for Revamping Shelter/Building Common Bolts&Nuts | S11AA012 | 00001 | S11AA012-00001 | SS | S11 | Main Steel Structure Fabrication Work for Revamping | AA | Shelter/Building | 012 | Common Bolts&Nuts |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S11AA012 | S11AA012-00001
|  |  |  | S11AA071 Main Steel Structure Fabrication Work for Revamping Shelter/Building Extra Heavy Steel - Standard | S11AA071-00001 Main Steel Structure Fabrication Work for Revamping Shelter/Building Extra Heavy Steel - Standard | S11AA071 | 00001 | S11AA071-00001 | SS | S11 | Main Steel Structure Fabrication Work for Revamping | AA | Shelter/Building | 071 | Extra Heavy Steel - Standard |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥( )KG/M | TON | TON | S11AA071 | S11AA071-00001
|  |  |  | S11AA072 Main Steel Structure Fabrication Work for Revamping Shelter/Building Heavy Steel - Standard | S11AA072-00001 Main Steel Structure Fabrication Work for Revamping Shelter/Building Heavy Steel - Standard | S11AA072 | 00001 | S11AA072-00001 | SS | S11 | Main Steel Structure Fabrication Work for Revamping | AA | Shelter/Building | 072 | Heavy Steel - Standard |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | TON | TON | S11AA072 | S11AA072-00001
|  |  |  | S11AA073 Main Steel Structure Fabrication Work for Revamping Shelter/Building Medium Steel - Standard | S11AA073-00001 Main Steel Structure Fabrication Work for Revamping Shelter/Building Medium Steel - Standard | S11AA073 | 00001 | S11AA073-00001 | SS | S11 | Main Steel Structure Fabrication Work for Revamping | AA | Shelter/Building | 073 | Medium Steel - Standard |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | TON | TON | S11AA073 | S11AA073-00001
|  |  |  | S11AA074 Main Steel Structure Fabrication Work for Revamping Shelter/Building Light Steel - Standard | S11AA074-00001 Main Steel Structure Fabrication Work for Revamping Shelter/Building Light Steel - Standard | S11AA074 | 00001 | S11AA074-00001 | SS | S11 | Main Steel Structure Fabrication Work for Revamping | AA | Shelter/Building | 074 | Light Steel - Standard |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | TON | TON | S11AA074 | S11AA074-00001
|  |  |  | S11AA075 Main Steel Structure Fabrication Work for Revamping Shelter/Building Extra Light Steel - Standard | S11AA075-00001 Main Steel Structure Fabrication Work for Revamping Shelter/Building Extra Light Steel - Standard | S11AA075 | 00001 | S11AA075-00001 | SS | S11 | Main Steel Structure Fabrication Work for Revamping | AA | Shelter/Building | 075 | Extra Light Steel - Standard |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | ( )KG/M>Weight | TON | TON | S11AA075 | S11AA075-00001
|  |  |  | S11AA076 Main Steel Structure Fabrication Work for Revamping Shelter/Building Extra Heavy Steel - Built up | S11AA076-00001 Main Steel Structure Fabrication Work for Revamping Shelter/Building Extra Heavy Steel - Built up | S11AA076 | 00001 | S11AA076-00001 | SS | S11 | Main Steel Structure Fabrication Work for Revamping | AA | Shelter/Building | 076 | Extra Heavy Steel - Built up |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥( )KG/M | TON | TON | S11AA076 | S11AA076-00001
|  |  |  | S11AA077 Main Steel Structure Fabrication Work for Revamping Shelter/Building Heavy Steel - Built up | S11AA077-00001 Main Steel Structure Fabrication Work for Revamping Shelter/Building Heavy Steel - Built up | S11AA077 | 00001 | S11AA077-00001 | SS | S11 | Main Steel Structure Fabrication Work for Revamping | AA | Shelter/Building | 077 | Heavy Steel - Built up |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | Weight≥(90)KG/M | TON | TON | S11AA077 | S11AA077-00001
|  |  |  | S11AA078 Main Steel Structure Fabrication Work for Revamping Shelter/Building Medium Steel - Built up | S11AA078-00001 Main Steel Structure Fabrication Work for Revamping Shelter/Building Medium Steel - Built up | S11AA078 | 00001 | S11AA078-00001 | SS | S11 | Main Steel Structure Fabrication Work for Revamping | AA | Shelter/Building | 078 | Medium Steel - Built up |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (90)KG/M>Weight≥(30)KG/M | TON | TON | S11AA078 | S11AA078-00001
|  |  |  | S11AA079 Main Steel Structure Fabrication Work for Revamping Shelter/Building Light Steel - Built up | S11AA079-00001 Main Steel Structure Fabrication Work for Revamping Shelter/Building Light Steel - Built up | S11AA079 | 00001 | S11AA079-00001 | SS | S11 | Main Steel Structure Fabrication Work for Revamping | AA | Shelter/Building | 079 | Light Steel - Built up |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | (30)KG/M>Weight | TON | TON | S11AA079 | S11AA079-00001
|  |  |  | S11AA080 Main Steel Structure Fabrication Work for Revamping Shelter/Building Extra Light Steel - Built up | S11AA080-00001 Main Steel Structure Fabrication Work for Revamping Shelter/Building Extra Light Steel - Built up | S11AA080 | 00001 | S11AA080-00001 | SS | S11 | Main Steel Structure Fabrication Work for Revamping | AA | Shelter/Building | 080 | Extra Light Steel - Built up |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | ( )KG/M>Weight | TON | TON | S11AA080 | S11AA080-00001
|  |  |  | S12AA017 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Checkered/Flooring Plate | S12AA017-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Checkered/Flooring Plate SUS Checkered plate | S12AA017 | 00001 | S12AA017-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 017 | Checkered/Flooring Plate | 07 | SUS Checkered plate |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | THK=( )mm | 0 | 0 | M2 | M2 | S12AA017 | S12AA017-00001
|  |  |  | S12AA017 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Checkered/Flooring Plate | S12AA017-00002 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Checkered/Flooring Plate Galvanized Steel THK ≤ 6mm | S12AA017 | 00002 | S12AA017-00002 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 017 | Checkered/Flooring Plate | 09 | Galvanized Steel | 18 | THK ≤ 6mm | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S12AA017 | S12AA017-00002
|  |  |  | S12AA017 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Checkered/Flooring Plate | S12AA017-00003 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Checkered/Flooring Plate Galvanized Steel THK > 6mm | S12AA017 | 00003 | S12AA017-00003 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 017 | Checkered/Flooring Plate | 09 | Galvanized Steel | 19 | THK > 6mm | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S12AA017 | S12AA017-00003
|  |  |  | S12AA017 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Checkered/Flooring Plate | S12AA017-00004 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Checkered/Flooring Plate Galvanized Steel W/Painting THK ≤ 6mm | S12AA017 | 00004 | S12AA017-00004 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 017 | Checkered/Flooring Plate | 10 | Galvanized Steel W/Painting | 18 | THK ≤ 6mm | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S12AA017 | S12AA017-00004
|  |  |  | S12AA017 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Checkered/Flooring Plate | S12AA017-00005 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Checkered/Flooring Plate Galvanized Steel W/Painting THK > 6mm | S12AA017 | 00005 | S12AA017-00005 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 017 | Checkered/Flooring Plate | 10 | Galvanized Steel W/Painting | 19 | THK > 6mm | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S12AA017 | S12AA017-00005
|  |  |  | S12AA018 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Grating | S12AA018-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Grating Hot-Dip Galvanized Steel, (I=25) | S12AA018 | 00001 | S12AA018-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 018 | Grating | 11 | Hot-Dip Galvanized Steel, (I=25) |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S12AA018 | S12AA018-00001
|  |  |  | S12AA018 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Grating | S12AA018-00002 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Grating Hot-Dip Galvanized Steel, (I=32) | S12AA018 | 00002 | S12AA018-00002 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 018 | Grating | 12 | Hot-Dip Galvanized Steel, (I=32) |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S12AA018 | S12AA018-00002
|  |  |  | S12AA018 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Grating | S12AA018-00003 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Grating Hot-Dip Galvanized Steel, (I=50) | S12AA018 | 00003 | S12AA018-00003 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 018 | Grating | 13 | Hot-Dip Galvanized Steel, (I=50) |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S12AA018 | S12AA018-00003
|  |  |  | S12AA018 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Grating | S12AA018-00004 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Grating Hot-Dip Galvanized Steel, (I=75) | S12AA018 | 00004 | S12AA018-00004 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 018 | Grating | 14 | Hot-Dip Galvanized Steel, (I=75) |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S12AA018 | S12AA018-00004
|  |  |  | S12AA019 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Stairs | S12AA019-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Stairs Galvanized Steel | S12AA019 | 00001 | S12AA019-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 019 | Steel Stairs | 09 | Galvanized Steel |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S12AA019 | S12AA019-00001
|  |  |  | S12AA019 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Stairs | S12AA019-00002 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Stairs Galvanized Steel W/Painting | S12AA019 | 00002 | S12AA019-00002 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 019 | Steel Stairs | 10 | Galvanized Steel W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S12AA019 | S12AA019-00002
|  |  |  | S12AA020 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Handrails | S12AA020-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Handrails W/Painting | S12AA020 | 00001 | S12AA020-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 020 | Steel Handrails | 08 | W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S12AA020 | S12AA020-00001
|  |  |  | S12AA020 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Handrails | S12AA020-00002 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Handrails Galvanized Steel | S12AA020 | 00002 | S12AA020-00002 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 020 | Steel Handrails | 09 | Galvanized Steel |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S12AA020 | S12AA020-00002
|  |  |  | S12AA020 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Handrails | S12AA020-00003 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Handrails Galvanized Steel W/Painting | S12AA020 | 00003 | S12AA020-00003 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 020 | Steel Handrails | 10 | Galvanized Steel W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S12AA020 | S12AA020-00003
|  |  |  | S12AA021 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Handrails - Removable | S12AA021-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Handrails - Removable W/Painting | S12AA021 | 00001 | S12AA021-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 021 | Steel Handrails - Removable | 08 | W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S12AA021 | S12AA021-00001
|  |  |  | S12AA021 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Handrails - Removable | S12AA021-00002 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Handrails - Removable Galvanized Steel | S12AA021 | 00002 | S12AA021-00002 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 021 | Steel Handrails - Removable | 09 | Galvanized Steel |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S12AA021 | S12AA021-00002
|  |  |  | S12AA021 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Handrails - Removable | S12AA021-00003 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Handrails - Removable Galvanized Steel W/Painting | S12AA021 | 00003 | S12AA021-00003 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 021 | Steel Handrails - Removable | 10 | Galvanized Steel W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S12AA021 | S12AA021-00003
|  |  |  | S12AA022 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Handrail | S12AA022-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Handrail SUS 304 | S12AA022 | 00001 | S12AA022-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 022 | Stainless Steel Handrail | 15 | SUS 304 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S12AA022 | S12AA022-00001
|  |  |  | S12AA022 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Handrail | S12AA022-00002 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Handrail SUS 316L | S12AA022 | 00002 | S12AA022-00002 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 022 | Stainless Steel Handrail | 16 | SUS 316L |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S12AA022 | S12AA022-00002
|  |  |  | S12AA022 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Handrail | S12AA022-00003 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Handrail SUS Duplex | S12AA022 | 00003 | S12AA022-00003 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 022 | Stainless Steel Handrail | 17 | SUS Duplex |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S12AA022 | S12AA022-00003
|  |  |  | S12AA024 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Galvanized Steel Deck Plate | S12AA024-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Galvanized Steel Deck Plate | S12AA024 | 00001 | S12AA024-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 024 | Galvanized Steel Deck Plate |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | M2 | M2 | S12AA024 | S12AA024-00001
|  |  |  | S12AA037 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Handrail - Removable | S12AA037-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Handrail - Removable SUS 304 | S12AA037 | 00001 | S12AA037-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 037 | Stainless Steel Handrail - Removable | 15 | SUS 304 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S12AA037 | S12AA037-00001
|  |  |  | S12AA037 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Handrail - Removable | S12AA037-00002 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Handrail - Removable SUS 316L | S12AA037 | 00002 | S12AA037-00002 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 037 | Stainless Steel Handrail - Removable | 16 | SUS 316L |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S12AA037 | S12AA037-00002
|  |  |  | S12AA037 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Handrail - Removable | S12AA037-00003 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Handrail - Removable SUS Duplex | S12AA037 | 00003 | S12AA037-00003 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 037 | Stainless Steel Handrail - Removable | 17 | SUS Duplex |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S12AA037 | S12AA037-00003
|  |  |  | S12AA038 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building FRP Grating | S12AA038-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building FRP Grating | S12AA038 | 00001 | S12AA038-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 038 | FRP Grating |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | M2 | M2 | S12AA038 | S12AA038-00001
|  |  |  | S12AA039 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building FRP Handrail | S12AA039-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building FRP Handrail | S12AA039 | 00001 | S12AA039-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 039 | FRP Handrail |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S12AA039 | S12AA039-00001
|  |  |  | S12AA040 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building FRP Handrail - Removable | S12AA040-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building FRP Handrail - Removable | S12AA040 | 00001 | S12AA040-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 040 | FRP Handrail - Removable |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=( )mm | 0 | M | M | S12AA040 | S12AA040-00001
|  |  |  | S12AA041 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Ladder w/ Cage | S12AA041-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Ladder w/ Cage W/Painting | S12AA041 | 00001 | S12AA041-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 041 | Steel Ladder w/ Cage | 08 | W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S12AA041 | S12AA041-00001
|  |  |  | S12AA041 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Ladder w/ Cage | S12AA041-00002 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Ladder w/ Cage Galvanized Steel | S12AA041 | 00002 | S12AA041-00002 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 041 | Steel Ladder w/ Cage | 09 | Galvanized Steel |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S12AA041 | S12AA041-00002
|  |  |  | S12AA041 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Ladder w/ Cage | S12AA041-00003 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Ladder w/ Cage Galvanized Steel W/Painting | S12AA041 | 00003 | S12AA041-00003 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 041 | Steel Ladder w/ Cage | 10 | Galvanized Steel W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S12AA041 | S12AA041-00003
|  |  |  | S12AA042 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Ladder w/ Cage | S12AA042-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Ladder w/ Cage SUS 304 | S12AA042 | 00001 | S12AA042-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 042 | Stainless Steel Ladder w/ Cage | 15 | SUS 304 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S12AA042 | S12AA042-00001
|  |  |  | S12AA042 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Ladder w/ Cage | S12AA042-00002 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Ladder w/ Cage SUS 316L | S12AA042 | 00002 | S12AA042-00002 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 042 | Stainless Steel Ladder w/ Cage | 16 | SUS 316L |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S12AA042 | S12AA042-00002
|  |  |  | S12AA042 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Ladder w/ Cage | S12AA042-00003 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Ladder w/ Cage SUS Duplex | S12AA042 | 00003 | S12AA042-00003 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 042 | Stainless Steel Ladder w/ Cage | 17 | SUS Duplex |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S12AA042 | S12AA042-00003
|  |  |  | S12AA043 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building FRP Ladder w/ Cage | S12AA043-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building FRP Ladder w/ Cage | S12AA043 | 00001 | S12AA043-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 043 | FRP Ladder w/ Cage |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S12AA043 | S12AA043-00001
|  |  |  | S12AA044 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Ladder w/o Cage | S12AA044-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Ladder w/o Cage W/Painting | S12AA044 | 00001 | S12AA044-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 044 | Steel Ladder w/o Cage | 08 | W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S12AA044 | S12AA044-00001
|  |  |  | S12AA044 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Ladder w/o Cage | S12AA044-00002 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Ladder w/o Cage Galvanized Steel | S12AA044 | 00002 | S12AA044-00002 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 044 | Steel Ladder w/o Cage | 09 | Galvanized Steel |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S12AA044 | S12AA044-00002
|  |  |  | S12AA044 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Ladder w/o Cage | S12AA044-00003 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Steel Ladder w/o Cage Galvanized Steel W/Painting | S12AA044 | 00003 | S12AA044-00003 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 044 | Steel Ladder w/o Cage | 10 | Galvanized Steel W/Painting |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S12AA044 | S12AA044-00003
|  |  |  | S12AA045 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Ladder w/o Cage | S12AA045-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Ladder w/o Cage SUS 304 | S12AA045 | 00001 | S12AA045-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 045 | Stainless Steel Ladder w/o Cage | 15 | SUS 304 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S12AA045 | S12AA045-00001
|  |  |  | S12AA045 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Ladder w/o Cage | S12AA045-00002 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Ladder w/o Cage SUS 316L | S12AA045 | 00002 | S12AA045-00002 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 045 | Stainless Steel Ladder w/o Cage | 16 | SUS 316L |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S12AA045 | S12AA045-00002
|  |  |  | S12AA045 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Ladder w/o Cage | S12AA045-00003 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building Stainless Steel Ladder w/o Cage SUS Duplex | S12AA045 | 00003 | S12AA045-00003 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 045 | Stainless Steel Ladder w/o Cage | 17 | SUS Duplex |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S12AA045 | S12AA045-00003
|  |  |  | S12AA046 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building FRP Ladder w/o Cage | S12AA046-00001 Miscellaneous Steel Fabrication Work for Revamping Shelter/Building FRP Ladder w/o Cage | S12AA046 | 00001 | S12AA046-00001 | SS | S12 | Miscellaneous Steel Fabrication Work for Revamping | AA | Shelter/Building | 046 | FRP Ladder w/o Cage |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S12AA046 | S12AA046-00001
|  |  |  | S13AA007 Main Steel Structure Erection Work for Revamping Shelter/Building Girth & Purlin | S13AA007-00001 Main Steel Structure Erection Work for Revamping Shelter/Building Girth & Purlin | S13AA007 | 00001 | S13AA007-00001 | SS | S13 | Main Steel Structure Erection Work for Revamping | AA | Shelter/Building | 007 | Girth & Purlin |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S13AA007 | S13AA007-00001
|  |  |  | S13AA008 Main Steel Structure Erection Work for Revamping Shelter/Building P.E.B. (Pre-Engineered Building) | S13AA008-00001 Main Steel Structure Erection Work for Revamping Shelter/Building P.E.B. (Pre-Engineered Building) | S13AA008 | 00001 | S13AA008-00001 | SS | S13 | Main Steel Structure Erection Work for Revamping | AA | Shelter/Building | 008 | P.E.B. (Pre-Engineered Building) |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S13AA008 | S13AA008-00001
|  |  |  | S13AA030 Main Steel Structure Erection Work for Revamping Shelter/Building Non-Shrink Grouting | S13AA030-00001 Main Steel Structure Erection Work for Revamping Shelter/Building Non-Shrink Grouting | S13AA030 | 00001 | S13AA030-00001 | SS | S13 | Main Steel Structure Erection Work for Revamping | AA | Shelter/Building | 030 | Non-Shrink Grouting |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | THK=( )mm | 0 | 0 | M3 | M3 | S13AA030 | S13AA030-00001
|  |  |  | S13AA031 Main Steel Structure Erection Work for Revamping Shelter/Building Epoxy Grouting | S13AA031-00001 Main Steel Structure Erection Work for Revamping Shelter/Building Epoxy Grouting | S13AA031 | 00001 | S13AA031-00001 | SS | S13 | Main Steel Structure Erection Work for Revamping | AA | Shelter/Building | 031 | Epoxy Grouting |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | THK=( )mm | 0 | 0 | M3 | M3 | S13AA031 | S13AA031-00001
|  |  |  | S13AA081 Main Steel Structure Erection Work for Revamping Shelter/Building Extra Heavy Steel | S13AA081-00001 Main Steel Structure Erection Work for Revamping Shelter/Building Extra Heavy Steel | S13AA081 | 00001 | S13AA081-00001 | SS | S13 | Main Steel Structure Erection Work for Revamping | AA | Shelter/Building | 081 | Extra Heavy Steel |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S13AA081 | S13AA081-00001
|  |  |  | S13AA082 Main Steel Structure Erection Work for Revamping Shelter/Building Heavy Steel | S13AA082-00001 Main Steel Structure Erection Work for Revamping Shelter/Building Heavy Steel | S13AA082 | 00001 | S13AA082-00001 | SS | S13 | Main Steel Structure Erection Work for Revamping | AA | Shelter/Building | 082 | Heavy Steel |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S13AA082 | S13AA082-00001
|  |  |  | S13AA083 Main Steel Structure Erection Work for Revamping Shelter/Building Medium Steel | S13AA083-00001 Main Steel Structure Erection Work for Revamping Shelter/Building Medium Steel | S13AA083 | 00001 | S13AA083-00001 | SS | S13 | Main Steel Structure Erection Work for Revamping | AA | Shelter/Building | 083 | Medium Steel |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S13AA083 | S13AA083-00001
|  |  |  | S13AA084 Main Steel Structure Erection Work for Revamping Shelter/Building Light Steel | S13AA084-00001 Main Steel Structure Erection Work for Revamping Shelter/Building Light Steel | S13AA084 | 00001 | S13AA084-00001 | SS | S13 | Main Steel Structure Erection Work for Revamping | AA | Shelter/Building | 084 | Light Steel |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S13AA084 | S13AA084-00001
|  |  |  | S13AA085 Main Steel Structure Erection Work for Revamping Shelter/Building Extra Light Steel | S13AA085-00001 Main Steel Structure Erection Work for Revamping Shelter/Building Extra Light Steel | S13AA085 | 00001 | S13AA085-00001 | SS | S13 | Main Steel Structure Erection Work for Revamping | AA | Shelter/Building | 085 | Extra Light Steel |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | TON | TON | S13AA085 | S13AA085-00001
|  |  |  | S14AA017 Miscellaneous Steel Erection Work for Revamping Shelter/Building Checkered/Flooring Plate | S14AA017-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building Checkered/Flooring Plate | S14AA017 | 00001 | S14AA017-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 017 | Checkered/Flooring Plate |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S14AA017 | S14AA017-00001
|  |  |  | S14AA018 Miscellaneous Steel Erection Work for Revamping Shelter/Building Grating | S14AA018-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building Grating Hot-Dip Galvanized Steel, (I=25) | S14AA018 | 00001 | S14AA018-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 018 | Grating | 11 | Hot-Dip Galvanized Steel, (I=25) |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S14AA018 | S14AA018-00001
|  |  |  | S14AA018 Miscellaneous Steel Erection Work for Revamping Shelter/Building Grating | S14AA018-00002 Miscellaneous Steel Erection Work for Revamping Shelter/Building Grating Hot-Dip Galvanized Steel, (I=32) | S14AA018 | 00002 | S14AA018-00002 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 018 | Grating | 12 | Hot-Dip Galvanized Steel, (I=32) |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S14AA018 | S14AA018-00002
|  |  |  | S14AA018 Miscellaneous Steel Erection Work for Revamping Shelter/Building Grating | S14AA018-00003 Miscellaneous Steel Erection Work for Revamping Shelter/Building Grating Hot-Dip Galvanized Steel, (I=50) | S14AA018 | 00003 | S14AA018-00003 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 018 | Grating | 13 | Hot-Dip Galvanized Steel, (I=50) |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S14AA018 | S14AA018-00003
|  |  |  | S14AA018 Miscellaneous Steel Erection Work for Revamping Shelter/Building Grating | S14AA018-00004 Miscellaneous Steel Erection Work for Revamping Shelter/Building Grating Hot-Dip Galvanized Steel, (I=75) | S14AA018 | 00004 | S14AA018-00004 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 018 | Grating | 14 | Hot-Dip Galvanized Steel, (I=75) |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S14AA018 | S14AA018-00004
|  |  |  | S14AA019 Miscellaneous Steel Erection Work for Revamping Shelter/Building Steel Stairs | S14AA019-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building Steel Stairs | S14AA019 | 00001 | S14AA019-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 019 | Steel Stairs |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S14AA019 | S14AA019-00001
|  |  |  | S14AA020 Miscellaneous Steel Erection Work for Revamping Shelter/Building Steel Handrails | S14AA020-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building Steel Handrails | S14AA020 | 00001 | S14AA020-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 020 | Steel Handrails |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S14AA020 | S14AA020-00001
|  |  |  | S14AA021 Miscellaneous Steel Erection Work for Revamping Shelter/Building Steel Handrails - Removable | S14AA021-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building Steel Handrails - Removable | S14AA021 | 00001 | S14AA021-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 021 | Steel Handrails - Removable |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S14AA021 | S14AA021-00001
|  |  |  | S14AA022 Miscellaneous Steel Erection Work for Revamping Shelter/Building Stainless Steel Handrail | S14AA022-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building Stainless Steel Handrail | S14AA022 | 00001 | S14AA022-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 022 | Stainless Steel Handrail |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S14AA022 | S14AA022-00001
|  |  |  | S14AA024 Miscellaneous Steel Erection Work for Revamping Shelter/Building Galvanized Steel Deck Plate | S14AA024-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building Galvanized Steel Deck Plate | S14AA024 | 00001 | S14AA024-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 024 | Galvanized Steel Deck Plate |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S14AA024 | S14AA024-00001
|  |  |  | S14AA037 Miscellaneous Steel Erection Work for Revamping Shelter/Building Stainless Steel Handrail - Removable | S14AA037-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building Stainless Steel Handrail - Removable | S14AA037 | 00001 | S14AA037-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 037 | Stainless Steel Handrail - Removable |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S14AA037 | S14AA037-00001
|  |  |  | S14AA038 Miscellaneous Steel Erection Work for Revamping Shelter/Building FRP Grating | S14AA038-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building FRP Grating | S14AA038 | 00001 | S14AA038-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 038 | FRP Grating |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M2 | M2 | S14AA038 | S14AA038-00001
|  |  |  | S14AA039 Miscellaneous Steel Erection Work for Revamping Shelter/Building FRP Handrail | S14AA039-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building FRP Handrail | S14AA039 | 00001 | S14AA039-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 039 | FRP Handrail |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S14AA039 | S14AA039-00001
|  |  |  | S14AA040 Miscellaneous Steel Erection Work for Revamping Shelter/Building FRP Handrail - Removable | S14AA040-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building FRP Handrail - Removable | S14AA040 | 00001 | S14AA040-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 040 | FRP Handrail - Removable |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S14AA040 | S14AA040-00001
|  |  |  | S14AA041 Miscellaneous Steel Erection Work for Revamping Shelter/Building Steel Ladder w/ Cage | S14AA041-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building Steel Ladder w/ Cage | S14AA041 | 00001 | S14AA041-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 041 | Steel Ladder w/ Cage |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S14AA041 | S14AA041-00001
|  |  |  | S14AA042 Miscellaneous Steel Erection Work for Revamping Shelter/Building Stainless Steel Ladder w/ Cage | S14AA042-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building Stainless Steel Ladder w/ Cage | S14AA042 | 00001 | S14AA042-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 042 | Stainless Steel Ladder w/ Cage |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S14AA042 | S14AA042-00001
|  |  |  | S14AA043 Miscellaneous Steel Erection Work for Revamping Shelter/Building FRP Ladder w/ Cage | S14AA043-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building FRP Ladder w/ Cage | S14AA043 | 00001 | S14AA043-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 043 | FRP Ladder w/ Cage |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S14AA043 | S14AA043-00001
|  |  |  | S14AA044 Miscellaneous Steel Erection Work for Revamping Shelter/Building Steel Ladder w/o Cage | S14AA044-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building Steel Ladder w/o Cage | S14AA044 | 00001 | S14AA044-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 044 | Steel Ladder w/o Cage |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S14AA044 | S14AA044-00001
|  |  |  | S14AA045 Miscellaneous Steel Erection Work for Revamping Shelter/Building Stainless Steel Ladder w/o Cage | S14AA045-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building Stainless Steel Ladder w/o Cage | S14AA045 | 00001 | S14AA045-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 045 | Stainless Steel Ladder w/o Cage |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S14AA045 | S14AA045-00001
|  |  |  | S14AA046 Miscellaneous Steel Erection Work for Revamping Shelter/Building FRP Ladder w/o Cage | S14AA046-00001 Miscellaneous Steel Erection Work for Revamping Shelter/Building FRP Ladder w/o Cage | S14AA046 | 00001 | S14AA046-00001 | SS | S14 | Miscellaneous Steel Erection Work for Revamping | AA | Shelter/Building | 046 | FRP Ladder w/o Cage |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | M | S14AA046 | S14AA046-00001
|  |  |  | S41AA051 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051-00001 Steel Structure Paint Work Shelter/Building for Non-Fireproofed Steel Surface | S41AA051 | 00001 | S41AA051-00001 | SS | S41 | Steel Structure Paint Work | AA | Shelter/Building | 051 | for Non-Fireproofed Steel Surface |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | M2 | M2 | S41AA051 | S41AA051-00001
|  |  |  | S41AA052 Steel Structure Paint Work Shelter/Building for Fireproofed Steel Surface | S41AA052-00001 Steel Structure Paint Work Shelter/Building for Fireproofed Steel Surface | S41AA052 | 00001 | S41AA052-00001 | SS | S41 | Steel Structure Paint Work | AA | Shelter/Building | 052 | for Fireproofed Steel Surface |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | M2 | M2 | S41AA052 | S41AA052-00001
|  |  |  | S41AA053 Steel Structure Paint Work Shelter/Building Additional Painting on Hot-Dip Galvanized Steel Surface (Non-Fireproofed Steel) | S41AA053-00001 Steel Structure Paint Work Shelter/Building Additional Painting on Hot-Dip Galvanized Steel Surface (Non-Fireproofed Steel) | S41AA053 | 00001 | S41AA053-00001 | SS | S41 | Steel Structure Paint Work | AA | Shelter/Building | 053 | Additional Painting on Hot-Dip Galvanized Steel Surface (Non-Fireproofed Steel) |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | M2 | M2 | S41AA053 | S41AA053-00001
|  |  |  | S41AA054 Steel Structure Paint Work Shelter/Building Touch up | S41AA054-00001 Steel Structure Paint Work Shelter/Building Touch up | S41AA054 | 00001 | S41AA054-00001 | SS | S41 | Steel Structure Paint Work | AA | Shelter/Building | 054 | Touch up |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | M2 | M2 | S41AA054 | S41AA054-00001
|  |  |  | S42AA055 Steel Structure Coating Work Shelter/Building Hot-Dip Galvanizing w/ Surface Preparation | S42AA055-00001 Steel Structure Coating Work Shelter/Building Hot-Dip Galvanizing w/ Surface Preparation | S42AA055 | 00001 | S42AA055-00001 | SS | S42 | Steel Structure Coating Work | AA | Shelter/Building | 055 | Hot-Dip Galvanizing w/ Surface Preparation |  | 0 |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | Material: ( ) | 0 | 0 | 0 | 0 | M2 | M2 | S42AA055 | S42AA055-00001
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00001 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) M12 | S43AA061 | 00001 | S43AA061-00001 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 01 | M12 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00001
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00002 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) M16 | S43AA061 | 00002 | S43AA061-00002 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 02 | M16 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00002
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00003 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) M20 | S43AA061 | 00003 | S43AA061-00003 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 03 | M20 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00003
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00004 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) M22 | S43AA061 | 00004 | S43AA061-00004 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 04 | M22 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00004
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00005 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) M24 | S43AA061 | 00005 | S43AA061-00005 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 05 | M24 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00005
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00006 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) M27 | S43AA061 | 00006 | S43AA061-00006 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 17 | M27 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00006
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00007 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) M30 | S43AA061 | 00007 | S43AA061-00007 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 06 | M30 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00007
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00008 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) M33 | S43AA061 | 00008 | S43AA061-00008 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 07 | M33 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00008
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00009 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) M36 | S43AA061 | 00009 | S43AA061-00009 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 08 | M36 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00009
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00010 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) M42 | S43AA061 | 00010 | S43AA061-00010 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 09 | M42 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00010
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00011 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) M48 | S43AA061 | 00011 | S43AA061-00011 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 10 | M48 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00011
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00012 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) M52 | S43AA061 | 00012 | S43AA061-00012 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 11 | M52 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00012
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00013 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) M56 | S43AA061 | 00013 | S43AA061-00013 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 12 | M56 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00013
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00014 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) M64 | S43AA061 | 00014 | S43AA061-00014 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 13 | M64 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00014
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00015 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) M72 | S43AA061 | 00015 | S43AA061-00015 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 14 | M72 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00015
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00016 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) M76 | S43AA061 | 00016 | S43AA061-00016 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 15 | M76 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00016
|  |  |  | S43AA061 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) | S43AA061-00017 Anchor Bolt Work Shelter/Building Anchor Bolt (Material Supply) Over M76 | S43AA061 | 00017 | S43AA061-00017 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 061 | Anchor Bolt (Material Supply) |  | 0 | 16 | Over M76 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA061 | S43AA061-00017
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00001 Anchor Bolt Work Shelter/Building Setting Bolt M12 | S43AA062 | 00001 | S43AA062-00001 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 01 | M12 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00001
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00002 Anchor Bolt Work Shelter/Building Setting Bolt M16 | S43AA062 | 00002 | S43AA062-00002 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 02 | M16 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00002
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00003 Anchor Bolt Work Shelter/Building Setting Bolt M20 | S43AA062 | 00003 | S43AA062-00003 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 03 | M20 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00003
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00004 Anchor Bolt Work Shelter/Building Setting Bolt M22 | S43AA062 | 00004 | S43AA062-00004 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 04 | M22 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00004
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00005 Anchor Bolt Work Shelter/Building Setting Bolt M24 | S43AA062 | 00005 | S43AA062-00005 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 05 | M24 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00005
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00006 Anchor Bolt Work Shelter/Building Setting Bolt M27 | S43AA062 | 00006 | S43AA062-00006 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 17 | M27 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00006
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00007 Anchor Bolt Work Shelter/Building Setting Bolt M30 | S43AA062 | 00007 | S43AA062-00007 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 06 | M30 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00007
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00008 Anchor Bolt Work Shelter/Building Setting Bolt M33 | S43AA062 | 00008 | S43AA062-00008 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 07 | M33 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00008
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00009 Anchor Bolt Work Shelter/Building Setting Bolt M36 | S43AA062 | 00009 | S43AA062-00009 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 08 | M36 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00009
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00010 Anchor Bolt Work Shelter/Building Setting Bolt M42 | S43AA062 | 00010 | S43AA062-00010 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 09 | M42 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00010
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00011 Anchor Bolt Work Shelter/Building Setting Bolt M48 | S43AA062 | 00011 | S43AA062-00011 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 10 | M48 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00011
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00012 Anchor Bolt Work Shelter/Building Setting Bolt M52 | S43AA062 | 00012 | S43AA062-00012 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 11 | M52 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00012
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00013 Anchor Bolt Work Shelter/Building Setting Bolt M56 | S43AA062 | 00013 | S43AA062-00013 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 12 | M56 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00013
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00014 Anchor Bolt Work Shelter/Building Setting Bolt M64 | S43AA062 | 00014 | S43AA062-00014 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 13 | M64 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00014
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00015 Anchor Bolt Work Shelter/Building Setting Bolt M72 | S43AA062 | 00015 | S43AA062-00015 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 14 | M72 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00015
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00016 Anchor Bolt Work Shelter/Building Setting Bolt M76 | S43AA062 | 00016 | S43AA062-00016 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 15 | M76 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00016
|  |  |  | S43AA062 Anchor Bolt Work Shelter/Building Setting Bolt | S43AA062-00017 Anchor Bolt Work Shelter/Building Setting Bolt Over M76 | S43AA062 | 00017 | S43AA062-00017 | SS | S43 | Anchor Bolt Work | AA | Shelter/Building | 062 | Setting Bolt |  | 0 | 16 | Over M76 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EA | EA | S43AA062 | S43AA062-00017
|  |  |  | #VALUE! |  | #VALUE!
|  |  |  | F01AA000 Building/Shelter Fire Proofing Work Dense Concrete - | F01AA000-00001 Building/Shelter Fire Proofing Work Dense Concrete - 0.5 hr. rating (UL 1709) | F01AA000 | 00001 | F01AA000-00001 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 01 | 0.5 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M3; UoM UoM2: M3 | F01AA000 | F01AA000-00001
|  |  |  | F01AA000 Building/Shelter Fire Proofing Work Dense Concrete - | F01AA000-00002 Building/Shelter Fire Proofing Work Dense Concrete - 1 hr. rating (UL 1709) | F01AA000 | 00002 | F01AA000-00002 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 02 | 1 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M3; UoM UoM2: M3 | F01AA000 | F01AA000-00002
|  |  |  | F01AA000 Building/Shelter Fire Proofing Work Dense Concrete - | F01AA000-00003 Building/Shelter Fire Proofing Work Dense Concrete - 1.5 hr. rating (UL 1709) | F01AA000 | 00003 | F01AA000-00003 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 03 | 1.5 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M3; UoM UoM2: M3 | F01AA000 | F01AA000-00003
|  |  |  | F01AA000 Building/Shelter Fire Proofing Work Dense Concrete - | F01AA000-00004 Building/Shelter Fire Proofing Work Dense Concrete - 2 hr. rating (UL 1709) | F01AA000 | 00004 | F01AA000-00004 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 04 | 2 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M3; UoM UoM2: M3 | F01AA000 | F01AA000-00004
|  |  |  | F01AA000 Building/Shelter Fire Proofing Work Dense Concrete - | F01AA000-00005 Building/Shelter Fire Proofing Work Dense Concrete - 2.5 hr. rating (UL 1709) | F01AA000 | 00005 | F01AA000-00005 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 05 | 2.5 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M3; UoM UoM2: M3 | F01AA000 | F01AA000-00005
|  |  |  | F01AA000 Building/Shelter Fire Proofing Work Dense Concrete - | F01AA000-00006 Building/Shelter Fire Proofing Work Dense Concrete - 3 hr. rating (UL 1709) | F01AA000 | 00006 | F01AA000-00006 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 06 | 3 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M3; UoM UoM2: M3 | F01AA000 | F01AA000-00006
|  |  |  | F01AA000 Building/Shelter Fire Proofing Work Dense Concrete - | F01AA000-00007 Building/Shelter Fire Proofing Work Dense Concrete - 3.5 hr. rating (UL 1709) | F01AA000 | 00007 | F01AA000-00007 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 07 | 3.5 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M3; UoM UoM2: M3 | F01AA000 | F01AA000-00007
|  |  |  | F01AA000 Building/Shelter Fire Proofing Work Dense Concrete - | F01AA000-00008 Building/Shelter Fire Proofing Work Dense Concrete - 4 hr. rating (UL 1709) | F01AA000 | 00008 | F01AA000-00008 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 08 | 4 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M3; UoM UoM2: M3 | F01AA000 | F01AA000-00008
|  |  |  | F01AA000 Building/Shelter Fire Proofing Work Dense Concrete - | F01AA000-00009 Building/Shelter Fire Proofing Work Dense Concrete - Others (UL1709 rating) | F01AA000 | 00009 | F01AA000-00009 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 09 | Others (UL1709 rating) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M3; UoM UoM2: M3 | F01AA000 | F01AA000-00009
|  |  |  | F01AB000 Building/Shelter Fire Proofing Work Lightweight Cementitious - | F01AB000-00001 Building/Shelter Fire Proofing Work Lightweight Cementitious - 0.5 hr. rating (UL 1709) | F01AB000 | 00001 | F01AB000-00001 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 01 | 0.5 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M2; UoM UoM2: M2 | F01AB000 | F01AB000-00001
|  |  |  | F01AB000 Building/Shelter Fire Proofing Work Lightweight Cementitious - | F01AB000-00002 Building/Shelter Fire Proofing Work Lightweight Cementitious - 1 hr. rating (UL 1709) | F01AB000 | 00002 | F01AB000-00002 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 02 | 1 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M2; UoM UoM2: M2 | F01AB000 | F01AB000-00002
|  |  |  | F01AB000 Building/Shelter Fire Proofing Work Lightweight Cementitious - | F01AB000-00003 Building/Shelter Fire Proofing Work Lightweight Cementitious - 1.5 hr. rating (UL 1709) | F01AB000 | 00003 | F01AB000-00003 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 03 | 1.5 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M2; UoM UoM2: M2 | F01AB000 | F01AB000-00003
|  |  |  | F01AB000 Building/Shelter Fire Proofing Work Lightweight Cementitious - | F01AB000-00004 Building/Shelter Fire Proofing Work Lightweight Cementitious - 2 hr. rating (UL 1709) | F01AB000 | 00004 | F01AB000-00004 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 04 | 2 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M2; UoM UoM2: M2 | F01AB000 | F01AB000-00004
|  |  |  | F01AB000 Building/Shelter Fire Proofing Work Lightweight Cementitious - | F01AB000-00005 Building/Shelter Fire Proofing Work Lightweight Cementitious - 2.5 hr. rating (UL 1709) | F01AB000 | 00005 | F01AB000-00005 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 05 | 2.5 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M2; UoM UoM2: M2 | F01AB000 | F01AB000-00005
|  |  |  | F01AB000 Building/Shelter Fire Proofing Work Lightweight Cementitious - | F01AB000-00006 Building/Shelter Fire Proofing Work Lightweight Cementitious - 3 hr. rating (UL 1709) | F01AB000 | 00006 | F01AB000-00006 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 06 | 3 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M2; UoM UoM2: M2 | F01AB000 | F01AB000-00006
|  |  |  | F01AB000 Building/Shelter Fire Proofing Work Lightweight Cementitious - | F01AB000-00007 Building/Shelter Fire Proofing Work Lightweight Cementitious - 3.5 hr. rating (UL 1709) | F01AB000 | 00007 | F01AB000-00007 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 07 | 3.5 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M2; UoM UoM2: M2 | F01AB000 | F01AB000-00007
|  |  |  | F01AB000 Building/Shelter Fire Proofing Work Lightweight Cementitious - | F01AB000-00008 Building/Shelter Fire Proofing Work Lightweight Cementitious - 4 hr. rating (UL 1709) | F01AB000 | 00008 | F01AB000-00008 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 08 | 4 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M2; UoM UoM2: M2 | F01AB000 | F01AB000-00008
|  |  |  | F01AB000 Building/Shelter Fire Proofing Work Lightweight Cementitious - | F01AB000-00009 Building/Shelter Fire Proofing Work Lightweight Cementitious - Others (UL1709 rating) | F01AB000 | 00009 | F01AB000-00009 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 09 | Others (UL1709 rating) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: THK=( )mm; UoM UoM1: M2; UoM UoM2: M2 | F01AB000 | F01AB000-00009
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00001 Building/Shelter Fire Proofing Work Intumescent Coating Type - 0.5 hr. rating (UL 1709) | F01AC000 | 00001 | F01AC000-00001 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 01 | 0.5 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00001
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00002 Building/Shelter Fire Proofing Work Intumescent Coating Type - 1 hr. rating (UL 1709) | F01AC000 | 00002 | F01AC000-00002 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 02 | 1 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00002
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00003 Building/Shelter Fire Proofing Work Intumescent Coating Type - 1.5 hr. rating (UL 1709) | F01AC000 | 00003 | F01AC000-00003 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 03 | 1.5 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00003
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00004 Building/Shelter Fire Proofing Work Intumescent Coating Type - 2 hr. rating (UL 1709) | F01AC000 | 00004 | F01AC000-00004 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 04 | 2 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00004
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00005 Building/Shelter Fire Proofing Work Intumescent Coating Type - 2.5 hr. rating (UL 1709) | F01AC000 | 00005 | F01AC000-00005 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 05 | 2.5 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00005
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00006 Building/Shelter Fire Proofing Work Intumescent Coating Type - 3 hr. rating (UL 1709) | F01AC000 | 00006 | F01AC000-00006 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 06 | 3 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00006
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00007 Building/Shelter Fire Proofing Work Intumescent Coating Type - 3.5 hr. rating (UL 1709) | F01AC000 | 00007 | F01AC000-00007 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 07 | 3.5 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00007
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00008 Building/Shelter Fire Proofing Work Intumescent Coating Type - 4 hr. rating (UL 1709) | F01AC000 | 00008 | F01AC000-00008 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 08 | 4 hr. rating (UL 1709) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00008
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00009 Building/Shelter Fire Proofing Work Intumescent Coating Type - 0.5 hr. rating (UL 263) | F01AC000 | 00009 | F01AC000-00009 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 10 | 0.5 hr. rating (UL 263) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00009
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00010 Building/Shelter Fire Proofing Work Intumescent Coating Type - 1 hr. rating (UL 263) | F01AC000 | 00010 | F01AC000-00010 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 11 | 1 hr. rating (UL 263) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00010
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00011 Building/Shelter Fire Proofing Work Intumescent Coating Type - 1.5 hr. rating (UL 263) | F01AC000 | 00011 | F01AC000-00011 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 12 | 1.5 hr. rating (UL 263) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00011
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00012 Building/Shelter Fire Proofing Work Intumescent Coating Type - 2 hr. rating (UL 263) | F01AC000 | 00012 | F01AC000-00012 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 13 | 2 hr. rating (UL 263) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00012
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00013 Building/Shelter Fire Proofing Work Intumescent Coating Type - 2.5 hr. rating (UL 263) | F01AC000 | 00013 | F01AC000-00013 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 14 | 2.5 hr. rating (UL 263) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00013
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00014 Building/Shelter Fire Proofing Work Intumescent Coating Type - 3 hr. rating (UL 263) | F01AC000 | 00014 | F01AC000-00014 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 15 | 3 hr. rating (UL 263) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00014
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00015 Building/Shelter Fire Proofing Work Intumescent Coating Type - 3.5 hr. rating (UL 263) | F01AC000 | 00015 | F01AC000-00015 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 16 | 3.5 hr. rating (UL 263) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00015
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00016 Building/Shelter Fire Proofing Work Intumescent Coating Type - 4 hr. rating (UL 263) | F01AC000 | 00016 | F01AC000-00016 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 17 | 4 hr. rating (UL 263) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00016
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00017 Building/Shelter Fire Proofing Work Intumescent Coating Type - Others (UL263 rating) | F01AC000 | 00017 | F01AC000-00017 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 18 | Others (UL263 rating) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00017
|  |  |  | F01AC000 Building/Shelter Fire Proofing Work Intumescent Coating Type - | F01AC000-00018 Building/Shelter Fire Proofing Work Intumescent Coating Type - Others (UL1709 rating) | F01AC000 | 00018 | F01AC000-00018 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 09 | Others (UL1709 rating) | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AC000 | F01AC000-00018
|  |  |  | F01AD000 Building/Shelter Fire Proofing Work Top Coat for Cementitious Fire Proofing - | F01AD000-00001 Building/Shelter Fire Proofing Work Top Coat for Cementitious Fire Proofing - | F01AD000 | 00001 | F01AD000-00001 | FP | F01 | Building/Shelter Fire Proofing Work | AD | Top Coat for Cementitious Fire Proofing | 000 | - |  | 0 | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AD000 | F01AD000-00001
|  |  |  | F01AF000 Building/Shelter Fire Proofing Work Cryogenic (Cold protection) - | F01AF000-00001 Building/Shelter Fire Proofing Work Cryogenic (Cold protection) - | F01AF000 | 00001 | F01AF000-00001 | FP | F01 | Building/Shelter Fire Proofing Work | AF | Cryogenic (Cold protection) | 000 | - |  | 0 | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AF000 | F01AF000-00001
|  |  |  | F01AM000 Building/Shelter Fire Proofing Work Top Coat for Dense Concrete Fire Proofing - | F01AM000-00001 Building/Shelter Fire Proofing Work Top Coat for Dense Concrete Fire Proofing - | F01AM000 | 00001 | F01AM000-00001 | FP | F01 | Building/Shelter Fire Proofing Work | AM | Top Coat for Dense Concrete Fire Proofing | 000 | - |  | 0 | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AM000 | F01AM000-00001
|  |  |  | F01AP000 Building/Shelter Fire Proofing Work Top Coat for Cryogenic (Cold protection) Fire Proofing - | F01AP000-00001 Building/Shelter Fire Proofing Work Top Coat for Cryogenic (Cold protection) Fire Proofing - | F01AP000 | 00001 | F01AP000-00001 | FP | F01 | Building/Shelter Fire Proofing Work | AP | Top Coat for Cryogenic (Cold protection) Fire Proofing | 000 | - |  | 0 | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AP000 | F01AP000-00001
|  |  |  | F01AQ000 Building/Shelter Fire Proofing Work Top Coat for Intumescent Fire Proofing - | F01AQ000-00001 Building/Shelter Fire Proofing Work Top Coat for Intumescent Fire Proofing - | F01AQ000 | 00001 | F01AQ000-00001 | FP | F01 | Building/Shelter Fire Proofing Work | AQ | Top Coat for Intumescent Fire Proofing | 000 | - |  | 0 | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AQ000 | F01AQ000-00001
|  |  |  | F01AR000 Building/Shelter Fire Proofing Work Intermediate and top Coat for Intumescent Fire Proofing - | F01AR000-00001 Building/Shelter Fire Proofing Work Intermediate and top Coat for Intumescent Fire Proofing - | F01AR000 | 00001 | F01AR000-00001 | FP | F01 | Building/Shelter Fire Proofing Work | AR | Intermediate and top Coat for Intumescent Fire Proofing | 000 | - |  | 0 | [13 empty] | BOQ Specifications B01: Material: ( ); BOQ Specifications B02: DFT=( )㎛; UoM UoM1: M2; UoM UoM2: M2 | F01AR000 | F01AR000-00001

## Sheet1
수정사항
1 | GS1 Steel trowel finish 삭제 ->Room family 로 적용
2 | Ext wall paint 적용 기존 Ext wall Family 에 적용 -> Manual input 에 적용으로 변경 | 미완료
3 | slab edge 거푸집 산출 추가되어야함 | 미완료
4 | FDN 산출기준 중 Bitmen coating 물량 2배 적용됨 수정 필요 -> 하부는 Lean 에 포함 , 줄기초의 경우 Wall 폭 공제 필요 | 미공제로 적용후 지침서 기재
5 | Control joint 수치 기입물량 Web page 에서는 산축되나 엑셀 BOQ 시트에선 산출안됨
6 | Pile length /1000 으로 산출식 수정필요
7 | TG Bitumen 산출식에 H2 mm 단위로 기재 필요 H2 길이 다를때 는 Family list 분리 적용 ?